## Disclaimer
TasNetworks - Annual Planning Report 2023 - Supplementary Information
This information contained in this file forms part of TasNetworks Annual Planning Report 2023.
This Annual Planning Report (APR) has been prepared and published by Tasmanian Networks Pty Ltd (TasNetworks) solely for the purposes of TasNetworks’ compliance with regulatory obligations, including sections 5.12.2 and 5.13.2 of the National Electricity Rules and our transmission licence. The APR sets out network planning proposals, scenarios and forecasts as at the date of publication, which may change at any time or not eventuate. It has been prepared in good faith, including information and assumptions provided by third parties without further verification. It may not contain all information on the subject matter. Nothing in this APR should be taken as a recommendation in respect of any possible investment. Anyone considering using the information contained in this document should independently verify the currency, reliability, accuracy and completeness of the information. Accordingly, reliance should not be placed on the information contained in this document and TasNetworks makes no representation or warranty as to the reliability, accuracy or completeness of the information, or its suitability for any purpose other than the purpose for which it has been prepared. To the maximum extent permitted by law, TasNetworks, its employees, agents and consultants will have no liability for any loss or damage arising out of, or in connection with, the statements, opinions or other information in this document (including liability by reason of negligence or negligent misstatement).

## Methodology
Fault level and sequence impedances
We calculate fault currents at transmission network substations in accordance with the recommendations of Australian Standard AS 3851-1991 – “The calculation of short-circuit currents in three-phase AC systems”. From this, the maximum fault currents calculated at 1.1 pu voltage and the minimum at 0.9 pu voltage. The Thevenin impedance is defined as the source impedance back to the generators, and large motors where considered. This method thus defines the extreme envelope for all fault currents and is appropriate to be used for future planning. We recognise that at particular network locations the actual envelope could be smaller but this would need confirmation with detailed local studies.
Figure B–1 illustrates the AC and DC components that make up fault currents. The size and rate of decay of the DC component is a function of the ratio between the reactance (X) and the resistance (R) of the impedance between the faulted point of the system and the generation feeding the fault. This ratio is defined as the X/R ratio of the system, with the DC component decaying with time constant X/2πfR.
The maximum current that a circuit breaker will be exposed to is defined as the Peak Make Current. During fault conditions, the current a circuit breaker is expected to break is known as the RMS Break Current. This is defined as the RMS of the symmetrical AC component of the fault current plus the offset by the DC component at that point.
Figure B–1: Components of AC fault current

## Maximum
Maximum fault levels in Tasmanian substations
Bus | Voltage | Fault Level (kA) |  | Sequence Impedances in PU (100 MVA Base)
Name | [kV] | 3 phase | 1 phase to ground | Positive |  |  | Negative |  |  | Zero
|  |  |  | R | X | X/R | R | X | X/R | R | X | X/R
Arthurs Lake | 110 | 3.8693 | 3.6352 | 0.053005 | 0.13951 | 2.632 | 0.055032 | 0.14255 | 2.5904 | 0.031479 | 0.17362 | 5.5155
Arthurs Lake | 6.6 | 18.9347 | 0.0026901 | 0.052097 | 0.50552 | 9.7035 | 0.063247 | 0.55684 | 8.8043 | 0 | 0 | 0.00012399
Avoca | 110 | 1.8181 | 1.1977 | 0.15116 | 0.27948 | 1.8489 | 0.15127 | 0.28064 | 1.8552 | 0.22869 | 0.78753 | 3.4437
Avoca | 22 | 3.5653 | 1.57 | 0.17566 | 0.79058 | 4.5006 | 0.17577 | 0.79174 | 4.5043 | 0 | 3.9308 | >50
Boyer | 110 | 10.6816 | 6.9259 | 0.0091364 | 0.053275 | 5.831 | 0.0093878 | 0.054708 | 5.8276 | 0.028623 | 0.13763 | 4.8085
Boyer (A & B) | 6.6 | 25.2879 | 8.4941 | 0.017685 | 0.38011 | 21.4928 | 0.01791 | 0.38141 | 21.2963 | 0 | 2.637 | >50
Boyer (D & E) | 6.6 | 35.4173 | 16.3623 | 0.010113 | 0.2715 | 26.8469 | 0.013621 | 0.3156 | 23.1712 | 0.0013249 | 1.177 | >50
Boyer (F) | 6.6 | 28.8323 | 12.3891 | 0.007016 | 0.33367 | 47.5581 | 0.0070516 | 0.33468 | 47.4615 | 0.00076509 | 1.6617 | >50
Boyer (G) | 6.6 | 24.2877 | 11.7729 | 0.0095523 | 0.39608 | 41.4639 | 0.0094548 | 0.39415 | 41.6871 | 0.0060606 | 1.6618 | >50
Bridgewater | 110 | 8.235 | 5.3746 | 0.0109 | 0.069261 | 6.354 | 0.010955 | 0.070102 | 6.3992 | 0.044959 | 0.17593 | 3.9132
Bridgewater | 11 | 14.1883 | 6.2063 | 0.016483 | 0.40659 | 24.6674 | 0.016537 | 0.40743 | 24.6371 | 0 | 1.9769 | >50
Bridgewater | 11 | 7.7931 | 3.1918 | 0.033 | 0.74016 | 22.4289 | 0.033055 | 0.741 | 22.4174 | 0 | 3.9471 | >50
Burnie | 220 | 5.24 | 4.2643 | 0.0083415 | 0.054462 | 6.529 | 0.0080651 | 0.052762 | 6.542 | 0.013385 | 0.093707 | 7.0009
Burnie | 110 | 7.6 | 5.3 | 0.011288 | 0.076037 | 6.7363 | 0.010944 | 0.068513 | 6.2606 | 0.024592 | 0.18248 | 7.4204
Burnie | 22 | 11.3809 | 5.5569 | 0.017631 | 0.25304 | 14.3525 | 0.017266 | 0.24532 | 14.2083 | 0 | 1.0599 | >50
Butlers Gorge | 110 | 4.6874 | 4.2121 | 0.044106 | 0.11502 | 2.6078 | 0.045492 | 0.1182 | 2.5982 | 0.027765 | 0.16095 | 5.7967
Cattle Hill | 220 | 9.6387 | 9.6556 | 0.0030623 | 0.029794 | 9.7291 | 0.0031631 | 0.030611 | 9.6774 | 0.0039577 | 0.02871 | 7.2543
Chapel Street | 220 | 8.3881 | 8.0947 | 0.0037413 | 0.034213 | 9.1445 | 0.0037927 | 0.034899 | 9.2016 | 0.0031603 | 0.037345 | 11.8168
Chapel Street | 110 | 14.781 | 15.9185 | 0.0041114 | 0.038844 | 9.4478 | 0.0041621 | 0.039699 | 9.5382 | 0.002049 | 0.029776 | 14.532
Chapel Street | 11 | 15.647 | 8.8558 | 0.013461 | 0.36874 | 27.3926 | 0.013512 | 0.3696 | 27.3532 | 0 | 1.2174 | >50
Chapel Street | 11 | 8.254 | 4.5189 | 0.022811 | 0.69914 | 30.6488 | 0.022862 | 0.7 | 30.6183 | 0 | 2.4342 | >50
Comalco | 220 | 12.5087 | 12.9602 | 0.0018909 | 0.023001 | 12.1641 | 0.0019346 | 0.023271 | 12.0287 | 0.0022589 | 0.020274 | 8.9751
Creek Road | 110 | 14.1716 | 14.0747 | 0.004535 | 0.040488 | 8.9277 | 0.0045889 | 0.041358 | 9.0127 | 0.0056532 | 0.040328 | 7.1336
Creek Road | 33 | 13.971 | 5.8552 | 0.0069464 | 0.13758 | 19.8056 | 0.0070002 | 0.13845 | 19.7777 | 0 | 0.71003 | >50
Creek Road | 33 | 10.3321 | 4.0497 | 0.0082354 | 0.18609 | 22.5962 | 0.0082892 | 0.18696 | 22.5544 | 0 | 1.0529 | >50
Derby | 110 | 3.8362 | 2.0227 | 0.025975 | 0.14827 | 5.7083 | 0.026639 | 0.15191 | 5.7025 | 0.15743 | 0.53057 | 3.3701
Derby | 22 | 4.2823 | 1.2729 | 0.045975 | 0.67267 | 14.6312 | 0.046639 | 0.67631 | 14.5008 | 0 | 5.4706 | >50
Derwent Bridge | 110 | 3.2718 | 2.4854 | 0.073104 | 0.16065 | 2.1975 | 0.074192 | 0.16357 | 2.2047 | 0.083667 | 0.33359 | 3.9872
Derwent Bridge | 22 | 4.1678 | 1.8348 | 0.088804 | 0.68705 | 7.7366 | 0.089892 | 0.68997 | 7.6755 | 0 | 3.345 | >50
Devonport | 110 | 6.9778 | 4.7119 | 0.010651 | 0.082059 | 7.7046 | 0.010982 | 0.08029 | 7.3109 | 0.03175 | 0.2014 | 6.3435
Devonport | 22 | 11.6969 | 5.3433 | 0.016079 | 0.24628 | 15.3164 | 0.016411 | 0.24451 | 14.8991 | 0 | 1.1299 | >50
Electrona | 110 | 6.1583 | 3.8245 | 0.026326 | 0.089986 | 3.4181 | 0.026377 | 0.090841 | 3.4439 | 0.053005 | 0.25964 | 4.8984
Electrona | 11 | 16.6606 | 6.7124 | 0.036504 | 0.34461 | 9.4404 | 0.036554 | 0.34547 | 9.4507 | 0 | 1.8895 | >50
Electrona1 | 11 | 9.3331 | 3.716 | 0.042226 | 0.61719 | 14.6161 | 0.042277 | 0.61804 | 14.6188 | 0 | 3.4264 | >50
Emu Bay | 110 | 7.0414 | 4.8356 | 0.013565 | 0.08087 | 5.9614 | 0.013283 | 0.073627 | 5.543 | 0.031144 | 0.19901 | 6.39
Emu Bay | 11 | 14.7869 | 6.2105 | 0.023541 | 0.38974 | 16.5562 | 0.023258 | 0.3825 | 16.4459 | 0 | 2.0166 | >50
Emu Bay | 11 | 8.2699 | 3.1963 | 0.033565 | 0.69737 | 20.7764 | 0.033283 | 0.69013 | 20.7352 | 0 | 4.0331 | >50
Farrell | 220 | 9.6459 | 10.0651 | 0.0023315 | 0.029837 | 12.7972 | 0.0024358 | 0.03054 | 12.538 | 0.0034162 | 0.025278 | 7.3996
Farrell | 110 | 8.2094 | 10.0925 | 0.0026908 | 0.07028 | 26.1185 | 0.0027747 | 0.07066 | 25.4653 | 0.0014266 | 0.030545 | 21.4107
George Town | 220 | 12.7834 | 13.5734 | 0.0017984 | 0.022511 | 12.5173 | 0.0018421 | 0.022781 | 12.3667 | 0.0016636 | 0.018292 | 10.9956
George Town | 110 | 14.5713 | 15.5915 | 0.0016406 | 0.039589 | 24.1309 | 0.0016901 | 0.040354 | 23.877 | 0.0014435 | 0.031045 | 21.5076
George Town | 22 | 10.0795 | 5.6428 | 0.0058578 | 0.28635 | 48.8837 | 0.0059073 | 0.28712 | 48.6037 | 0 | 0.96143 | >50
Gordon | 220 | 7.2386 | 8.2329 | 0.0025086 | 0.039804 | 15.867 | 0.0024655 | 0.039784 | 16.1365 | 0.00063067 | 0.02546 | 40.3692
Gordon | 22 | 2.0953 | 0.09 | 0.070609 | 1.3771 | 19.5033 | 0.070565 | 1.3771 | 19.515 | 0 | 0 | >50
Hadspen | 220 | 12.4415 | 11.3856 | 0.0023037 | 0.023089 | 10.0226 | 0.0023757 | 0.023584 | 9.9273 | 0.0043279 | 0.028857 | 6.6677
Hadspen | 110 | 14.5217 | 14.3038 | 0.0034336 | 0.03961 | 11.5359 | 0.0035416 | 0.040788 | 11.5168 | 0.0036741 | 0.040225 | 10.9482
Hadspen | 22 | 10.0095 | 5.3402 | 0.0077028 | 0.28831 | 37.4289 | 0.0078109 | 0.28949 | 37.0622 | 0 | 1.0441 | >50
Hampshire | 110 | 3.3938 | 2.1067 | 0.043671 | 0.16446 | 3.766 | 0.043306 | 0.15674 | 3.6194 | 0.10768 | 0.47813 | 4.4404
Huon River | 110 | 2.619 | 1.6506 | 0.087544 | 0.2024 | 2.3119 | 0.087595 | 0.20325 | 2.3204 | 0.16852 | 0.58686 | 3.4824
Huon River | 11 | 7.899 | 3.5693 | 0.10344 | 0.7236 | 6.9951 | 0.10349 | 0.72445 | 6.9999 | 0 | 3.4017 | >50
Kermandie | 110 | 3.236 | 1.9683 | 0.066534 | 0.16559 | 2.4888 | 0.066585 | 0.16644 | 2.4997 | 0.13261 | 0.5075 | 3.827
Kermandie | 11 | 8.7451 | 11.473 | 0.094444 | 0.65344 | 6.9188 | 0.094495 | 0.65429 | 6.9241 | 0.037784 | 0.18486 | 4.8926
Kingston | 110 | 8.3258 | 5.0433 | 0.01503 | 0.0677 | 4.5044 | 0.01508 | 0.068554 | 4.546 | 0.035618 | 0.20087 | 5.6397
Kingston | 33 | 7.2092 | 2.0947 | 0.01928 | 0.26627 | 13.8111 | 0.01933 | 0.26713 | 13.8192 | 0 | 2.2251 | >50
Kingston | 11 | 14.4552 | 6.0337 | 0.026029 | 0.39857 | 15.3122 | 0.02608 | 0.39942 | 15.3152 | 0 | 2.0725 | >50
Kingston | 11 | 7.9438 | 3.0911 | 0.03693 | 0.7259 | 19.6564 | 0.03698 | 0.72675 | 19.6526 | 0 | 4.1526 | >50
Knights Rd | 110 | 5.6352 | 3.5172 | 0.027634 | 0.098667 | 3.5705 | 0.027685 | 0.099521 | 3.5948 | 0.058841 | 0.28096 | 4.775
Knights Rd | 11 | 10.3313 | 3.5675 | 0.033734 | 0.55784 | 16.5365 | 0.033784 | 0.55869 | 16.537 | 0 | 3.7397 | >50
Liapootah | 220 | 9.5685 | 9.651 | 0.0029375 | 0.030027 | 10.222 | 0.0031141 | 0.031217 | 10.0242 | 0.0030252 | 0.028034 | 9.267
Lindisfarne | 220 | 6.0611 | 6.339 | 0.0045965 | 0.04741 | 10.3143 | 0.004674 | 0.048215 | 10.3155 | 0.0050388 | 0.040256 | 7.9892
Lindisfarne | 110 | 12.864 | 11.4554 | 0.0051053 | 0.044591 | 8.7341 | 0.0051598 | 0.045432 | 8.805 | 0.0093747 | 0.0599 | 6.3896
Lindisfarne | 33 | 7.9263 | 2.5085 | 0.01 | 0.243 | 24.9041 | 0.01 | 0.245 | 24.776 | 0 | 1.821 | >50
Meadowbank | 110 | 8.8266 | 7.1456 | 0.013223 | 0.064062 | 4.8447 | 0.013342 | 0.065421 | 4.9034 | 0.012759 | 0.10972 | 8.5988
Meadowbank | 22 | 5.0047 | 3.9348 | 0.037623 | 0.57566 | 15.3007 | 0.037742 | 0.57702 | 15.2886 | 0 | 1.0475 | >50
Mornington | 110 | 10.5364 | 7.4579 | 0.0070694 | 0.054339 | 7.6865 | 0.0071239 | 0.055181 | 7.7459 | 0.022165 | 0.11987 | 5.4083
Mornington | 33 | 7.8261 | 2.1293 | 0.011294 | 0.24566 | 21.7509 | 0.011349 | 0.24651 | 21.7207 | 0 | 2.2216 | >50
Mowbray | 110 | 11.4784 | 11.2101 | 0.0050242 | 0.050049 | 9.9616 | 0.0051889 | 0.051428 | 9.9112 | 0.0062584 | 0.052156 | 8.3337
Mowbray | 22 | 9.7039 | 4.3395 | 0.0098287 | 0.29733 | 30.2516 | 0.0099934 | 0.29871 | 29.891 | 0 | 1.3999 | >50
New Norfolk | 110 | 11.8151 | 7.7698 | 0.0082351 | 0.048168 | 5.8491 | 0.0084594 | 0.049532 | 5.8553 | 0.021513 | 0.12193 | 5.6679
New Norfolk | 22 | 7.811 | 3.7496 | 0.016735 | 0.36922 | 22.0625 | 0.016959 | 0.37058 | 21.8512 | 0 | 1.5703 | >50
Newton | 110 | 4.3688 | 3.586 | 0.013501 | 0.13149 | 9.7391 | 0.013585 | 0.13187 | 9.7069 | 0.049588 | 0.21365 | 4.3084
Newton | 11 | 7.551 | 0.21917 | 0.042201 | 0.76349 | 18.0917 | 0.042285 | 0.76387 | 18.0648 | 78.7191 | 4.6116 | 0.058583
Newton | 22 | 3.7503 | 1.4654 | 0.042201 | 0.76879 | 18.2173 | 0.042285 | 0.76917 | 18.1901 | 0 | 4.3822 | >50
North Hobart | 110 | 13.3261 | 12.9709 | 0.0064959 | 0.042836 | 6.5943 | 0.0065497 | 0.043706 | 6.673 | 0.010633 | 0.044878 | 4.2205
North Hobart | 11 | 11.4331 | 6.1144 | 0.0098095 | 0.5049 | 51.4705 | 0.0098633 | 0.50577 | 51.2779 | 0 | 1.8223 | >50
Norwood | 110 | 11.9915 | 10.6841 | 0.0049097 | 0.047897 | 9.7556 | 0.0050381 | 0.049174 | 9.7603 | 0.0099291 | 0.063826 | 6.4282
Norwood | 22 | 9.1523 | 5.5526 | 0.012129 | 0.31519 | 25.9868 | 0.012257 | 0.31647 | 25.8187 | 0 | 0.92802 | >50
Palmerston | 220 | 13.9112 | 14.2163 | 0.0016824 | 0.020683 | 12.2939 | 0.0017647 | 0.021267 | 12.0516 | 0.0020604 | 0.018719 | 9.0848
Palmerston | 110 | 13.7102 | 14.0813 | 0.004281 | 0.041894 | 9.7859 | 0.0043933 | 0.043052 | 9.7993 | 0.0028494 | 0.03752 | 13.1678
Palmerston | 22 | 9.5673 | 3.3462 | 0.015355 | 0.30135 | 19.6253 | 0.015468 | 0.30251 | 19.5576 | 0 | 1.9849 | >50
Paloona | 110 | 8.9425 | 8.999 | 0.0082529 | 0.064036 | 7.7592 | 0.0086646 | 0.061955 | 7.1503 | 0.0079591 | 0.064874 | 8.1509
Pieman | 220 | 7.6433 | 8.7035 | 0.0035391 | 0.037604 | 10.6253 | 0.0035814 | 0.03798 | 10.6048 | 0.0017747 | 0.023526 | 13.256
Port Latta | 110 | 3.6759 | 2.4695 | 0.053345 | 0.15434 | 2.8932 | 0.03603 | 0.12023 | 3.3369 | 0.1211 | 0.42361 | 3.4981
Port Latta | 22 | 8.2956 | 3.3647 | 0.066639 | 0.3556 | 5.3363 | 0.049324 | 0.3215 | 6.518 | 0 | 1.9964 | >50
Port Latta | 22 | 5.4491 | 1.9497 | 0.079345 | 0.54504 | 6.8692 | 0.06203 | 0.51093 | 8.2368 | 0 | 3.5599 | >50
Que | 110 | 4.0522 | 3.3177 | 0.027881 | 0.13975 | 5.0124 | 0.027965 | 0.14013 | 5.0109 | 0.066562 | 0.22778 | 3.422
Que | 22 | 3.8588 | 1.7086 | 0.046181 | 0.74685 | 16.1723 | 0.046265 | 0.74723 | 16.1512 | 0 | 3.5806 | >50
Queenstown | 110 | 3.0099 | 2.3094 | 0.021358 | 0.1907 | 8.9284 | 0.021442 | 0.19108 | 8.9111 | 0.075467 | 0.35932 | 4.7613
Queenstown | 22 | 6.4213 | 3.32 | 0.029709 | 0.44862 | 15.1004 | 0.029793 | 0.449 | 15.0706 | 0 | 1.7111 | >50
Queenstown | 11 | 12.7352 | 6.5878 | 0.029028 | 0.45243 | 15.5858 | 0.029112 | 0.45281 | 15.5539 | 0 | 1.7235 | >50
Railton | 110 | 8.7674 | 6.5276 | 0.0064891 | 0.065535 | 10.0991 | 0.0068207 | 0.063766 | 9.3488 | 0.031214 | 0.1323 | 4.2386
Railton | 22 | 8.4196 | 3.7831 | 0.013614 | 0.34261 | 25.1657 | 0.013946 | 0.34084 | 24.4405 | 0 | 1.6062 | >50
Risdon | 110 | 13.4049 | 12.198 | 0.0049915 | 0.042781 | 8.5707 | 0.0050444 | 0.04363 | 8.6493 | 0.008927 | 0.054315 | 6.0844
Risdon | 33 | 11.016 | 4.5319 | 0.0081304 | 0.17452 | 21.4648 | 0.0081833 | 0.17537 | 21.4299 | 0 | 0.92423 | >50
Risdon | 11 | 20.4011 | 3.2405 | 0.009291 | 0.27291 | 29.374 | 0.0093439 | 0.27376 | 29.2988 | 4.8476 | 1.1622 | 0.23975
Rokeby | 110 | 8.1721 | 5.3516 | 0.010206 | 0.069911 | 6.8499 | 0.010261 | 0.070753 | 6.8956 | 0.034115 | 0.17839 | 5.229
Rokeby | 11 | 14.4706 | 6.0479 | 0.01962 | 0.3985 | 20.311 | 0.019675 | 0.39935 | 20.2975 | 0 | 2.0661 | >50
Rokeby | 11 | 7.8056 | 3.0879 | 0.032106 | 0.73901 | 23.0178 | 0.032161 | 0.73985 | 23.005 | 0 | 4.1322 | >50
Rosebery | 110 | 7.3347 | 7.6213 | 0.0058207 | 0.078505 | 13.4872 | 0.0059046 | 0.078884 | 13.3598 | 0.015318 | 0.068273 | 4.457
Rosebery | 44 | 5.6961 | 2.8158 | 0.012349 | 0.25313 | 20.4983 | 0.012433 | 0.2535 | 20.3905 | 0.0617 | 1.0295 | 16.6854
Rosebery | 22 | 2.8515 | 2.2813 | 0.073649 | 1.0101 | 13.7155 | 0.073732 | 1.0105 | 13.705 | 0 | 1.7755 | >50
Savage River | 110 | 1.849 | 1.2076 | 0.087031 | 0.30013 | 3.4486 | 0.087115 | 0.30051 | 3.4496 | 0.1843 | 0.79109 | 4.2923
Savage River | 22 | 5.5563 | 3.0863 | 0.10053 | 0.50978 | 5.0709 | 0.10061 | 0.51016 | 5.0704 | 0 | 1.78 | >50
Scottsdale | 110 | 5.172 | 3.282 | 0.02246 | 0.10936 | 4.8691 | 0.022751 | 0.11127 | 4.8907 | 0.079418 | 0.29233 | 3.6809
Scottsdale | 22 | 12.0176 | 6.6281 | 0.02816 | 0.23856 | 8.4716 | 0.028451 | 0.24047 | 8.4521 | 0 | 0.82645 | >50
Sheffield | 220 | 12.9283 | 13.2314 | 0.0017706 | 0.022259 | 12.5712 | 0.001819 | 0.022134 | 12.1681 | 0.0027008 | 0.020757 | 7.6856
Sheffield | 110 | 12.066 | 13.3836 | 0.0028219 | 0.047767 | 16.9272 | 0.0031535 | 0.045998 | 14.5865 | 0.0026509 | 0.035365 | 13.3405
Sheffield | 22 | 5.1337 | 1.2482 | 0.022896 | 0.56637 | 24.7363 | 0.023303 | 0.56518 | 24.2534 | 0 | 5.8676 | >50
Smithton | 110 | 3.1287 | 2.0885 | 0.065871 | 0.18225 | 2.7668 | 0.036918 | 0.13216 | 3.5799 | 0.15514 | 0.51745 | 3.3354
Smithton | 22 | 6.7537 | 7.6986 | 0.071441 | 0.42145 | 5.8993 | 0.043024 | 0.37059 | 8.6136 | 0 | 0.3271 | >50
Smithton | 22 | 4.4577 | 4.7272 | 0.079271 | 0.65765 | 8.8296 | 0.050318 | 0.60756 | 12.0745 | 0 | 0.6543 | >50
Sorell | 110 | 4.9136 | 3.0418 | 0.029651 | 0.11371 | 3.835 | 0.029705 | 0.11455 | 3.8563 | 0.065345 | 0.32752 | 5.0122
Sorell | 22 | 8.4422 | 2.8815 | 0.022356 | 0.34123 | 15.2638 | 0.02241 | 0.34207 | 15.2642 | 0 | 2.3232 | >50
St Leonards | 110 | 11.1723 | 10.4757 | 0.0051478 | 0.051421 | 9.9889 | 0.0052906 | 0.052738 | 9.9682 | 0.0087268 | 0.060071 | 6.8835
St Leonards | 22 | 9.3001 | 2.5218 | 0.0085479 | 0.3103 | 36.301 | 0.0086906 | 0.31161 | 35.856 | 0 | 2.8144 | >50
St Marys | 110 | 1.1221 | 0.71696 | 0.25382 | 0.4484 | 1.7666 | 0.25393 | 0.44956 | 1.7704 | 0.43408 | 1.3383 | 3.0831
St Marys | 22 | 3.0274 | 4.1708 | 0.28685 | 0.90965 | 3.1712 | 0.28696 | 0.91081 | 3.174 | 0 | 0.1754 | >50
Starwood | 110 | 10.1838 | 8.9427 | 0.0096406 | 0.055869 | 5.7952 | 0.0096901 | 0.056634 | 5.8445 | 0.019053 | 0.077345 | 4.0594
Tarraleah | 110 | 10.5711 | 11.8255 | 0.0084348 | 0.053962 | 6.3976 | 0.0090011 | 0.056364 | 6.262 | 0.0018018 | 0.034875 | 19.3556
Temco | 110 | 12.9016 | 11.7197 | 0.0033706 | 0.044624 | 13.2392 | 0.0034201 | 0.045389 | 13.2713 | 0.0080785 | 0.05703 | 7.0596
Trevallyn | 110 | 12.6638 | 12.6023 | 0.0044646 | 0.045373 | 10.1627 | 0.0046457 | 0.046794 | 10.0726 | 0.0033614 | 0.044708 | 13.3003
Trevallyn | 22 | 13.9616 | 5.8402 | 0.0072979 | 0.20664 | 28.3147 | 0.0074791 | 0.20806 | 27.8191 | 0 | 1.0683 | >50
Trevallyn | 22 | 10.0446 | 3.9796 | 0.0087146 | 0.28727 | 32.9645 | 0.0088957 | 0.28869 | 32.4531 | 0 | 1.6007 | >50
Triabunna | 110 | 1.6297 | 1.1319 | 0.23955 | 0.2612 | 1.0904 | 0.2396 | 0.26204 | 1.0936 | 0.31902 | 0.78475 | 2.4598
Triabunna | 22 | 4.9882 | 2.7755 | 0.24955 | 0.5222 | 2.0926 | 0.2496 | 0.52304 | 2.0955 | 0 | 2.0362 | >50
Tungatinah | 110 | 10.7574 | 12.1187 | 0.0079604 | 0.053078 | 6.6678 | 0.0084986 | 0.055443 | 6.5237 | 0.0013254 | 0.033296 | 25.1216
Tungatinah | 22 | 4.939 | 1.4395 | 0.02836 | 0.58388 | 20.5878 | 0.028899 | 0.58624 | 20.2862 | 0 | 4.8574 | >50
Ulverstone | 110 | 6.2555 | 4.7232 | 0.019323 | 0.090256 | 4.6709 | 0.019551 | 0.086448 | 4.4218 | 0.038433 | 0.18181 | 4.7307
Ulverstone | 22 | 8.8727 | 4.4956 | 0.026873 | 0.32426 | 12.0662 | 0.027101 | 0.32045 | 11.8244 | 0 | 1.2813 | >50
Waddamana | 220 | 10.7859 | 10.8329 | 0.0024296 | 0.026654 | 10.9707 | 0.0025322 | 0.027477 | 10.851 | 0.0034786 | 0.025368 | 7.2926
Waddamana | 110 | 7.2483 | 5.1262 | 0.01626 | 0.077981 | 4.7959 | 0.016573 | 0.079825 | 4.8166 | 0.030315 | 0.17417 | 5.7451
Waddamana | 22 | 1.8068 | 2.2673 | 0.15426 | 1.592 | 10.3201 | 0.15457 | 1.5938 | 10.3112 | 0 | 0.624 | >50
Waratah Tee | 110 | 2.5095 | 1.7617 | 0.057741 | 0.22281 | 3.8588 | 0.057825 | 0.22319 | 3.8598 | 0.12568 | 0.50805 | 4.0423
Wesley Vale | 110 | 6.4532 | 3.7312 | 0.013634 | 0.088429 | 6.4858 | 0.013966 | 0.08666 | 6.2051 | 0.049956 | 0.2827 | 5.659
Wesley Vale | 22 | 7.1217 | 2.889 | 0.028075 | 0.4044 | 14.4041 | 0.028407 | 0.40263 | 14.1737 | 0 | 2.1915 | >50
Notes on above maximum fault levels 1. Boyer 6.6 kV F & G buses, Chapel Street 11 kV, Electrona 11 kV, Emu Bay 11 kV and Kingston 11 kV buses are kept open due to exceedance of 13 kA fault level. 2. Bridgewater 11 kV and Rokeby 11 kV buses are kept normally open for protection reasons. 3. Mowbray 22 kV and Trevallyn 22 kV buses are closed but the 22 kV Trevallyn–Mowbray super feeders are normally kept open to keep fault levels below 13 kA. 4. At Emu Bay Substation, 0.82 mH/Phase reactors are installed on feeders 19, 20, 21, 23 and 24 to limit the downstream distribution fault currents. With these reactors, when the 11 kV bus coupler is closed, fault current is below 13.0 kA. We are investigating the opportunity to operate the bus coupler at this substation closed. The maximum fault currents on the feeders with the reactors in service and bus coupler closed are listed below. 5. At Creek Road and Trevallyn substations the supply transformer incoming circuit breaker is operated open due to exceedance of 13 kA fault level. It is only opened when fault level exceeds 13 kA. 6. Port Latta 22 kV BC usually operated open. 7. Smithton 22 kV BC operated open due to distribution earthing issue.
Maximum fault levels
Bus | Voltage | Fault Level (kA) |  | Sequence Impedances in PU
Name [feeder number] | [kV] | 3 phase | 1 phase to ground | Positive |  |  | Negative |  |  | Zero
|  |  |  | R | X | X/R | R | X | X/R | R | X | X/R
Emu Bay [19] | 11 | 9.5165 | 5.0349 | 0.023537 | 0.60681 | 25.7807 | 0.023299 | 0.60019 | 25.7606 | 1.3694e-16 | 2.2355 | >50
Emu Bay [20] | 11 | 9.7883 | 5.1099 | 0.023537 | 0.58993 | 25.0638 | 0.023299 | 0.58332 | 25.0363 | 1.3591e-16 | 2.2186 | >50
Emu Bay [21] | 11 | 9.7883 | 5.1099 | 0.023537 | 0.58993 | 25.0638 | 0.023299 | 0.58332 | 25.0363 | 1.3591e-16 | 2.2186 | >50
Emu Bay [23] | 11 | 9.7883 | 5.1099 | 0.023537 | 0.58993 | 25.0638 | 0.023299 | 0.58332 | 25.0363 | 1.3591e-16 | 2.2186 | >50
Emu Bay [24] | 11 | 9.5732 | 5.0513 | 0.033464 | 0.60274 | 18.0115 | 0.033226 | 0.59612 | 17.9417 | 0.0099268 | 2.2314 | >50

## Minimum
Minimum fault levels in Tasmanian substations
Bus | Voltage | Fault Level (kA) |  | Sequence Impedances in PU (100 MVA Base)
Name | [kV] | 3 phase | 1 phase to ground | Positive |  |  | Negative |  |  | Zero
|  |  |  | R | X | X/R | R | X | X/R | R | X | X/R
Arthurs Lake | 110 | 2.248 | 2.3683 | 0.06366 | 0.20037 | 3.1475 | 0.06382 | 0.20319 | 3.1838 | 0.031479 | 0.17362 | 5.5155
Arthurs Lake | 6.6 | 10.9606 | 0.09 | 0.08246 | 0.71357 | 8.6535 | 0.08262 | 0.71639 | 8.6709 | 0 | 0 | >50
Avoca | 110 | 1.2819 | 0.91339 | 0.1563 | 0.33422 | 2.1383 | 0.15646 | 0.33704 | 2.1542 | 0.22869 | 0.78753 | 3.4437
Avoca | 22 | 2.7334 | 1.2602 | 0.1808 | 0.84532 | 4.6754 | 0.18096 | 0.84814 | 4.6869 | 0 | 3.9308 | >50
Boyer | 110 | 3.7924 | 3.6167 | 0.018748 | 0.12317 | 6.5698 | 0.018784 | 0.1255 | 6.6814 | 0.028623 | 0.13763 | 4.8085
Boyer (A & B) | 6.6 | 9.0602 | 3.1064 | 0.042467 | 0.86797 | 20.4388 | 0.042503 | 0.8703 | 20.4763 | 0 | 5.8678 | >50
Boyer (D & E) | 6.6 | 10.3687 | 6.0957 | 0.03542 | 0.7585 | 21.4143 | 0.035457 | 0.76084 | 21.4583 | 0.0053 | 2.355 | >50
Boyer (F) | 6.6 | 10.5946 | 7.4979 | 0.037124 | 0.74221 | 19.9929 | 0.03716 | 0.74454 | 20.0362 | 0.00076558 | 1.6626 | >50
Boyer (G) | 6.6 | 10.5151 | 7.4709 | 0.036713 | 0.74785 | 20.3704 | 0.036749 | 0.75019 | 20.4138 | 0.0060656 | 1.6626 | >50
Bridgewater | 110 | 3.1041 | 2.7275 | 0.021445 | 0.15071 | 7.028 | 0.021482 | 0.15304 | 7.124 | 0.050894 | 0.2075 | 4.0771
Bridgewater | 11 | 5.9214 | 2.5578 | 0.03775 | 0.79694 | 21.1112 | 0.037787 | 0.79927 | 21.1519 | 0 | 3.9471 | >50
Burnie | 220 | 0.84052 | 0.97469 | 0.040885 | 0.27936 | 6.8328 | 0.040986 | 0.28122 | 6.8614 | 0.015969 | 0.16239 | 10.1692
Burnie | 110 | 2.3481 | 1.7313 | 0.039785 | 0.19731 | 4.9594 | 0.039886 | 0.19917 | 4.9935 | 0.083469 | 0.40648 | 4.8699
Burnie | 22 | 4.8089 | 2.2854 | 0.031627 | 0.49021 | 15.4998 | 0.031728 | 0.49207 | 15.5091 | 0 | 2.1198 | >50
Butlers Gorge | 110 | 2.0835 | 2.2947 | 0.072812 | 0.21486 | 2.9509 | 0.072856 | 0.21724 | 2.9817 | 0.027765 | 0.16095 | 5.7967
Cattle Hill | 220 | 3.3549 | 4.1181 | 0.0054261 | 0.070215 | 12.9401 | 0.0054665 | 0.072532 | 13.2684 | 0.0039577 | 0.02871 | 7.2543
Chapel Street | 220 | 2.178 | 2.7478 | 0.012017 | 0.10786 | 8.9754 | 0.012055 | 0.11018 | 9.1402 | 0.0031427 | 0.038505 | 12.2522
Chapel Street | 110 | 4.6724 | 5.8734 | 0.010007 | 0.10062 | 10.0547 | 0.010044 | 0.10295 | 10.2493 | 0.0025801 | 0.036676 | 14.2148
Chapel Street | 11 | 6.2181 | 3.5839 | 0.028669 | 0.75921 | 26.4819 | 0.028706 | 0.76154 | 26.5286 | 0 | 2.4342 | >50
Comalco | 220 | 2.9915 | 3.8889 | 0.0075935 | 0.078619 | 10.3535 | 0.0077801 | 0.081918 | 10.5292 | 0.0023636 | 0.020842 | 8.818
Creek Road | 110 | 4.5212 | 5.5679 | 0.011281 | 0.10389 | 9.2092 | 0.011318 | 0.10622 | 9.3848 | 0.0058999 | 0.042842 | 7.2615
Creek Road | 33 | 6.3916 | 2.9819 | 0.013729 | 0.24599 | 17.9184 | 0.013766 | 0.24832 | 18.0391 | 0 | 1.0903 | >50
Derby | 110 | 1.7979 | 1.3132 | 0.049266 | 0.25834 | 5.2438 | 0.04945 | 0.26131 | 5.2843 | 0.15743 | 0.53057 | 3.3701
Derby | 22 | 3.0069 | 1.0103 | 0.069266 | 0.78274 | 11.3005 | 0.06945 | 0.78571 | 11.3133 | 0 | 5.4706 | >50
Derwent Bridge | 110 | 1.7014 | 1.5756 | 0.1002 | 0.25918 | 2.5865 | 0.10025 | 0.26156 | 2.6092 | 0.083667 | 0.33359 | 3.9872
Derwent Bridge | 22 | 2.9755 | 1.4417 | 0.1159 | 0.78558 | 6.7779 | 0.11595 | 0.78796 | 6.7959 | 0 | 3.345 | >50
Devonport | 110 | 2.085 | 1.8604 | 0.043682 | 0.22248 | 5.0931 | 0.043783 | 0.22434 | 5.1238 | 0.057481 | 0.30172 | 5.2491
Devonport | 22 | 6.0488 | 2.9619 | 0.025607 | 0.38967 | 15.2174 | 0.025708 | 0.39153 | 15.2301 | 0 | 1.6116 | >50
Electrona | 110 | 1.8799 | 1.3605 | 0.065288 | 0.24285 | 3.7197 | 0.065326 | 0.24518 | 3.7532 | 0.13072 | 0.52196 | 3.9929
Electrona | 11 | 6.9579 | 2.9634 | 0.048084 | 0.67725 | 14.0848 | 0.048121 | 0.67958 | 14.1222 | 0 | 3.4264 | >50
Emu Bay | 110 | 1.6425 | 1.4933 | 0.073456 | 0.27838 | 3.7897 | 0.073556 | 0.28024 | 3.8098 | 0.099528 | 0.35907 | 3.6077
Emu Bay | 11 | 6.2258 | 2.5545 | 0.041027 | 0.7577 | 18.4684 | 0.041128 | 0.75956 | 18.4684 | 0 | 4.0331 | >50
Farrell | 220 | 1.6619 | 2.2667 | 0.016872 | 0.14129 | 8.3741 | 0.016973 | 0.14315 | 8.4339 | 0.0032818 | 0.026158 | 7.9706
Farrell | 110 | 2.2595 | 3.0158 | 0.014192 | 0.20873 | 14.7072 | 0.014293 | 0.21059 | 14.7336 | 0.0023772 | 0.04975 | 20.9281
George Town | 220 | 2.832 | 3.7488 | 0.0082568 | 0.083028 | 10.0557 | 0.0084531 | 0.086443 | 10.2262 | 0.001632 | 0.018698 | 11.4569
George Town | 110 | 3.939 | 5.1127 | 0.0079657 | 0.11969 | 15.0252 | 0.0081523 | 0.12299 | 15.086 | 0.0013031 | 0.033998 | 26.0898
George Town | 22 | 3.9091 | 2.1447 | 0.016776 | 0.60412 | 36.0121 | 0.016962 | 0.60742 | 35.8105 | 0 | 2.095 | >50
Gordon | 220 | 1.2545 | 1.7498 | 0.024083 | 0.18714 | 7.7707 | 0.024121 | 0.18946 | 7.8546 | 0.00050108 | 0.025851 | >50
Gordon | 22 | 1.5966 | 0.09 | 0.085263 | 1.4791 | 17.3474 | 0.085301 | 1.4814 | 17.3668 | 0 | 0 | >50
Hadspen | 220 | 3.0761 | 3.7609 | 0.0075756 | 0.076435 | 10.0897 | 0.0077465 | 0.079566 | 10.2713 | 0.0045916 | 0.031395 | 6.8376
Hadspen | 110 | 4.1839 | 5.0344 | 0.011142 | 0.11238 | 10.0853 | 0.01133 | 0.11529 | 10.1755 | 0.0048326 | 0.052541 | 10.8722
Hadspen | 22 | 3.9683 | 2.1366 | 0.017648 | 0.59507 | 33.7185 | 0.017833 | 0.59804 | 33.5367 | 0 | 2.126 | >50
Hampshire | 110 | 2.0515 | 1.4894 | 0.051117 | 0.22468 | 4.3954 | 0.051218 | 0.22654 | 4.423 | 0.10768 | 0.47813 | 4.4404
Huon River | 110 | 1.6971 | 1.214 | 0.093402 | 0.26246 | 2.8101 | 0.093439 | 0.26479 | 2.8338 | 0.16852 | 0.58686 | 3.4824
Huon River | 11 | 5.9706 | 2.8492 | 0.1093 | 0.78367 | 7.1697 | 0.10934 | 0.78599 | 7.1886 | 0 | 3.4017 | >50
Kermandie | 110 | 1.9946 | 1.4185 | 0.072392 | 0.22565 | 3.1171 | 0.072429 | 0.22798 | 3.1476 | 0.13261 | 0.5075 | 3.827
Kermandie | 11 | 3.903 | 5.0529 | 0.12459 | 1.2042 | 9.6648 | 0.12463 | 1.2065 | 9.6806 | 0.0738 | 0.3757 | 5.0908
Kingston | 110 | 3.1048 | 2.5845 | 0.029323 | 0.14934 | 5.0931 | 0.02936 | 0.15167 | 5.1658 | 0.045716 | 0.23754 | 5.196
Kingston | 33 | 2.9926 | 0.86331 | 0.029287 | 0.52557 | 17.9453 | 0.029324 | 0.52789 | 18.0019 | 0 | 4.4475 | >50
Kingston | 11 | 6.0019 | 2.4759 | 0.042787 | 0.78597 | 18.3692 | 0.042824 | 0.78829 | 18.4076 | 0 | 4.1526 | >50
Knights Rd | 110 | 2.1039 | 1.555 | 0.061077 | 0.21621 | 3.5399 | 0.061114 | 0.21853 | 3.5758 | 0.11864 | 0.44527 | 3.7531
Knights Rd | 11 | 4.3691 | 1.4723 | 0.045792 | 1.0804 | 23.5946 | 0.045829 | 1.0828 | 23.6262 | 0 | 7.4793 | >50
Liapootah | 220 | 2.6361 | 3.3462 | 0.0089077 | 0.089199 | 10.0137 | 0.0089471 | 0.091519 | 10.229 | 0.0027849 | 0.030093 | 10.8057
Lindisfarne | 220 | 2.116 | 2.6419 | 0.010525 | 0.11121 | 10.5665 | 0.010563 | 0.11353 | 10.7479 | 0.0047669 | 0.042351 | 8.8844
Lindisfarne | 110 | 4.3522 | 4.9361 | 0.010994 | 0.108 | 9.8238 | 0.01103 | 0.11033 | 10.0019 | 0.011365 | 0.066866 | 5.8837
Lindisfarne | 33 | 3.3817 | 1.048 | 0.018 | 0.474 | 26.382 | 0.018 | 0.476 | 26.2049 | 0 | 3.642 | >50
Meadowbank | 110 | 2.656 | 2.9879 | 0.036484 | 0.17415 | 4.7733 | 0.036519 | 0.17649 | 4.833 | 0.01374 | 0.11582 | 8.4291
Meadowbank | 22 | 3.5989 | 3.0023 | 0.050329 | 0.65454 | 13.0052 | 0.050365 | 0.65689 | 13.0426 | 0 | 1.0475 | >50
Mornington | 110 | 3.8835 | 3.7298 | 0.013788 | 0.12088 | 8.7672 | 0.013825 | 0.12321 | 8.9116 | 0.024165 | 0.13241 | 5.4795
Mornington | 33 | 3.1871 | 0.87363 | 0.020219 | 0.49382 | 24.4239 | 0.020256 | 0.49615 | 24.4936 | 0 | 4.4456 | >50
Mowbray | 110 | 3.4825 | 3.293 | 0.014318 | 0.13492 | 9.4232 | 0.014503 | 0.13789 | 9.5083 | 0.031384 | 0.15343 | 4.8887
Mowbray | 22 | 3.9061 | 1.1902 | 0.021613 | 0.60443 | 27.9656 | 0.021797 | 0.6074 | 27.8655 | 0 | 4.7583 | >50
New Norfolk | 110 | 3.9148 | 3.8394 | 0.017992 | 0.11934 | 6.6329 | 0.018029 | 0.12167 | 6.7489 | 0.021667 | 0.12363 | 5.7061
New Norfolk | 22 | 3.1078 | 1.5224 | 0.034599 | 0.75951 | 21.9514 | 0.034636 | 0.76184 | 21.9959 | 0 | 3.1405 | >50
Newton | 110 | 2.1408 | 2.1429 | 0.024253 | 0.21949 | 9.0501 | 0.024353 | 0.22135 | 9.089 | 0.049588 | 0.21365 | 4.3084
Newton | 11 | 5.5376 | 0.17927 | 0.052953 | 0.85149 | 16.0802 | 0.053053 | 0.85335 | 16.0847 | 78.7191 | 4.6116 | 0.058583
Newton | 22 | 2.7528 | 1.1653 | 0.052953 | 0.85679 | 16.1803 | 0.053053 | 0.85865 | 16.1846 | 0 | 4.3822 | >50
North Hobart | 110 | 4.5704 | 5.5595 | 0.012249 | 0.10264 | 8.3801 | 0.012286 | 0.10497 | 8.5441 | 0.010633 | 0.044878 | 4.2205
North Hobart | 11 | 4.5691 | 3.0472 | 0.020644 | 1.0338 | 50.0796 | 0.020681 | 1.0362 | 50.1022 | 0 | 2.5824 | >50
Norwood | 110 | 4.149 | 4.7607 | 0.011808 | 0.11326 | 9.5922 | 0.011992 | 0.11623 | 9.6925 | 0.010642 | 0.066224 | 6.2227
Norwood | 22 | 3.3049 | 1.4164 | 0.0292 | 0.71432 | 24.463 | 0.029384 | 0.71729 | 24.4107 | 0 | 3.5806 | >50
Palmerston | 220 | 3.2896 | 4.2638 | 0.0060177 | 0.071571 | 11.8933 | 0.0061691 | 0.07468 | 12.1056 | 0.0019555 | 0.019361 | 9.9008
Palmerston | 110 | 4.6124 | 5.7672 | 0.010104 | 0.10193 | 10.0883 | 0.010263 | 0.10472 | 10.2034 | 0.0028406 | 0.037997 | 13.3766
Palmerston | 22 | 3.7637 | 1.3483 | 0.02942 | 0.62703 | 21.3128 | 0.02958 | 0.62985 | 21.2933 | 0 | 4.0097 | >50
Paloona | 110 | 1.5112 | 1.9192 | 0.079508 | 0.30271 | 3.8073 | 0.079609 | 0.30457 | 3.8258 | 0.015955 | 0.11068 | 6.9369
Pieman | 220 | 1.7202 | 2.3085 | 0.016396 | 0.13648 | 8.324 | 0.016497 | 0.13834 | 8.3858 | 0.0023742 | 0.030286 | 12.7563
Port Latta | 110 | 1.4494 | 1.0732 | 0.12707 | 0.31731 | 2.4972 | 0.12744 | 0.3198 | 2.5094 | 0.2176 | 0.66474 | 3.0548
Port Latta | 22 | 3.922 | 1.497 | 0.094589 | 0.59881 | 6.3307 | 0.09624 | 0.60024 | 6.3434 | 0 | 3.56 | >50
Que | 110 | 2.0465 | 2.0257 | 0.038632 | 0.22775 | 5.8953 | 0.038733 | 0.22961 | 5.928 | 0.066562 | 0.22778 | 3.422
Que | 22 | 2.8239 | 1.3517 | 0.056932 | 0.83485 | 14.6639 | 0.057033 | 0.83671 | 14.6706 | 0 | 3.5806 | >50
Queenstown | 110 | 1.6859 | 1.5274 | 0.03211 | 0.2787 | 8.6794 | 0.032211 | 0.28056 | 8.71 | 0.075467 | 0.35932 | 4.7613
Queenstown | 22 | 2.9332 | 1.0086 | 0.05211 | 0.8039 | 15.4269 | 0.052211 | 0.80576 | 15.4327 | 0 | 5.4421 | >50
Queenstown | 11 | 5.8791 | 2.8053 | 0.04745 | 0.80217 | 16.9055 | 0.047551 | 0.80403 | 16.9088 | 0 | 3.4471 | >50
Railton | 110 | 3.2489 | 3.1632 | 0.017664 | 0.14437 | 8.1729 | 0.017765 | 0.14623 | 8.2311 | 0.040901 | 0.151 | 3.692
Railton | 22 | 3.467 | 1.551 | 0.028159 | 0.68088 | 24.1797 | 0.02826 | 0.68274 | 24.1592 | 0 | 3.2121 | >50
Risdon | 110 | 4.4721 | 5.109 | 0.010457 | 0.10513 | 10.0531 | 0.010495 | 0.10745 | 10.2386 | 0.010161 | 0.063085 | 6.2088
Risdon | 33 | 5.2486 | 2.3775 | 0.014325 | 0.2997 | 20.9212 | 0.014363 | 0.30203 | 21.0288 | 0 | 1.3863 | >50
Risdon | 11 | 10.2523 | 2.5401 | 0.016665 | 0.44429 | 26.6594 | 0.016703 | 0.44661 | 26.7392 | 4.8518 | 1.3714 | 0.28265
Rokeby | 110 | 3.7037 | 3.2306 | 0.014955 | 0.12669 | 8.4715 | 0.014993 | 0.12902 | 8.6054 | 0.034115 | 0.17839 | 5.229
Rokeby | 11 | 5.9302 | 2.4763 | 0.036855 | 0.79579 | 21.5923 | 0.036893 | 0.79812 | 21.6334 | 0 | 4.1322 | >50
Rosebery | 110 | 2.686 | 3.264 | 0.019742 | 0.17484 | 8.8561 | 0.019843 | 0.1767 | 8.9048 | 0.018517 | 0.078855 | 4.2586
Rosebery | 44 | 2.7436 | 1.3724 | 0.027622 | 0.42976 | 15.5583 | 0.027723 | 0.43162 | 15.5688 | 0 | 1.725 | >50
Rosebery | 22 | 2.1462 | 1.7837 | 0.0844 | 1.0981 | 13.011 | 0.084501 | 1.1 | 13.0174 | 0 | 1.7755 | >50
Savage River | 110 | 1.1826 | 0.88104 | 0.097782 | 0.38813 | 3.9693 | 0.097883 | 0.38999 | 3.9843 | 0.1843 | 0.79109 | 4.2923
Savage River | 22 | 2.892 | 1.37 | 0.12478 | 0.80743 | 6.4707 | 0.12488 | 0.80929 | 6.4804 | 0 | 3.5599 | >50
Scottsdale | 110 | 1.7747 | 1.3162 | 0.05755 | 0.26014 | 4.5203 | 0.057734 | 0.26311 | 4.5573 | 0.15021 | 0.52207 | 3.4756
Scottsdale | 22 | 5.3186 | 2.7898 | 0.04545 | 0.4418 | 9.7206 | 0.045634 | 0.44477 | 9.7464 | 0 | 1.6529 | >50
Sheffield | 220 | 2.2995 | 3.0783 | 0.013385 | 0.1019 | 7.6133 | 0.013484 | 0.10376 | 7.6946 | 0.0028714 | 0.022672 | 7.8959
Sheffield | 110 | 3.5171 | 4.4746 | 0.012745 | 0.13374 | 10.4935 | 0.012846 | 0.1356 | 10.5559 | 0.0039875 | 0.046031 | 11.5439
Sheffield | 22 | 4.176 | 1.1107 | 0.03075 | 0.62917 | 20.4611 | 0.030821 | 0.63109 | 20.476 | 0 | 5.8676 | >50
Smithton | 110 | 1.1171 | 0.852 | 0.17271 | 0.37588 | 2.2343 | 0.17308 | 0.38837 | 2.2439 | 0.028146 | 0.85349 | 3.0324
Smithton | 22 | 3.3159 | 3.4629 | 0.10769 | 0.73923 | 6.8642 | 0.10807 | 0.74172 | 6.8633 | 0 | 0.6541 | >50
Sorell | 110 | 2.6469 | 2.0455 | 0.037585 | 0.17454 | 4.644 | 0.037622 | 0.17687 | 4.7012 | 0.065345 | 0.32752 | 5.0122
Sorell | 22 | 3.3817 | 1.1915 | 0.044385 | 0.69724 | 15.7091 | 0.044422 | 0.69957 | 15.7482 | 0 | 4.5662 | >50
St Leonards | 110 | 3.5823 | 4.1172 | 0.014363 | 0.13112 | 9.1286 | 0.014547 | 0.13408 | 9.2171 | 0.013926 | 0.076396 | 5.4859
St Leonards | 22 | 3.7528 | 1.0345 | 0.017853 | 0.62929 | 35.2475 | 0.018038 | 0.63226 | 35.0521 | 0 | 5.6136 | >50
St Marys | 110 | 0.83714 | 0.56354 | 0.25896 | 0.50314 | 1.9429 | 0.25912 | 0.50596 | 1.9526 | 0.43408 | 1.3383 | 3.0831
St Marys | 22 | 1.6167 | 2.1676 | 0.32456 | 1.4261 | 4.3941 | 0.32472 | 1.429 | 4.4006 | 0 | 0.3508 | >50
Starwood | 110 | 3.8501 | 4.3212 | 0.015776 | 0.1217 | 7.7146 | 0.015962 | 0.125 | 7.8311 | 0.019053 | 0.077345 | 4.0594
Tarraleah | 110 | 3.0859 | 4.1311 | 0.032532 | 0.14963 | 4.5994 | 0.032576 | 0.15201 | 4.6663 | 0.0018018 | 0.034875 | 19.3556
Temco | 110 | 4.0718 | 4.6827 | 0.011236 | 0.11549 | 10.2792 | 0.011422 | 0.11879 | 10.4001 | 0.010963 | 0.066525 | 6.0679
Trevallyn | 110 | 4.1273 | 5.0631 | 0.011155 | 0.11393 | 10.2132 | 0.01134 | 0.1169 | 10.3091 | 0.0031767 | 0.047921 | 15.0853
Trevallyn | 22 | 6.798 | 3.0845 | 0.014943 | 0.34715 | 23.2318 | 0.015127 | 0.35012 | 23.1452 | 0 | 1.6007 | >50
Triabunna | 110 | 1.1792 | 0.86818 | 0.2443 | 0.31798 | 1.3016 | 0.24434 | 0.32031 | 1.3109 | 0.31902 | 0.78475 | 2.4598
Triabunna | 22 | 2.6832 | 1.2291 | 0.2643 | 0.83998 | 3.1782 | 0.26434 | 0.84231 | 3.1865 | 0 | 4.0723 | >50
Tungatinah | 110 | 2.8593 | 3.8744 | 0.03582 | 0.16134 | 4.5042 | 0.035866 | 0.16374 | 4.5652 | 0.0013267 | 0.033409 | 25.1819
Tungatinah | 22 | 3.4672 | 1.1427 | 0.052352 | 0.67941 | 12.9777 | 0.052396 | 0.68179 | 13.0122 | 0 | 4.8574 | >50
Ulverstone | 110 | 1.8846 | 1.7497 | 0.056328 | 0.24445 | 4.3397 | 0.056429 | 0.24631 | 4.3649 | 0.075563 | 0.29778 | 3.9409
Ulverstone | 22 | 3.8004 | 1.6083 | 0.042446 | 0.62019 | 14.6113 | 0.042547 | 0.62205 | 14.6203 | 0 | 3.1694 | >50
Waddamana | 220 | 2.8432 | 3.6103 | 0.0071218 | 0.082804 | 11.6269 | 0.0071609 | 0.085125 | 11.8874 | 0.0033298 | 0.027598 | 8.2881
Waddamana | 110 | 2.8819 | 2.656 | 0.031581 | 0.1609 | 5.095 | 0.031633 | 0.16335 | 5.1638 | 0.034892 | 0.20045 | 5.7448
Waddamana | 22 | 1.4145 | 1.7872 | 0.16748 | 1.6643 | 9.9378 | 0.16753 | 1.6668 | 9.9493 | 0 | 0.624 | >50
Warratah Tee | 110 | 1.4862 | 1.2224 | 0.068492 | 0.31081 | 4.5379 | 0.068593 | 0.31267 | 4.5583 | 0.12568 | 0.50805 | 4.0423
Wesley Vale | 110 | 2.4474 | 1.9493 | 0.031982 | 0.19045 | 5.9548 | 0.032083 | 0.19231 | 5.994 | 0.060761 | 0.33407 | 5.4982
Wesley Vale | 22 | 2.9945 | 1.1919 | 0.050274 | 0.78748 | 15.6636 | 0.050375 | 0.78934 | 15.6691 | 0 | 4.384 | >50
Notes on above minimum fault levels 1. Boyer 6.6 kV, Arthur's Lake — Fault level calculation excludes current contribution from synchronous motors. 2. Bridgewater 11 kV — Fault level calculation made with 11 kV bus coupler open (normal operation). 3. Mowbray 22 kV — Fault level calculation made with 22 kV Trevallyn–Mowbray super feeders out of service (normal operation). 4. Rokeby 11 kV — Fault level calculation made with 11 kV bus coupler open (normal operation). 5. Trevallyn 22 kV — Fault level calculation made with 22 kV Trevallyn–Mowbray super feeders out of service (normal operation). 6. Emu Bay 11 kV, Kingston 11 kV and Electrona 11 kV bus couplers are normally open. 7. The reactors installed on feeders from Emu Bay Substation to reduce maximum fault level (see notes in 'Maximum' tab) also reduce the minimum fault level. The minimum fault currents on the feeders with the reactors in service and bus coupler closed are listed in the Emu Bay tab.
8
Bus | Voltage | Fault Level (kA) |  | Sequence Impedances in PU
Name [feeder number] | [kV] | 3 phase | 1 phase to ground | Positive |  |  | Negative |  |  | Zero
|  |  |  | R | X | X/R | R | X | X/R | R | X | X/R
Emu Bay [19] | 11 | 4.9229 | 2.3031 | 0.039817 | 0.9591 | 24.0874 | 0.039166 | 0.9434 | 24.0872 | 2.6043e-16 | 4.2514 | >50
Emu Bay [20] | 11 | 5.0108 | 2.3222 | 0.039817 | 0.94223 | 23.6638 | 0.039166 | 0.92654 | 23.6566 | 2.594e-16 | 4.2345 | >50
Emu Bay [21] | 11 | 5.0108 | 2.3222 | 0.039817 | 0.94223 | 23.6638 | 0.039166 | 0.92654 | 23.6566 | 2.594e-16 | 4.2345 | >50
Emu Bay [23] | 11 | 5.0108 | 2.3222 | 0.039817 | 0.94223 | 23.6638 | 0.039166 | 0.92654 | 23.6566 | 2.594e-16 | 4.2345 | >50
Emu Bay [24] | 11 | 4.9414 | 2.3073 | 0.049738 | 0.95503 | 19.2012 | 0.049087 | 0.93933 | 19.1362 | 0.0099208 | 4.2473 | >50