## info
TasNetworks Materials and Assemblies Document
Materials List
All materials for installation and construction work are to be procured by the Developer or its contractors and must be in accordance with TasNetworks’ Materials and Assemblies document. All materials and goods must be new, free from defects, of merchantable quality, fit for the specified purpose, and conform fully to the requirements of TasNetworks. To ensure the maintenance of appropriate reliability and safety standards during the transition period to contestability, TasNetworks’ Materials List will have the following three categories of materials: 1. Prescribed Materials –These items must be from the specified manufacturer and have the listed part number in TasNetworks' Materials and Assemblies document. Kiosk substations and Switching stations are Prescribed materials and must be ordered in accordance with the Kiosk Ordering Guide (KOG). Kiosk and Switching stations are pre-installation inspection material. 2. Approved Materials – For each type of material or good in this category, product details including manufacturer and part number are specified together with a known supplier. A process will be developed for TasNetworks to assess the suitability of additional products. If a product is assessed as meeting TasNetworks’ requirements (including being of sufficient quality and compatible with the distribution network), they will be added to the Approved Materials category in TasNetworks' Materials and Assemblies List. Further information including timelines and associated fees will be released at a later date. 3. Consumable Materials – TasNetworks preference is for these items to be purchased from the listed vendor. Alternative vendors may be used but these items must be equivalent to those in the materials list and comply with all relevant Australian Standards. Example items that do not have to be purchased from an approved vendor include PVC electrical insulation tape, nuts, bolts and washers.
Assemblies
The TasNetworks approved materials list consists of parts that have been grouped into standard assemblies (e.g. turret or cabinet assemblies), which can be referenced by the designer to indicate required materials. It is recommended that the designer make reference to these assemblies for standard arrangements throughout the design. Note there may be cases where additional components are required to complete an assembly. TasNetworks accepts no liability for the accuracy of the standard assemblies, and it is the responsibility of the developer to check and ensure accuracy for the bill of materials, to ensure correct equipment and quantities are ordered for construction.

## Materials List
Category | Type | Type Desc | SI No. | Description | Technical Description | Manufacturer Part No. | Manufacturer | Vendor name | Aus Std | Minimum Required Warranty Period | Pre-Installation Inspection Required
cable | 2 | Approved | 083810 | Cable 11kV Al 3c 185mm2 a x shc pvc hdpe - TR (HD Screens) | 3 CORE,185 SQMM,6.35/11KV,AL, COMPACTED,XLPE-TR,HEAVY DUTY COPPER WIRE SCREENED,PVC/HDPE SHEATHED,TO AS 1429 & 4026 | 5083217 | PRYSMIAN | PRYSMIAN POWER CABLES & SYSTEMS AUSTRALIA PTY LTD |  | 5 years | Yes
cable | 2 | Approved | 083811 | Cable 11kV Al 3c 240mm2 a x shc pvc hdpe - TR (HD Screens) | 3 CORE,240 SQMM,6.35/11KV,AL, COMPACTED,XLPE-TR,HEAVY DUTY COPPERWIRE SCREENED,PVC/HDPE SHEATHED,TO AS 1429 & 4026 | 5082135 | PRYSMIAN | PRYSMIAN POWER CABLES & SYSTEMS AUSTRALIA PTY LTD |  | 5 years | Yes
cable | 2 | Approved | 085701 | Cable 22kV Al 3c 185mm2 a x shc pvc hdpe - TR (HD Screens) | 3 CORE,185 SQMM,12.7/22KV,AL, COMPACTED,XLPE-TR,HEAVY DUTY COPPERWIRE SCREENED,PVC/HDPE SHEATHED,TO AS 1429 & 4026 | 5082708 | PRYSMIAN | PRYSMIAN POWER CABLES & SYSTEMS AUSTRALIA PTY LTD |  | 5 years | Yes
cable | 2 | Approved | 085702 | Cable 22kV Al 3c 240mm2 a x shc pvc hdpe - TR (HD Screens) | 3 CORE,240 SQMM,12.7/22KV,AL, COMPACTED,XLPE-TR,HEAVY DUTY COPPERWIRE SCREENED,PVC/HDPE SHEATHED,TO AS 1429 & 4026 | 5082180 | PRYSMIAN | PRYSMIAN POWER CABLES & SYSTEMS AUSTRALIA PTY LTD |  | 5 years | Yes
cable | 2 | Approved | 103008 | Cable LV Al 4c 150mm2 a x pvc | 4 CORE,150 SQMM,0.6/1 KV, ALUMINIUM,XLPE,500 M DRUM,TO AS 3560 | 5013788 | PRYSMIAN | PRYSMIAN POWER CABLES & SYSTEMS AUSTRALIA PTY LTD |  | 12 months | No
cable | 2 | Approved | 082671 | Cable LV Al 4c 185mm2 sa x pvc | 4 CORE,185 SQMM,0.6/1 KV,XLPE INSULATED,ALUMINIUM,SOLID SECTOR SHAPED,PVC SHEATHERED,TO AS 4026,250M DRUM | 5013269 | PRYSMIAN | PRYSMIAN POWER CABLES & SYSTEMS AUSTRALIA PTY LTD |  | 5 years | Yes
cable | 2 | Approved | 082670 | Cable LV Al 4c 240mm2 a x pvc | 4 CORE,240 SQMM,0.6/1 KV,XLPE INSULATED,ALUMINIUM,STRANDED SECTOR SHAPED,PVC SHEATHED,TO AS 4026,250M DRUM | 5099454 | PRYSMIAN | PRYSMIAN POWER CABLES & SYSTEMS AUSTRALIA PTY LTD |  | 5 years | Yes
cable | 2 | Approved | 082667 | Cable LV Al 4c 300mm2 a x pvc | 4 CORE,300 SQMM,0.6/1 KV,XLPE INSULATED,ALUMINIUM,STRANDED SECTOR SHAPED,PVC SHEATHED,TO AS 4026,250M DRUMS | 5026290 | PRYSMIAN | PRYSMIAN POWER CABLES & SYSTEMS AUSTRALIA PTY LTD |  | 5 years | Yes
cable | 2 | Approved | 082668 | Cable LV Al 4c 400mm2 a x pvc | 4 CORE,400 SQMM,0.6/1 KV,XLPE INSULATED,ALUMINIUM,STRANDED SECTOR SHAPED,PVC SHEATHED,TO AS 4026 | 5026481 | PRYSMIAN | PRYSMIAN POWER CABLES & SYSTEMS AUSTRALIA PTY LTD |  | 5 years | Yes
cable | 2 | Approved | 095070 | Cable LV Cu 1c 70mm2 c x pvc | 70 SQMM,1 CORE,0.6/1 KV,ANNEALED COPPER,XLPE INSULATION,DOUBLE INSULATED,PVC SHEATHED,BLACK,100M DRUM TO AS 5000 | 5012781 | PRYSMIAN | PRYSMIAN POWER CABLES & SYSTEMS AUSTRALIA PTY LTD |  | 5 years | No
cable | 2 | Approved | 095120 | Cable LV Cu 1c 120mm2 c x pvc | 120 SQMM,ANNEALED COPPER,XLPE INSULATED,DOUBLE INSULATED,PVC SHEATHED,BLACK,100M DRUM,TO AS 5000 | 5012552 | PRYSMIAN | PRYSMIAN POWER CABLES & SYSTEMS AUSTRALIA PTY LTD |  | 5 years | No
cable | 2 | Approved | 094195 | Cable LV Cu 1c 150mm2 c x pvc | BUILDING,ANNEALED COPPER,150 SQMM,37/2.25 MM,0.6/1 KV,V-90 XLPE,WITH 1% CARBON BLK,TO AS 5000,BLACK,100M DRUM | 5022100 | PRYSMIAN | PRYSMIAN POWER CABLES & SYSTEMS AUSTRALIA PTY LTD |  | 5 years | No
cable | 2 | Approved | 095185 | Cable LV Cu 1c 185mm2 c x pvc | 185 SQMM,ANNEALED COPPER,XLPE INSULATED,DOUBLE INSULATED,PVC SHEATHED,BLACK,100M DRUM,TO AS 5000 | 5012422 | PRYSMIAN | PRYSMIAN POWER CABLES & SYSTEMS AUSTRALIA PTY LTD |  | 5 years | No
cable | 2 | Approved | 095240 | Cable LV Cu 1c 240mm2 c x pvc | 240 SQMM,ANNEALED COPPER,XLPE INSULATED,DOUBLE INSULATED,PVC SHEATHED,BLACK,100M DRUM,TO AS 5000 | 5022117 | PRYSMIAN | PRYSMIAN POWER CABLES & SYSTEMS AUSTRALIA PTY LTD |  | 5 years | No
cable | 2 | Approved | 095715 | Cable LV ECC Cu 10mm2 twin (+ 4mm2 earth) circular | 10 SQMM,2 CORE+EARTH,CIRCULAR, V-90 INSULATED,PVC SHEATHED,TO AS/NZS 5000 | 5010787 | PRYSMIAN | PRYSMIAN POWER CABLES & SYSTEMS AUSTRALIA PTY LTD |  | 5 years | No
cable | 2 | Approved | 095714 | Cable LV ECC Cu 4mm2 twin (+ 2.5mm2 earth) circular | 4 SQMM,0.6/1 KV,7/0.85MM,ANNEALED COPPER,2 CORE+EARTH,ROUND,TO AS 5000,100M DRUM | 5058437 | PRYSMIAN | PRYSMIAN POWER CABLES & SYSTEMS AUSTRALIA PTY LTD |  | 5 years | No
cable | 2 | Approved | 095713 | Cable LV ECC Cu 2.5mm2 twin & earth circular | 2.5 SQMM,0.6/1 KV,7/0.67MM,2 CORE+ EARTH,ANNEALED COPPER,ORANGE, ROUND,TO AS 5000,100M DRUM | 5058390 | PRYSMIAN | PRYSMIAN POWER CABLES & SYSTEMS AUSTRALIA PTY LTD |  | 5 years | No
cable | 2 | Approved | 094170 | Wire Electrical Cu 10mm2 1c Red | BUILDING,ANNEALED COPPER,10 SQMM, 7/1.35 MM, 0.6/1 KV, RED | 5010466 | PIRELLI | PRYSMIAN POWER CABLES & SYSTEMS AUSTRALIA PTY LTD |  | 12 months | No
cable | 2 | Approved | 094433 | Wire Electrical Cu 120mm2 1c Green/Yellow | BUILDING,ANNEALED COPPER, 120 SQMM, 37/2.03 MM,0.6/1 KV,GREEN/YELLOW 100M DRUM | 5010053 | PRYSMIAN | PRYSMIAN POWER CABLES & SYSTEMS AUSTRALIA PTY LTD |  | 5 years | No
cable | 2 | Approved | 095021 | Wire Electrical Cu 2.5mm2 1c Red (PVC/PVC) | 1 CORE,2.5 SQMM,7/0.67 MM,0.6/1 KV,COPPER,ANNEALED,RED WITH WHITE OUTER SHEATH,TO AS 5000,100M DRUM | 5010572 | PRYSMIAN | PRYSMIAN POWER CABLES & SYSTEMS AUSTRALIA PTY LTD |  | 5 years | No
cable | 2 | Approved | 095020 | Wire Electrical Cu 2.5mm2 1c Black (PVC/PVC) | 1 CORE,2.5 SQMM,7/0.67 MM,0.6/1 KV,COPPER,ANNEALED,BLACK WITH WHITE OUTER SHEATH,100M DRUM | 5011425 | PRYSMIAN | PRYSMIAN POWER CABLES & SYSTEMS AUSTRALIA PTY LTD |  | 5 years | No
cable | 2 | Approved | 094187 | Wire Electrical Cu 35mm2 1c (V-90 PVC) - Black | BUILDING,ANNEALED COPPER,35 SQMM, 19/1.53 MM,0.6/1 KV,V-90 PVC INULATED, BLACK,TO AS 5000,100M DRUM | 5010725 | PRYSMIAN | PRYSMIAN POWER CABLES & SYSTEMS AUSTRALIA PTY LTD |  | 5 years | No
cable | 2 | Approved | 094178 | Wire Electrical Cu 35mm2 1c (V-90 PVC) - Green/Yellow | BUILDING,ANNEALED COPPER,35 SQMM,19/1.53 MM,0.6/1 KV,V-90 PVC INSULATED,GREEN/YELLOW,TO AS 5000,100M DRUM | 5010541 | PRYSMIAN | PRYSMIAN POWER CABLES & SYSTEMS AUSTRALIA PTY LTD |  | 5 years | No
cable | 2 | Approved | 094161 | Wire Electrical Cu 35mm2 1c (V-90 PVC) - Red | BUILDING, ANNEALED COPPER 35SQMM, 19/1.53MM, 0.6/1 KV, V-90 PVC INSULATED, RED,TO AS5000, 100MTR DRUM | 5010480 | PRYSMIAN | PRYSMIAN POWER CABLES & SYSTEMS AUSTRALIA PTY LTD |  | 5 years | No
cable | 2 | Approved | 094180 | Wire Electrical Cu 50mm2 1c Black | BUILDING,ANNEALED COPPER,50 SQMM, 19/1.78 MM,0.6/1 KV,V-90 PVC INSULATED,WITH 1% CARBON BLK,BLACK,100M DRUM | 5010763 | PRYSMIAN | PRYSMIAN POWER CABLES & SYSTEMS AUSTRALIA PTY LTD |  | 5 years | No
cable | 2 | Approved | 094182 | Wire Electrical Cu 50mm2 1c Red | BUILDING,ANNEALED COPPER,50 SQMM, 19/1.78 MM, 0.6/1 KV, RED 100Mtr Drums | 5013238 | PRYSMIAN | PRYSMIAN POWER CABLES & SYSTEMS AUSTRALIA PTY LTD |  | 5 years | No
cable | 2 | Approved | 094184 | Wire Electrical Cu 70mm2 1c Black | BUILDING,ANNEALED COPPER,70 SQMM, 19/2.14 MM,0.6/1 KV,V-90 PVC INSULATED,WITH 1% CARBON BLK,BLACK,100 M DRUM | 5014730 | PRYSMIAN | PRYSMIAN POWER CABLES & SYSTEMS AUSTRALIA PTY LTD |  | 5 years | No
cable | 2 | Approved | 094240 | Wire Electrical Cu 70mm2 1c Green/Yellow | BUILDING,ANNEALED COPPER,70 SQMM,0.6/1KV,GREEN/YELLOW,PVC V90 INSULATED,100M DRUM | 5010398 | PRYSMIAN | PRYSMIAN POWER CABLES & SYSTEMS AUSTRALIA PTY LTD |  | 5 years | No
cable | 2 | Approved | 094185 | Wire Electrical Cu 70mm2 1c Red | BUILDING,ANNEALED COPPER,70 SQMM, 19/2.14 MM, 0.6/1 KV, RED | 5011180 | PRYSMIAN | PRYSMIAN POWER CABLES & SYSTEMS AUSTRALIA PTY LTD |  | 5 years | No
conduit | 3 | Consumables | 153994 | Conduit Coupler 32mm Orange | PVC,ORANGE,32 MM PLAIN,TO AS 2053 | 242/32EO | CLIPSAL | REXEL | AS 2053 | 12 months | No
conduit | 3 | Consumables | 153996 | Conduit Coupler 50mm Orange | PVC,ORANGE,50 MM PLAIN,TO AS 2053 | 242/50 | CLIPSAL | REXEL | AS 2053 | 12 months | No
conduit | 3 | Consumables | 152823 | Conduit Adapter 25mm grey | SCREWED TO PLAIN,PVC,GREY,25 MM,TO AS 2053 | LANAPSHD25 | LANSON | REXEL | AS 2053 | 12 months | No
conduit | 3 | Consumables | 154480 | Conduit Locknut 20mm | NYLON,BLACK,HEX,20 MM INTERNAL THDSIZE,TO AS 2053 | 259/20 | CLIPSAL | REXEL | AS 2053 | 12 months | No
conduit | 3 | Consumables | 154481 | Conduit Locknut 25mm | NYLON,BLACK,HEX,25 MM INTERNAL THDSIZE,TO AS 2053 | LANLN25 | LANSON | REXEL | AS 2053 | 12 months | No
conduit | 3 | Consumables | 152924 | Conduit PVC Bend 32mm large sweep | 90 DEG,PVC,ORANGE,32 MM,HVY DUTY,LARGESWEEP,TO AS 2053 | 257L32EO | CLIPSAL | REXEL | AS 2053 | 12 months | No
conduit | 3 | Consumables | 152926 | Conduit PVC Bend 50mm large sweep | 90 DEG,PVC,ORANGE,50 MM,HVY DUTY,LARGESWEEP,TO AS 2053 | 247L50EO | CLIPSAL | REXEL | AS 2053 | 12 months | No
conduit | 3 | Consumables | 152745 | Conduit Rigid 32mm orange UPVC (per 4m Length) | PVC,ORANGE,32 MM,4 M LG,HVY DUTY,TO AS 2053 | 32HD | KEY | REXEL | AS 2053 | 12 months | No
conduit | 3 | Consumables | 152747 | Conduit Rigid 50mm orange UPVC (per 4m Length) | PVC,ORANGE,50 MM,4 M LG,HVY DUTY,TO AS 2053 | 50HD | KEY | REXEL | AS 2053 | 12 months | No
conduit | 3 | Consumables | 243988 | Pipe 100NB 6m orange UPVC class4.5 | UPVC,ORANGE,INT SOCKET ENDS,100 MM NB,6 M LG,CLASS 6,U/GROUND CABLE,AS 1477 | KEPP4001006 | KEY | REXEL | AS 1477 | 12 months | No
conduit | 3 | Consumables | 243989 | Pipe PVC 125NB x 6m orange class 4.5 | UPVC,ORANGE,INT SOCKET ENDS,125 MM NB,6 M LG,CLASS 6,U/GROUND CABLE,AS 1477 | P4001256 | KEY | REXEL | AS 1477 | 12 months | No
conduit | 3 | Consumables | 243990 | Pipe PVC 150NB x 6m orange class 4.5 | UPVC,ORANGE,INT SOCKET ENDS,150 MM NB,6 M LG,CLASS 6,U/GROUND CABLE,AS 1477 | P4001506 | KPLAST | REXEL | AS 1477 | 12 months | No
Conduit | 3 | Consumables | 152724 | Flexible Conduit 25mm | PVC,GREY,25 MM,4 M LG,LT DUTY,TO AS 2053 | 25MD | KEY | REXEL | AS 2053 | 12 months | No
conduit | 3 | Consumables | 152631 | Conduit Flexible Corr 25mm grey | UPVC,LIGHT GREY,25 MM DIA,MED DUTY,CORRUGATED,TO AS 2053,50 METRE COIL | LANCCM2550 | LANSON | REXEL | AS 2053 | 12 months | No
connectors | 2 | Approved | 141346 | Lug Crimp 10mm2 Copper M10 | EYE TYPE,CRIMP CONNECTION,10 SQMM,M10 HOLE,COPPER,UTILUX H1406B | H1406B/50 | TYCO | TYCO ELECTRONICS - ENERGY DIV. |  | 24 months | No
connectors | 2 | Approved | 141371 | Lug Crimp 120mm2 tinned copper M12 | EYE TYPE,CRIMP CONNECTION,120 SQMM,M12 HOLE,COPPER | EPTCU-120-16.5AF-M12 | PLP | PREFORMED LINE PRODUCTS (AUST) |  | 12 months | No
connectors | 2 | Approved | 141337 | Lug Crimp 2.5mm2 tinned copper M6 | EYE TYPE,CRIMP CONNECTION,2.5 SQMM,M6 HOLE,COPPER,BOX OF 100. | H1437 | UTILUX | TYCO ELECTRONICS - ENERGY DIV. |  | 12 months | No
connectors | 2 | Approved | 141358 | Lug Crimp 35mm2 tinned copper M10 | EYE TYPE,CRIMP CONNECTION,35 SQMM,M10 HOLE,COPPER | EPTCU-35-9.2AF-M10 | PLP | PREFORMED LINE PRODUCTS (AUST) |  | 12 months | No
connectors | 2 | Approved | 141363 | Lug Crimp 70mm2 tinned copper | EYE TYPE,CRIMP CONNECTION,70 SQMM,M12 HOLE,COPPER | EPTCU-7-11.5AF-M12 | PLP | PREFORMED LINE PRODUCTS (AUST) |  | 12 months | No
connectors | 2 | Approved | 141367 | Lug Crimp 95mm2 tinned copper M12 | EYE TYPE,CRIMP CONNECTION,95 SQMM,M12 HOLE,COPPER | EPTCU-95-14.2AF-M12 | PLP | PREFORMED LINE PRODUCTS (AUST) |  | 12 months | No
connectors | 2 | Approved | 152475 | Lug Crimp Al 300mm2 M12 | EYE TYPE,CRIMP CONNECTION,300 SQMM,M12HOLE,ALUMINIUM,PRE-FILLED | H15159/1 | TYCO | TYCO ELECTRONICS - ENERGY DIV. |  | 24 months | No
connectors | 2 | Approved | 152474 | Lug Crimp Aluminium 185mm2 M12 4c solid Sector | EYE TYPE,CRIMP CONNECTION,185 SQMM,M12HOLE,ALUMINIUM,4 CORE SOLID SECTOR | AG4H185M12/1 | TYCO | TYCO ELECTRONICS - ENERGY DIV. |  | 24 months | No
connectors | 2 | Approved | 152466 | Lug Crimp Aluminium 240mm2 M12 4c Sector | EYE TYPE,CRIMP CONNECTION,240 SQMM,M12 HOLE,ALUMINIUM, 4 CORE STRANDED | H15357/1 | TYCO | TYCO ELECTRONICS - ENERGY DIV. |  | 24 months | No
connectors | 2 | Approved | 152470 | Lug Crimp Aluminium 400mm2 M12 Round | EYE TYPE,CRIMP CONNECTION,400 SQMM,M12HOLE,ALUMINIUM | E-EPTE-400-39A/F-M12 | PLP | PREFORMED LINE PRODUCTS (AUST) |  | 12 months | No
connectors | 2 | Approved | 152482 | Lug Crimp Bimetal 185mm2 M12 | EYE TYPE,CRIMP CONNECTION,185 SQMM,M12 HOLE, BI-METAL, PRE-FILLED | EPTB-185-22.0AF-M12 | PLP | PREFORMED LINE PRODUCTS (AUST) |  | 12 months | No
connectors | 2 | Approved | 152492 | Lug Crimp Bimetal 185mm2 M12 4c solid Sector | EYE TYPE,CRIMP CONNECTION,185 SQMM,M12 HOLE, BI-METAL, PRE-FILLED, 4 CORE SOLID | EPTBS-175/4-12 | PLP | PREFORMED LINE PRODUCTS (AUST) |  | 12 months | No
connectors | 2 | Approved | 152483 | Lug Crimp Bimetal 240mm2 M12 | EYE TYPE,CRIMP CONNECTION,240 SQMM,M12HOLE,BI-METAL,PRE-FILLED | BG240M12/1 | UTILUX | TYCO ELECTRONICS - ENERGY DIV. |  | 12 months | No
connectors | 2 | Approved | 152484 | Lug Crimp Bimetal 300mm2 M12 | EYE TYPE,CRIMP CONNECTION,300 SQMM,M12HOLE,BI-METAL,PRE-FILLED | BG300M12/1 | TYCO | TYCO ELECTRONICS - ENERGY DIV. |  | 24 months | No
connectors | 2 | Approved | 152485 | Lug Crimp Bimetal 400mm2 Blank | EYE TYPE,CRIMP CONNECTION,400 SQMM,BLANK,BI-METAL,PRE-FILLED | BG400MB | TYCO | TYCO ELECTRONICS - ENERGY DIV. |  | 24 months | No
connectors | 2 | Approved | 152490 | Lug Crimp Bimetal 50mm2 M12 | EYE TYPE,CRIMP CONNECTION,50 SQMM,M12 HOLE, BI-METAL, PRE-FILLED | EPTB-50-13.2AF-M12 | PLP | PREFORMED LINE PRODUCTS (AUST) |  | 12 months | No
connectors | 2 | Approved | 141372 | Lug Crimp Copper 150mm2 | EYE TYPE,CRIMP CONNECTION,150 SQMM,M12 HOLE,COPPER | H1384/20 | TYCO | TYCO ELECTRONICS - ENERGY DIV. |  | 24 months | No
connectors | 2 | Approved | 141373 | Lug Crimp Copper 150mm2 M16 | EYE TYPE,CRIMP CONNECTION,150 SQMM,M16 HOLE,COPPER | TBA | PLP | PREFORMED LINE PRODUCTS (AUST) |  | 12 months | No
connectors | 2 | Approved | 141376 | Lug Crimp Copper 185mm2 M12 | EYE TYPE,CRIMP CONNECTION,185 SQMM,M12 HOLE,COPPER | EPTCU-185-20.0AF-M12 | PLP | PREFORMED LINE PRODUCTS (AUST) |  | 12 months | No
connectors | 2 | Approved | 141377 | Lug Crimp Copper 240mm2 Blank | BLANK PALM TYPE,CRIMP CONNECTION,COPPER,240 SQMM CABLE | TBA | PLP | PREFORMED LINE PRODUCTS (AUST) |  | 12 months | No
connectors | 2 | Approved | 141356 | Lug Crimp Copper 25mm2 | EYE TYPE,CRIMP CONNECTION,25 SQMM,M10 HOLE,COPPER,BOX OF 50. | EPTCU-25-7.7AF-M10 | PLP | PREFORMED LINE PRODUCTS (AUST) |  | 12 months | No
connectors | 2 | Approved | 141379 | Lug Crimp Copper 300mm2 Blank | BLANK PALM TYPE,CRIMP CONNECTION,COPPER,300 SQMM CABLE | H1391/1 | TYCO | TYCO ELECTRONICS - ENERGY DIV. |  | 24 months | No
connectors | 2 | Approved | 141369 | Lug Crimp Copper 35mm2 M12 | EYE TYPE,CRIMP CONNECTION,35 SQMM,M12 HOLE,COPPER | EPTCU-35-9.2AF-M12 | PLP | PREFORMED LINE PRODUCTS (AUST) |  | 12 months | No
connectors | 3 | Consumables | 140177 | Spacer Plate aluminium | ALUMINIUM,40 MM LG,36 MM W,16 MM THK,12 MM DIA HOLE,TO HEC DWG Y41 | N/A | BRETT GLEESON | BRETT GLEESON |  | 12 months | No
connectors | 2 | Approved | 141159 | Splice Crimp Aluminium 120mm2 4c solid Sector | CRIMP TYPE,ALUMINIUM,120 SQMM CONDUCTORAREA,4 CORE SOLID SECTOR | H8949 | UTILUX | TYCO ELECTRONICS - ENERGY DIV. |  | 12 months | No
connectors | 2 | Approved | 141164 | Splice Crimp Aluminium 185/240mm2 Round | CRIMP TYPE,ALUMINIUM,185/240 SQMMCONDUCTOR AREA,BOX OF 40. | H15211X06/1 | TYCO | TYCO ELECTRONICS - ENERGY DIV. |  | 24 months | No
connectors | 2 | Approved | 141165 | Splice Crimp Aluminium 185mm2 4c Solid Sector | CRIMP TYPE,ALUMINIUM,185 SQMM CONDUCTORAREA,4 CORE SOLID SECTOR | AK4H185/1 | UTILUX | LEGEND CORP SERVICES P/L T/A LEGEND POWER SYSTEMS |  | 12 months | No
connectors | 2 | Approved | 141160 | Splice Crimp Aluminium 185mm2 Round | CRIMP TYPE,ALUMINIUM,185 SQMM CONDUCTORAREA,UTILUX H15210 OR EQUIV | H15210/1 | TYCO | TYCO ELECTRONICS - ENERGY DIV. |  | 24 months | No
connectors | 2 | Approved | 141166 | Splice Crimp Aluminium 240mm2 4c Stranded Sector | CRIMP TYPE,ALUMINIUM,240 SQMM CONDUCTORAREA,4 CORE STRANDED | AK4HR240 | UTILUX | TYCO ELECTRONICS - ENERGY DIV. |  | 12 months | No
connectors | 2 | Approved | 141161 | Splice Crimp Aluminium 240mm2 Round | CRIMP TYPE,ALUMINIUM,240 SQMM CONDUCTORAREA,UTILUX H15211 OR EQUIV | H15211/1 | TYCO | TYCO ELECTRONICS - ENERGY DIV. |  | 24 months | No
connectors | 2 | Approved | 141162 | Splice Crimp Aluminium 300mm2 Round | CRIMP TYPE,ALUMINIUM,300 SQMM CONDUCTORAREA,UTILUX H15212 (AK300) OR EQUIV | H15212/1 | TYCO | TYCO ELECTRONICS - ENERGY DIV. |  | 24 months | No
connectors | 2 | Approved | 141163 | Splice Crimp Aluminium 400mm2 Round | CRIMP TYPE,ALUMINIUM,400 SQMM CONDUCTORAREA,UTILUX H15213 (AK400) OR EQUIV | H15213/1 | TYCO | TYCO ELECTRONICS - ENERGY DIV. |  | 24 months | No
connectors | 2 | Approved | 141196 | Splice Crimp Bimetal 120al/70cu 4c solid Sector/Round | CRIMP TYPE,BIMETAL,120SQMM ALUMINIUM,70SQMM COPPER,4 CORE SECTOR | H15760 | UTILUX | TYCO ELECTRONICS - ENERGY DIV. |  | 12 months | No
connectors | 2 | Approved | 141194 | Splice Crimp Bimetal 150Al/120Cu Round/Round | CRIMP TYPE,BIMETAL,150SQMM ALUMINIUM,120SQMM COPPER,UTILUX H15418 (BK150/120) | H15366 BG4HR2240M12 | UTILUX | TYCO ELECTRONICS - ENERGY DIV. |  | 12 months | No
connectors | 2 | Approved | 141198 | Splice Crimp Bimetal 185al/120cu 4c solid Sector/Round | CRIMP TYPE,BIMETAL,185SQMM ALUMINIUM,120 SQMM COPPER, 4 CORE SECTOR | BK4I185-120 | TYCO | TYCO ELECTRONICS - ENERGY DIV. |  | 24 months | No
connectors | 2 | Approved | 141197 | Splice Crimp Bimetal 240al/150cu 4c solid Sector/Round | CRIMP TYPE,BIMETAL,240 SQMM ALUMINIUM,150 SQMM COPPER,STRANDED CABLE,4 CORE | BK4HR240150/1 | TYCO | TYCO ELECTRONICS - ENERGY DIV. |  | 24 months | No
connectors | 2 | Approved | 141192 | Splice Crimp Bimetal 300al/185cu Round/Round | H15424X08/1,300SQMM, ALUMINIUM, 185SQMM,COPPER, UTILUX H15424X08/1 | BK300-185 | TYCO | TYCO ELECTRONICS - ENERGY DIV. |  | 24 months | No
connectors | 2 | Approved | 141193 | Splice Crimp Bimetal 300al/240cu Round/Round | CRIMP TYPE,BIMETAL,300SQMM ALUMINIUM,240SQMM COPPER,UTILUX H15424 (BK300/240) | BK300-240/1 | TYCO | TYCO ELECTRONICS - ENERGY DIV. |  | 24 months | No
connectors | 2 | Approved | 141199 | Splice Crimp Bimetal 400al/240cu Round/Round | BI-METAL CRIMP LINK,SUIT CONDUCTOR 400/240SQMM,ALUMINIUM/COPPER, CABAC BLK400/240 | BLK400/240 | CABACC | LEGEND CORP SERVICES P/L T/A LEGEND POWER SYSTEMS |  | 12 months | No
connectors | 2 | Approved | 141195 | Splice Crimp Bimetal 50al/50cu Round/Round | CRIMP TYPE,BIMETAL,50SQMM ALUMINIUM,50SQMM COPPER,UTILUX H15411(BK50/50) EQUIV | H15411 | UTILUX | TYCO ELECTRONICS - ENERGY DIV. |  | 12 months | No
connectors | 2 | Approved | 141224 | Splice Crimp Copper 120mm2 Round | CRIMP TYPE,COPPER,120SQMM CONDUCTOR AREASOLID BARRIER,UTILUX H1792 | H1792/10 | UTILUX | TYCO ELECTRONICS - ENERGY DIV. |  | 12 months | No
connectors | 2 | Approved | 141228 | Splice Crimp Copper 150mm2 Round | CRIMP TYPE,COPPER,150SQMM CONDUCTOR AREACENTRE DIMPLE,UTILUX H1493 (CK 150) | H1493 | UTILUX | TYCO ELECTRONICS - ENERGY DIV. |  | 12 months | No
connectors | 2 | Approved | 141230 | Splice Crimp Copper 185mm2 Round | SOLID CENTRE BARRIER,CRIMP,COPPER,185 SQMM CONDUCTOR,UTILUX H1794 | H1794 | UTILUX | TYCO ELECTRONICS - ENERGY DIV. |  | 12 months | No
connectors | 2 | Approved | 141229 | Splice Crimp Copper 240mm2 Round | SOLID CENTRE BARRIER,CRIMP,COPPER,240 SQMM CONDUCTOR,UTILUX H1795 | H1795/10 | UTILUX | TYCO ELECTRONICS - ENERGY DIV. |  | 12 months | No
connectors | 2 | Approved | 141219 | Splice Crimp Copper 35mm2 Round | CRIMP TYPE,COPPER,35 SQMM CONDUCTOR AREACENTRE DIMPLE | H1488/25 | TYCO | TYCO ELECTRONICS - ENERGY DIV. |  | 24 months | No
connectors | 2 | Approved | 141220 | Splice Crimp Copper 50mm2 Round | CRIMP TYPE,COPPER,50 SQMM COMDUCTOR AREACENTRE DIMPLE, 25/PKT | H1460 | UTILUX | TYCO ELECTRONICS - ENERGY DIV. |  | 12 months | No
connectors | 2 | Approved | 141221 | Splice Crimp Copper 70mm2 Round | CRIMP TYPE,COPPER,70 SQMM CONDUCTOR AREACENTRE DIMPLE | H1461/20 | TYCO | TYCO ELECTRONICS - ENERGY DIV. |  | 24 months | No
connectors | 2 | Approved | 141226 | Splice Crimp Copper 95mm2 Round | SOLID BARRIER,COPPER,95 SQ MMSOLID BARRIER | H1772/25 | TYCO | TYCO ELECTRONICS - ENERGY DIV. |  | 24 months | No
consumables - common | 3 | Consumables | 032207 | Bolt Hex Hd M12 x 25 GMS | ISO,GRADE 4.6,HEX HEAD WITH HEX NUT,THREAD 25MM,TO AS1111 | M12X25BNG | AUSTSTD | WEBSTERBSC | AS1111 | 12 months | No
consumables - common | 3 | Consumables | 032177 | Bolt Hex M10 X 25 | ISO,GRADE 4.6,HEX HEAD WITH HEX NUT,THREAD 25MM,TO AS1111 | M10X25BNG | AUSTSTD | WEBSTERBSC | AS1111 | 12 months | No
consumables - common | 3 | Consumables | 032178 | Bolt Hex M10 X 30 | ISO,GRADE 4.6,HEX HEAD WITH HEX NUT,THREAD 30MM,TO AS1111 | M10X30BNG | AUSTSTD | WEBSTERBSC | AS1111 | 12 months | No
consumables - common | 3 | Consumables | 032181 | Bolt Hex M10 X 45 | ISO,GRADE 4.6,HEX HEAD WITH HEX NUT,THREAD 30MM,TO AS1111 | M10X45BNG | AUSTSTD | WEBSTERBSC | AS1111 | 12 months | No
consumables - common | 3 | Consumables | 032221 | Bolt Hex M12 X 100 | ISO,GRADE 4.6,HEX HEAD WITH HEX NUT,THREAD 35MM,TO AS1111 | M12X100BNG | AUSTSTD | WEBSTERBSC | AS1111 | 12 months | No
consumables - common | 3 | Consumables | 032212 | Bolt Hex M12 X 50 | ISO,GRADE 4.6,HEX HEAD WITH HEX NUT,THREAD 30MM,TO AS1111 | M12X50BNG | AUSTSTD | WEBSTERBSC | AS1111 | 12 months | No
consumables - common | 3 | Consumables | 032217 | Bolt Hex M12 X 75 | ISO,GRADE 4.6,HEX HEAD WITH HEX NUT,THREAD 35MM,TO AS1111 | M12X75BNG | AUSTSTD | WEBSTERBSC | AS1111 | 12 months | No
consumables - common | 3 | Consumables | 033771 | Bolt Tower M12 X 35 | ISO,GRADE 4.6,STEEL,TOWER,HEX HD,WITH SINGLE NUT,THREAD 30MM,TO AS1559 | M12X35STR | AUSTSTD | WEBSTERBSC | AS1559 | 12 months | No
consumables - common | 3 | Consumables | 040439 | Nut M10 | NUT,PLAIN,HEXAGON,GALV M10,STEEL,GDE5,TO AS1112,HEX,WASHER & THIMBLE,DWG DS-OH-1.2/2 | M10G | AUSTSTD | WEBSTERBSC | AS1112 | 12 months | No
consumables - common | 3 | Consumables | 040440 | Nut M12 | NUT,PLAIN,HEXAGON,GALV,M12,STEEL,GDE5,TO AS1112,HEX,WASHER & THIMBLE,DWG DS-OH-1.2/2 | M12G | AUSTSTD | WEBSTERBSC | AS1112 | 12 months | No
consumables - common | 3 | Consumables | 026111 | Rivet 3.2mm dia x 7.9mm long, Stainless Steel | DOME HD,STAINLESS STEEL 3.2 MM DIA,7.9 MM LG | STST4-6 | BREMICK HOBSON | WEBSTERBSC |  | 12 months | No
consumables - common | 3 | Consumables | 158390 | Tape PVC 20mm Black | PVC,ADHESIVE BACKED,19 MM W,20 M LG,0.15 MM THK,BLACK | PVC21EBK | NITTO | REXEL | IEC 60454-2 | 12 months | No
consumables - common | 3 | Consumables | 158393 | Tape PVC 20mm Yellow/Green 0.15 | PVC,ADHESIVE BACKED,19 MM W,20 M LG,0.15 MM THK,GREEN/YELLOW | PVC21G/Y | NITTO | REXEL | IEC 60454-2 | 12 months | No
consumables - common | 3 | Consumables | 158391 | Tape PVC Blue 19mm | PVC,ADHESIVE BACKED,19 MM W,20 M LG,0.15 MM THK,BLUE | PVC21EBL | NITTO | REXEL | IEC 60454-2 | 12 months | No
consumables - common | 3 | Consumables | 158395 | Tape PVC Red 19mm | PVC,ADHESIVE BACKED,19 MM W,20 M LG,0.15 MM THK,RED | PVC21ER | NITTO | REXEL | IEC 60454-2 | 12 months | No
consumables - common | 3 | Consumables | 158397 | Tape PVC White 19mm | PVC,ADHESIVE BACKED,19 MM W,20 M LG,0.15 MM THK,WHITE | PVC21EW | NITTO | REXEL | IEC 60454-2 | 12 months | No
consumables - common | 3 | Consumables | 065614 | Washer Flat 10mm X 21mm X 2mm Round Galvanised Steel | WASHER,FLAT,10MM X 21MM X 2MM,STEEL,ROUND,GALV,TO AS1237 | FWM10HDG | AUSTSTD | WEBSTERBSC | AS1237 | 12 months | No
consumables - common | 3 | Consumables | 065615 | Washer Flat 12mm X 28mm X 2.5mm Round Galvanised Steel | WASHER,FLAT,12MM X 28MM X 2.5MM,STEEL,ROUND,GALV,TO AS1237 | FWM12HDG | AUSTSTD | WEBSTERBSC | AS1237 | 12 months | No
consumables - rare | 3 | Consumables | 032176 | Bolt Hex Hd M10 x 20 GMS | ISO,GRADE 4.6,HEX HEAD WITH HEX NUT,THREAD 20MM,TO AS1111 | M10X20BNG | AUSTSTD | WEBSTERBSC | AS1111 | 12 months | No
consumables - rare | 3 | Consumables | 032184 | Bolt Hex Hd M10 x 60 GMS | ISO,GRADE 4.6,HEX HEAD WITH HEX NUT,THREAD 30MM,TO AS1111 | M10X60BNG | AUSTSTD | WEBSTERBSC | AS1111 | 12 months | No
consumables - rare | 3 | Consumables | 032213 | Bolt Hex Hd M12 x 55 GMS | ISO,GRADE 4.6,HEX HEAD WITH HEX NUT,THREAD 35MM,TO AS1111 | M12X55BNG | AUSTSTD | WEBSTERBSC | AS1111 | 12 months | No
consumables - rare | 3 | Consumables | 032218 | Bolt Hex Hd M12 x 80 GMS | ISO,GRADE 4.6,HEX HEAD WITH HEX NUT,THREAD 35MM,TO AS1111 | M12X80BNG | AUSTSTD | WEBSTERBSC | AS1111 | 12 months | No
consumables - rare | 3 | Consumables | 032220 | Bolt Hex Hd M12 x 90 GMS | ISO,GRADE 4.6,HEX HEAD WITH HEX NUT,THREAD 35MM,TO AS1111 | M12X90BNG | AUSTSTD | WEBSTERBSC | AS1111 | 12 months | No
consumables - rare | 3 | Consumables | 058660 | Bolt Hex Hd M6X20 S/S | SCREW,MACHINE,M6 X 20MM,HEX HEAD,S/S,WITH NUT | SM6X20-316 | AUSTSTD | WEBSTERBSC | AS1111 | 12 months | No
consumables - rare | 3 | Consumables | 032191 | Bolt Hex M10 X 100 | ISO,GRADE 4.6,HEX HEAD WITH HEX NUT,THREAD 30MM,TO AS1111 | M10X100BNG | AUSTSTD | WEBSTERBSC | AS1111 | 12 months | No
consumables - rare | 3 | Consumables | 032199 | Bolt Hex M10 X 180 | ISO,GRADE 4.6,HEX HEAD WITH HEX NUT,THREAD 80MM,TO AS1111 | M10X180BNG | AUSTSTD | WEBSTERBSC | AS1111 | 12 months | No
consumables - rare | 3 | Consumables | 032179 | Bolt Hex M10 X 35 | ISO,GRADE 4.6,HEX HEAD WITH HEX NUT,THREAD 35MM,TO AS1111 | M10X35BNG | AUSTSTD | WEBSTERBSC | AS1111 | 12 months | No
consumables - rare | 3 | Consumables | 032180 | Bolt Hex M10 X 40 | ISO,GRADE 4.6,HEX HEAD WITH HEX NUT,THREAD 40MM,TO AS1111 | M10X40BNG | AUSTSTD | WEBSTERBSC | AS1111 | 12 months | No
consumables - rare | 3 | Consumables | 032182 | Bolt Hex M10 X 50 | ISO,GRADE 4.6,HEX HEAD WITH HEX NUT,THREAD 30MM,TO AS1111 | M10X50BNG | AUSTSTD | WEBSTERBSC | AS1111 | 12 months | No
consumables - rare | 3 | Consumables | 032185 | Bolt Hex M10 X 50 | ISO,GRADE 4.6,HEX HEAD WITH HEX NUT,THREAD 30MM,TO AS1111 | M10X65BNG | AUSTSTD | WEBSTERBSC | AS1111 | 12 months | No
consumables - rare | 3 | Consumables | 032183 | Bolt Hex M10 X 55 | ISO,GRADE 4.6,HEX HEAD WITH HEX NUT,THREAD 30MM,TO AS1111 | M10X55BNG | AUSTSTD | WEBSTERBSC | AS1111 | 12 months | No
consumables - rare | 3 | Consumables | 032187 | Bolt Hex M10 X 75 | ISO,GRADE 4.6,HEX HEAD WITH HEX NUT,THREAD 30MM,TO AS1111 | M10X75BNG | AUSTSTD | WEBSTERBSC | AS1111 | 12 months | No
consumables - rare | 3 | Consumables | 032190 | Bolt Hex M10 X 90 | ISO,GRADE 4.6,HEX HEAD WITH HEX NUT,THREAD 30MM,TO AS1111 | M10X90BNG | AUSTSTD | WEBSTERBSC | AS1111 | 12 months | No
consumables - rare | 3 | Consumables | 032223 | Bolt Hex M12 X 120 | ISO,GRADE 4.6,HEX HEAD WITH HEX NUT,THREAD 35MM,TO AS1111 | M12X120BNG | AUSTSTD | WEBSTERBSC | AS1111 | 12 months | No
consumables - rare | 3 | Consumables | 032224 | Bolt Hex M12 X 130 | ISO,GRADE 4.6,HEX HEAD WITH HEX NUT,THREAD 50MM,TO AS1111 | M12X130BNG | AUSTSTD | WEBSTERBSC | AS1111 | 12 months | No
consumables - rare | 3 | Consumables | 032225 | Bolt Hex M12 X 140 | ISO,GRADE 4.6,HEX HEAD WITH HEX NUT,THREAD 50MM,TO AS1111 | M12X140BNG | AUSTSTD | WEBSTERBSC | AS1111 | 12 months | No
consumables - rare | 3 | Consumables | 032226 | Bolt Hex M12 X 150 | ISO,GRADE 4.6,HEX HEAD WITH HEX NUT,THREAD 50MM,TO AS1111 | M12X150BNG | AUSTSTD | WEBSTERBSC | AS1111 | 12 months | No
consumables - rare | 3 | Consumables | 032229 | Bolt Hex M12 X 180 | ISO,GRADE 4.6,HEX HEAD WITH HEX NUT,THREAD 50MM,TO AS1111 | M12X180BNG | AUSTSTD | WEBSTERBSC | AS1111 | 12 months | No
consumables - rare | 3 | Consumables | 032215 | Bolt Hex M12 X 65 | ISO,GRADE 4.6,HEX HEAD WITH HEX NUT,THREAD 35MM,TO AS1111 | M12X65BNG | AUSTSTD | WEBSTERBSC | AS1111 | 12 months | No
consumables - rare | 3 | Consumables | 032274 | Bolt Hex M16 X 130 | ISO,GRADE 4.6,HEX HEAD WITH HEX NUT,THREAD 55MM,TO AS1111 | M16X130BNG | AUSTSTD | WEBSTERBSC | AS1111 | 12 months | No
consumables - rare | 3 | Consumables | 032275 | Bolt Hex M16 X 140 | ISO,GRADE 4.6,HEX HEAD WITH HEX NUT,THREAD 55MM,TO AS1111 | M16X140BNG | AUSTSTD | WEBSTERBSC | AS1111 | 12 months | No
consumables - rare | 3 | Consumables | 032276 | Bolt Hex M16 X 150 | ISO,GRADE 4.6,HEX HEAD WITH HEX NUT,THREAD 55MM,TO AS1111 | M16X150BNG | AUSTSTD | WEBSTERBSC | AS1111 | 12 months | No
consumables - rare | 3 | Consumables | 032279 | Bolt Hex M16 X 180 | ISO,GRADE 4.6,HEX HEAD WITH HEX NUT,THREAD 55MM,TO AS1111 | M16X180BNG | AUSTSTD | WEBSTERBSC | AS1111 | 12 months | No
consumables - rare | 3 | Consumables | 032281 | Bolt Hex M16 X 200 | ISO,GRADE 4.6,HEX HEAD WITH HEX NUT,THREAD 100MM,TO AS1111 | M16X200BNG | AUSTSTD | WEBSTERBSC | AS1111 | 12 months | No
consumables - rare | 3 | Consumables | 032282 | Bolt Hex M16 X 220 | ISO,GRADE 4.6,HEX HEAD WITH HEX NUT,THREAD 100MM,TO AS1111 | M16X220BNG | AUSTSTD | WEBSTERBSC | AS1111 | 12 months | No
consumables - rare | 3 | Consumables | 032283 | Bolt Hex M16 X 240 | ISO,GRADE 4.6,HEX HEAD WITH HEX NUT,THREAD 100MM,TO AS1111 | M16X240BNG | AUSTSTD | WEBSTERBSC | AS1111 | 12 months | No
consumables - rare | 3 | Consumables | 032284 | Bolt Hex M16 X 260 | ISO,GRADE 4.6,HEX HEAD WITH HEX NUT,THREAD 100MM,TO AS1111 | M16X260BNG | AUSTSTD | WEBSTERBSC | AS1111 | 12 months | No
consumables - rare | 3 | Consumables | 032285 | Bolt Hex M16 X 280 | ISO,GRADE 4.6,HEX HEAD WITH HEX NUT,THREAD 150MM,TO AS1111 | M16X280BNG | AUSTSTD | WEBSTERBSC | AS1111 | 12 months | No
consumables - rare | 3 | Consumables | 032286 | Bolt Hex M16 X 300 | ISO,GRADE 4.6,HEX HEAD WITH HEX NUT,THREAD 150MM,TO AS1111 | M16X300BNG | AUSTSTD | WEBSTERBSC | AS1111 | 12 months | No
consumables - rare | 3 | Consumables | 032287 | Bolt Hex M16 X 325 | ISO,GRADE 4.6,HEX HEAD WITH HEX NUT,THREAD 150MM,TO AS1111 | M16X325BNG | AUSTSTD | WEBSTERBSC | AS1111 | 12 months | No
consumables - rare | 3 | Consumables | 032288 | Bolt Hex M16 X 350 | ISO,GRADE 4.6,HEX HEAD WITH HEX NUT,THREAD 150MM,TO AS1111 | M16X350BNG | AUSTSTD | WEBSTERBSC | AS1111 | 12 months | No
consumables - rare | 3 | Consumables | 032289 | Bolt Hex M16 X 375 | ISO,GRADE 4.6,HEX HEAD WITH HEX NUT,THREAD 150MM,TO AS1111 | M16X375BNG | AUSTSTD | WEBSTERBSC | AS1111 | 12 months | No
consumables - rare | 3 | Consumables | 032290 | Bolt Hex M16 X 400 | ISO,GRADE 4.6,HEX HEAD WITH HEX NUT,THREAD 150MM,TO AS1111 | M16X400BNG | AUSTSTD | WEBSTERBSC | AS1111 | 12 months | No
consumables - rare | 3 | Consumables | 032291 | Bolt Hex M16 X 425 | ISO,GRADE 4.6,HEX HEAD WITH HEX NUT,THREAD 150MM,TO AS1111 | M16X425BNG | AUSTSTD | WEBSTERBSC | AS1111 | 12 months | No
consumables - rare | 3 | Consumables | 032261 | Bolt Hex M16 X 45 | ISO,GRADE 4.6,HEX HEAD WITH HEX NUT,THREAD 45MM,TO AS1111 | M16X45BNG | AUSTSTD | WEBSTERBSC | AS1111 | 12 months | No
consumables - rare | 3 | Consumables | 032292 | Bolt Hex M16 X 450 | ISO,GRADE 4.6,HEX HEAD WITH HEX NUT,THREAD 150MM,TO AS1111 | M16X450BNG | AUSTSTD | WEBSTERBSC | AS1111 | 12 months | No
consumables - rare | 3 | Consumables | 032293 | Bolt Hex M16 X 475 | ISO,GRADE 4.6,HEX HEAD WITH HEX NUT,THREAD 150MM,TO AS1111 | M16X475BNG | AUSTSTD | WEBSTERBSC | AS1111 | 12 months | No
consumables - rare | 3 | Consumables | 032294 | Bolt Hex M16 X 500 | ISO,GRADE 4.6,HEX HEAD WITH HEX NUT,THREAD 150MM,TO AS1111 | M16X500BNG | AUSTSTD | WEBSTERBSC | AS1111 | 12 months | No
consumables - rare | 3 | Consumables | 032296 | Bolt Hex M16 X 550 | ISO,GRADE 4.6,HEX HEAD WITH HEX NUT,THREAD 150MM,TO AS1111 | M16X550BNG | AUSTSTD | WEBSTERBSC | AS1111 | 12 months | No
consumables - rare | 3 | Consumables | 032298 | Bolt Hex M16 X 600 | ISO,GRADE 4.6,HEX HEAD WITH HEX NUT,THREAD 150MM,TO AS1111 | M16X600BNG | AUSTSTD | WEBSTERBSC | AS1111 | 12 months | No
consumables - rare | 3 | Consumables | 032265 | Bolt Hex M16 X 65 | ISO,GRADE 4.6,HEX HEAD WITH HEX NUT,THREAD 45MM,TO AS1111 | M16X65BNG | AUSTSTD | WEBSTERBSC | AS1111 | 12 months | No
consumables - rare | 3 | Consumables | 032299 | Bolt Hex M16 x 650 | ISO,GRADE 4.6,HEX HEAD WITH HEX NUT,THREAD 150MM,TO AS1111 | M16X650BNG | AUSTSTD | WEBSTERBSC | AS1111 | 12 months | No
consumables - rare | 3 | Consumables | 032336 | Bolt Hex M20 X 300 | ISO,GRADE 4.6,HEX HEAD WITH HEX NUT,THREAD 150MM,TO AS1111 | M20X300BNG | AUSTSTD | WEBSTERBSC | AS1111 | 12 months | No
consumables - rare | 3 | Consumables | 032338 | Bolt Hex M20 X 350 | ISO, GRADE 4.6, HEX HEAD WITH HEX NUT, TO AS1111 | GSF/032338 | GREG SEWELL FORGINGS PTY LTD | GREG SEWELL FORGINGS PTY LTD | AS1111 | 12 months | No
consumables - rare | 3 | Consumables | 032340 | Bolt Hex M20 X 400 | ISO,GRADE 4.6,HEX HEAD WITH HEX NUT,THREAD 150MM,TO AS1111 | M20X400BNG | AUSTSTD | WEBSTERBSC | AS1111 | 12 months | No
consumables - rare | 3 | Consumables | 032342 | Bolt Hex M20 X 450 | ISO,GRADE 4.6,HEX HEAD WITH HEX NUT,THREAD 150MM,TO AS1111 | M20X450BNG | AUSTSTD | WEBSTERBSC | AS1111 | 12 months | No
consumables - rare | 3 | Consumables | 032344 | Bolt Hex M20 x 500 | ISO,GRADE 4.6,HEX HEAD WITH HEX NUT,THREAD 150MM,TO AS1111 | M20X500BNG | AUSTSTD | WEBSTERBSC | AS1111 | 12 months | No
consumables - rare | 3 | Consumables | 032346 | Bolt Hex M20 x 550 | ISO, GRADE 4.6, HEX HEAD WITH HEX NUT,TO AS 1111 | GSF/032346 | GREG SEWELL FORGINGS PTY LTD | GREG SEWELL FORGINGS PTY LTD | AS1111 | 12 months | No
consumables - rare | 3 | Consumables | 032348 | Bolt Hex M20 x 600 | STEEL LONG HEX NUT,TO AS 1111 | GSF/032348 | GREG SEWELL FORGINGS PTY LTD | GREG SEWELL FORGINGS PTY LTD | AS1111 | 12 months | No
consumables - rare | 3 | Consumables | 032350 | Bolt Hex M20 x 650 | STEEL LONG HEX NUT,TO AS 1111 | GSF/032350 | GREG SEWELL FORGINGS PTY LTD | GREG SEWELL FORGINGS PTY LTD | AS1111 | 12 months | No
consumables - rare | 3 | Consumables | 032158 | Bolt Hex M8 X 100 GMS | ISO,GRADE 4.6,HEX HEAD WITH HEX NUT,THREAD 25MM,TO AS1111,USED WITH SERVICE FUSE | M8X100BNG | AUSTSTD | WEBSTERBSC | AS1111 | 12 months | No
consumables - rare | 3 | Consumables | 032159 | Bolt Hex M8 X 150 GMS | ISO,GRADE 4.6,HEX HEAD WITH HEX NUT,THREAD 30MM,TO AS1111,USED WITH SERVICE FUSE | M8X150BNG | AUSTSTD | WEBSTERBSC | AS1111 | 12 months | No
consumables - rare | 3 | Consumables | 032147 | Bolt Hex M8 X 25 | ISO,GRADE 4.6,HEX HEAD WITH HEX NUT,THREAD 25MM,TO AS1111 | M8X25BNG | AUSTSTD | WEBSTERBSC | AS1111 | 12 months | No
consumables - rare | 3 | Consumables | 033770 | Bolt Tower M12 X 30 | ISO,GRADE 4.6,STEEL,TOWER,HEX HD,WITH SINGLE NUT,THREAD 20MM,TO AS1559 | M12X30STR | AUSTSTD | WEBSTERBSC | AS1559 | 12 months | No
consumables - rare | 3 | Consumables | 033772 | Bolt Tower M12 X 40 | ISO,GRADE 4.6,STEEL,TOWER,HEX HD,WITH SINGLE NUT,THREAD 30MM,TO AS1559 | M12X40STR | AUSTSTD | WEBSTERBSC | AS1559 | 12 months | No
consumables - rare | 3 | Consumables | 033780 | Bolt Tower M16 X 35 | ISO,GRADE 4.6,STEEL,TOWER,HEX HD,WITH SINGLE NUT,THREAD 38MM,TO AS1559 | M16X35STR | AUSTSTD | WEBSTERBSC | AS1559 | 12 months | No
consumables - rare | 3 | Consumables | 033783 | Bolt Tower M16 X 50 | ISO,GRADE 4.6,STEEL,TOWER,HEX HD,WITH SINGLE NUT,THREAD 38MM,TO AS1559 | M16X50STR | AUSTSTD | WEBSTERBSC | AS1559 | 12 months | No
consumables - rare | 3 | Consumables | 033784 | Bolt Tower M16 X 55 | ISO,GRADE 4.6,STEEL,TOWER,HEX HD,WITH SINGLE NUT,THREAD 38MM,TO AS1559 | M16X55STR | AUSTSTD | WEBSTERBSC | AS1559 | 12 months | No
consumables - rare | 3 | Consumables | 033744 | Bolt Tower M20 X 45 | ISO,GRADE 4.6,STEEL,TOWER,HEX HD,WITH SINGLE NUT,THREAD 45MM,TO AS1559 | M20X45STR | AUSTSTD | WEBSTERBSC | AS1559 | 12 months | No
consumables - rare | 3 | Consumables | 141697 | Cable Tie Self Locking 2.5mm x 142mm Nylon (pkt 100) | CABLE TIE BLACK 150mm x 3.6mm 100/PKT ANTI-UV TREATMENT | BIZCTB15036100 | BIZLINE | REXEL |  | 12 months | No
consumables - rare | 3 | Consumables | 141668 | Cable Tie Self Locking 4.8mm x 368mm Black (pkt 100) | CABLE TIE BLACK 370mm x 4.8mm 100/PKT ANTI-UV TREATMENT | BIZCTB37048100 | BIZLINE | REXEL |  | 12 months | No
consumables - rare | 3 | Consumables | 141693 | Cable Tie Self Locking 5mm x 178mm Black (pkt 100) | CABLE TIE BLACK 200mm x 4.8mm 100/PKT ANTI-UV TREATMENT | BIZCTB20048100 | BIZLINE | REXEL |  | 12 months | No
consumables - rare | 3 | Consumables | 141694 | Cable Tie Self Locking 8mm x 380mm Black (pkt 100) | CABLE TIE BLACK 380mm x 7.6mm 100/PKT ANTI-UV TREATMENT | BIZCTBHD38076100 | BIZLINE | REXEL |  | 12 months | No
consumables - rare | 3 | Consumables | 050230 | Coach Screw M10 X 100 | SCREW,COACH,GALV,10MM X 100MM,HEX HEAD,GIMBLET POINT,FULL THREAD,TO AS1393 | CSM10X100G | AUSTSTD | WEBSTERBSC | AS1393 | 12 months | No
consumables - rare | 3 | Consumables | 050224 | Coach Screw M10 x 40 | SCREW,COACH,GALV,10MM X 40MM,HEX HEAD,GIMBLET POINT,FULL THREAD,TO AS1393 | CSM10X40G | AUSTSTD | WEBSTERBSC | AS1393 | 12 months | No
consumables - rare | 3 | Consumables | 050225 | Coach Screw M10 X 50 | SCREW,COACH,GALV,10MM X 50MM,HEX HEAD,GIMBLET POINT,FULL THREAD,TO AS1393 | CSM10X50G | AUSTSTD | WEBSTERBSC | AS1393 | 12 months | No
consumables - rare | 3 | Consumables | 050226 | Coach Screw M10 X 65 | SCREW,COACH,GALV,10MM X 65MM,HEX HEAD,GIMBLET POINT,FULL THREAD,TO AS1393 | CSM10X65G | AUSTSTD | WEBSTERBSC | AS1393 | 12 months | No
consumables - rare | 3 | Consumables | 050228 | Coach Screw M10 X 80 | SCREW,COACH,GALV,10MM X 75MM,HEX HEAD,GIMBLET POINT,FULL THREAD,TO AS1393 | CSM10X75G | AUSTSTD | WEBSTERBSC | AS1393 | 12 months | No
consumables - rare | 3 | Consumables | 050250 | Coach Screw M12 X 100 | SCREW,COACH,GALV,12MM X 100MM,HEX HEAD,GIMBLET POINT,FULL THREAD,TO AS1393 | CSM12X100G | AUSTSTD | WEBSTERBSC | AS1393 | 12 months | No
consumables - rare | 3 | Consumables | 050253 | Coach Screw M12 X 130 | SCREW,COACH,GALV,12MM X 130MM,HEX HEAD,GIMBLET POINT,FULL THREAD,TO AS1393 | CSM12X130G | AUSTSTD | WEBSTERBSC | AS1393 | 12 months | No
consumables - rare | 3 | Consumables | 050255 | Coach Screw M12 X 150 | SCREW,COACH,GALV,12MM X 150MM,HEX HEAD,GIMBLET POINT,FULL THREAD,TO AS1393 | CSM12X150G | AUSTSTD | WEBSTERBSC | AS1393 | 12 months | No
consumables - rare | 3 | Consumables | 050248 | Coach Screw M12 X 75 | SCREW,COACH,GALV,12MM X 75MM,HEX HEAD,GIMBLET POINT,FULL THREAD,TO AS1393 | CSM12X75G | AUSTSTD | WEBSTERBSC | AS1393 | 12 months | No
consumables - rare | 3 | Consumables | 040441 | Nut M16 | NUT,PLAIN,HEXAGON,GALV,M16,STEEL,GDE5,TO AS1112,HEX,WASHER & THIMBLE,DWG DS-OH-1.2/2 | M16G | AUSTSTD | WEBSTERBSC | AS1112 | 12 months | No
consumables - rare | 3 | Consumables | 040442 | Nut M20 | NUT,PLAIN,HEXAGON,GALV,M20,STEEL,GDE5,TO AS1112,HEX,WASHER & THIMBLE,DWG DS-OH-1.2/2 | M20G | AUSTSTD | WEBSTERBSC | AS1112 | 12 months | No
consumables - rare | 3 | Consumables | 066412 | Washer Flat 12mm X 24mm X 5mm Round Galvanised Steel | WASHER,FLAT,12MM X 24MM X 5MM,STEEL,ROUND,GALV,TO AS1559 | FWM12STR | AUSTSTD | WEBSTERBSC | AS1559 | 12 months | No
consumables - rare | 3 | Consumables | 065157 | Washer Flat 12mm X 37mm X 3mm Round Galvanised Steel | WASHER,FLAT,12MM X 37MM X 3MM, STEEL,ROUND,GALV,TO AS1237 | FWM12HDG-BUILD | AUSTSTD | WEBSTERBSC | AS1237 | 12 months | No
consumables - rare | 3 | Consumables | 065616 | Washer Flat 16mm X 30mm X 3mm Round Galvanised Steel | WASHER,FLAT,16MM x 30MM x 3MM,STEEL,ROUND,GALV,TO AS1237 | FWM16HDG | AUSTSTD | WEBSTERBSC | AS1237 | 12 months | No
consumables - rare | 3 | Consumables | 066413 | Washer Flat 16mm X 30mm X 5mm Round Galvanised Steel | WASHER,FLAT,16MM X 30MM X 5MM,STEEL,ROUND,GALV,TO AS1559 | FWM16STR | AUSTSTD | WEBSTERBSC | AS1559 | 12 months | No
consumables - rare | 3 | Consumables | 065158 | Washer Flat 16mm X 50mm X 4mm Round Galvanised Steel | WASHER,FLAT,16MM X 50MM X 4MM,STEEL,ROUND,GALV,TO AS1237 | FWM16HDG-BUILD | AUSTSTD | WEBSTERBSC | AS1237 | 12 months | No
consumables - rare | 3 | Consumables | 065617 | Washer Flat 20mm X 37mm X 3mm Round Galvanised Steel | WASHER,FLAT,20MM X 37MM X 3MM,STEEL,ROUND,GALV,TO AS1237 | FWM20HDG | AUSTSTD | WEBSTERBSC | AS1237 | 12 months | No
consumables - rare | 3 | Consumables | 065159 | Washer Flat 20mm X 60mm X 4mm Round Galvanised Steel | WASHER,FLAT,20MM X 60MM X 4MM,STEEL,ROUND,GALV,TO AS1237 | FWM20HDG-BUILD | AUSTSTD | WEBSTERBSC | AS1237 | 12 months | No
consumables - rare | 3 | Consumables | 066803 | Washer Flat 75mm X 75mm X 6mm Round Galvanised Steel | WASHER,FLAT,STEEL,75MM X 75MM X 6MM,SQUARE,GALV,M20 HOLE,FOR ITEM 323449 | SQFWM20X75X75X6G | RIDGE-BAT WASHERS | WEBSTERBSC | AS1237 | 12 months | No
consumables - rare | 3 | Consumables | 065613 | Washer Flat 8mm X 17mm X 1.6mm Round Galvanised Steel | WASHER,FLAT,8MM X 17MM X 1.6MM,STEEL,ROUND,GALV,TO AS1237 | FWM8HDG | AUSTSTD | WEBSTERBSC | AS1237 | 12 months | No
earthing | 2 | Approved | 103458 | Braid tinned Copper 25mm2 | SINGLE TYPE,COPPER CONDUCTOR,TINNED,25 MM,448/0.25 MM,FLAT SECT,FLEXIBLE | CB38R | Primex Electech Corporation | LEGEND CORP SERVICES P/L T/A LEGEND POWER SYSTEMS |  | 12 months | No
earthing | 2 | Approved | 102311 | Conductor 70mm2 Bare Cu for Earthing | AERIAL,ANNEALED BARE EARTHING, 70SQMM,COPPER,19/2.14 MM STRANDING,100M DRUM | 5015645 | PRYSMIAN | PRYSMIAN POWER CABLES & SYSTEMS AUSTRALIA PTY LTD |  | 5 years | No
earthing | 2 | Approved | 155184 | Driving Point for Earth Rod | HAND DRIVING,TO DWG D-OH1-1.7/12 22MM W O/A,14.4MM AF,55 MM HOLE D | DP13 | DULMISON | PREFORMED LINE PRODUCTS (AUST) |  | 12 months | No
earthing | 2 | Approved | 155136 | Earth Crimp - Conductor 50-70mm to Conductor 50-70mm | IRREVERSIBLE COMPRESSION CONNECTION, 50-70mm CABLE to 50-70mm CABLE, YGHC26C26 | YGH C26C26 | ERICO | ERICO LIGHTNING TECHN. P/L |  | 12 months | No
earthing | 2 | Approved | 155137 | Earth Crimp - Conductor 50-70mm to Conductor 95-120mm | IRREVERSIBLE COMPRESSION CONNECTION, 50-70mm CABLE to 95-120mm CABLE, YGHC29C26 | YGH C29C26 | ERICO | ERICO LIGHTNING TECHN. P/L |  | 12 months | No
earthing | 2 | Approved | 155138 | Earth Crimp - Conductor 95-120mm to Conductor 95-120mm | IRREVERSIBLE COMPRESSION CONNECTION, 95-120mm CABLE to 95-120mm CABLE, YGHC29C29 | YGH C29C29 | ERICO | ERICO LIGHTNING TECHN. P/L |  | 12 months | No
earthing | 2 | Approved | 155133 | Earth Rod Clamp (13-15mm Electrode to 16-120mm Conductor) | EARTHING TYPE,13-15MM ELECTRODE,SUITABLE FOR 16-120SQMM EARTH LEAD | D-CLAMP210 |  | PREFORMED LINE PRODUCTS (AUST) |  | 12 months | No
earthing | 2 | Approved | 155134 | Earth Crimp - Rod 13-16mm to Conductor 50-70mm | IRREVERSIBLE COMPRESSION CONNECTION, 13-16mm EARTH ROD to 50-70mm CABLE, YGHP29C26 | YGH P29C26 | ERICO | ERICO LIGHTNING TECHN. P/L |  | 12 months | No
earthing | 2 | Approved | 155135 | Earth Crimp - Rod 13-16mm to Conductor 95-120mm | IRREVERSIBLE COMPRESSION CONNECTION, 13-16mm EARTH ROD to 95-120mm CABLE, YGHP29C29 | YGH P29C29 | ERICO | ERICO LIGHTNING TECHN. P/L |  | 12 months | No
earthing | 2 | Approved | 155010 | Earth Electrode 1800 x 13mm Dia. (Solid Flush Coupling, Extendable) | STEEL, COPPER CLAD, 1800mm LG, 13mm DIA, SOLID FLUSH COUPLING, EXTENDABLE | 611360 | ERICO | ERICO LIGHTNING TECHN. P/L |  | 12 months | No
earthing | 2 | Approved | 155132 | Earth Rod Clamp (Brass) for 10-35sq-mm Cable | EARTHING TYPE,COPPER ALLOY CAST BODY,13 MM,TO DWG D-OH1-1.7/12 | GRC5 | DULMISON | PREFORMED LINE PRODUCTS (AUST) |  | 12 months | No
earthing | 2 | Approved | 155145 | Earth Rod Coupling 13mm (cw locking pin) | 13MM, COMPLETE WITH LOCKING PIN, DWG D-OH1-1.7/12 | CC12F | ERICO | ERICO LIGHTNING TECHN. P/L |  | 12 months | No
earthing | 2 | Approved | 155171 | Earth Rod Driving Head | TEMPERED / HARDENED DRIVING HEAD to SUIT 1/2" EARTH ROD (611360 SIN 155010) | 158120 | ERICO | ERICO LIGHTNING TECHN. P/L |  | 12 months | No
earthing | 2 | Approved | 147350 | Earthing Crimp - Conductor 50-70mm to Conductor 50-70mm (CEC070) | COMPRESSION,PARALLEL,35 MM TO 70 MM DIACOND,35 MM TO 70 MM TAP,BURNDY YGHC | D-CEC070 | PLP | PREFORMED LINE PRODUCTS (AUST) |  | 12 months | No
earthing | 3 | Consumables | 117440 | Earthing Resistance Reducing Compound GEM (11.1 kg Bag) | COMPOND,POWDER,11.1 KG PAPER BAG, C/W INSTRUCTIONS,90 BAGS PER PALLET GEM | GEM25A | ERICO | ERICO LIGHTNING TECHN. P/L | IEC 62561-7 | 12 months | No
earthing | 3 | Consumables | 117432 | Earthing Resistance Reducing Compound LO-OHM (15 kg Bag) | POWDER,15 KG PAPER BAG, C/W INSTRUCTIONS 60 BAGS PER PALLET LO-OHM |  | GOOD EARTH | J F MACHINERY PTY LTD | IEC 62561-7 | 12 months | No
earthing | 2 | Approved | 155182 | Machine Driving Pin for Earth Rod | GROUND ROD,TO DWG D-OH1-1.7/1222 MM W O/A,14.4 MM AF,55 MM HOLE D | MDP10M | DULMISON | PREFORMED LINE PRODUCTS (AUST) |  | 12 months | No
earthing | 2 | Approved | 146860 | Split Bolt Clamp (for 35sq-mm Earth Leads) | SPLIT BOLT CLAMP,SUITABLE FOR 35SQMM COPPER CABLE TO METAL PLATE FOR CONNECTION TO EARTH STUD IN LV CABINETS SBC24L | SBC24L | CABACC | LEGEND CORP SERVICES P/L T/A LEGEND POWER SYSTEMS |  | 12 months | No
earthing | 2 | Approved | 146859 | Split Bolt Clamp (for 70-120sq-mm Earth Leads) | SPLIT BOLT CLAMP,SUITABLE FOR 70 TO 120MMSQ EARTH LEAD | SBC26L | CABACC | LEGEND CORP SERVICES P/L T/A LEGEND POWER SYSTEMS |  | 12 months | No
earthing | 2 | Approved | 077556 | Polymeric streetlight pit | POLYMERIC, 320 MM X 530 MM LID | D-PIT300D |  | PREFORMED LINE PRODUCTS (AUST) |  | 12 months | No
earthing | 2 | Approved | 077557 | Streetlight Pit Concrete Lid (Tamperproof) | T/PROOF ELECTRICAL TO SUIT D-PIT300D | D-PIT300DLCTE |  | PREFORMED LINE PRODUCTS (AUST) |  | 12 months | No
enclosure - cabinet | 2 | Approved | 237370 | Cabinet, Fuse Link 200A 700x500x250 | FOR FUSE LINK,200 A,PRIMED & PAINTED,700 MM H,500 MM W,250 MM D, TO DWG D-UG1-1.6/11 | 237370 | DYNAMIC WELDING & ENGINEERING | DYNAMIC WELDING & ENGINEERING |  | 12 months | Yes
enclosure - cabinet | 2 | Approved | 237371 | Cabinet, Fuse Link 400A 1000x500x250 | GREY,FOR FUSE LINK,400 A,1000 MM H, 500 MM W,250 MM D, PRIMED & PAINTED,TO DWG D-UG1-1.6/11 | 237371 | DYNAMIC WELDING & ENGINEERING | DYNAMIC WELDING & ENGINEERING |  | 12 months | Yes
enclosure - cabinet | 2 | Approved | 237372 | Cabinet, Fuse Link 400A 1100x750x300 | FUSE LINK,400 A,EXTRA LARGE,1100 MM H, 750 MM W,300 MM D,PRIMED & PAINTED,TO DWG D-UG1-1.6/11 | 237372 | DYNAMIC WELDING & ENGINEERING | DYNAMIC WELDING & ENGINEERING |  | 12 months | Yes
enclosure - cabinet | 2 | Approved | 312051 | Insulation panel 400x400x12 for LV Fuse Cabinetsfor LV Fuse Cabinets | PHENOLIC PAPER LAMINATED,BLACK,400 MMLG,400 MM W,12 MM THK,TYPE X,AS 1795 | 312051 | EMT | REXEL |  | 12 months | No
enclosure - cabinet | 2 | Approved | 312052 | Insulation panel 600x400x12 for XL LV Fuse Cabinets | PHENOLIC PAPER LAMINATED,BLACK,600 MMLG,400 MM W,12 MM THK,TYPE X,AS 1795 | 312052 | EMT | REXEL |  | 12 months | No
enclosure - cabinet | 2 | Approved | 237380 | Support Frame 200 & 400amp Fuse Link Cabinet | FUSE LINK CABINET,200 A & 400 A,GALV C/W 1 GALV L BRACKET,TO DWG D-UG1-1.6/10 | 237380 | DYNAMIC WELDING & ENGINEERING | DYNAMIC WELDING & ENGINEERING |  | 12 months | No
enclosure - cabinet | 2 | Approved | 237373 | Support Frame extra large 400amp Fuse Link Cabinet | FUSE LINK CABINET,400 A,GALV,EXTRA LARGE,C/W BRACKET - ITEM 2,TO DWG D-UG1-1.6/10 | 237373 | DYNAMIC WELDING & ENGINEERING | DYNAMIC WELDING & ENGINEERING |  | 12 months | No
enclosure - turret | 2 | Approved | 312053 | Fuse Panel Turret (XL) - 600H x 320W | 01BDP46 TYPE 'X' SWITCH PANEL, BLACK 600H x320W x 10THICK, 0.28Kg | 01BDP46 | FULTON INDUSTRIES AUST P/L | FULTON INDUSTRIES AUST P/L |  | 36 months | No
enclosure - turret | 2 | Approved | 032896 | Pan HD M10 X 35 Tamper proof | STAINLESS STEEL GR340 D HEAD for TURRET BASES | RS3000 | Flowline Industries Pty Ltd | FLOWLINE INDUSTRIES PTY LTD |  | 36 months | No
enclosure - turret | 2 | Approved | 325742 | Turret Base (Series 2) | POLYETHYLENE,HIGH DENSITY, GREEN, 350 MM H550 MM LG, 510 MM W SERIES II,C/W SCREWS | ES1006 | Flowline Industries Pty Ltd | FLOWLINE INDUSTRIES PTY LTD |  | 36 months | No
enclosure - turret | 2 | Approved | 325754 | Turret Base (XL) - 300H x 330W x 530D | PB4G POLY BASE GRN, SPHPB4 SLIDING PANEL HOLDER, APP PANEL SIZE: 600MMLx320MMWx10mmTHICK, COMPLETE WITH CHAMFERS ON BOTTOM CORNERS OF 320MM | PB4G/SPH/BDP | FULTON INDUSTRIES AUST P/L | FULTON INDUSTRIES AUST P/L |  | 36 months | No
enclosure - turret | 2 | Approved | 325745 | Turret Cover | POLYETHYLENE,GREEN,TOP & BOTTOM VENTING,TALL URD TURRET TOP | ES1002 | Flowline Industries Pty Ltd | FLOWLINE INDUSTRIES PTY LTD |  | 36 months | No
enclosure - turret | 2 | Approved | 325753 | Turret Cover (XL) - 600H x 325W x 330D | PPB4TVG GRN VENTED POLY PILLAR UV STABILISED, 600MMHx325MMWx330MMD, COMPLETE WITH PSFB2 BUTTON SECURITY BOLTS/WASHERS, | PPB4TVGAUR | FULTON INDUSTRIES AUST P/L | FULTON INDUSTRIES AUST P/L |  | 36 months | No
enclosure - turret | 2 | Approved | 325730 | Turret Fuse Panel Melamine - 3 x S/Fuses + S/L & N/Link | MELAMINE PANEL, FOR URD TURRET 3 FUSE PILLAR,PRE WIRED,WITH NEUTRAL LINK,495mm H,205mm W | ETSA035/1 | Flowline Industries Pty Ltd | HAMMER CONTRACTING PTY LTD |  | 36 months | No
enclosure - turret | 2 | Approved | 325729 | Turret Fuse Panel Melamine - 6 x S/Fuses + S/L & N/Link | PANEL, URD TURRET, 6 FUSE PANEL, PREWIRED WITH 6 SERVICE FUSES,STREELIGHT FUSE & NEUTAL LINK | as per UG-618 | HAMMER CONTRACTING PTY LTD | HAMMER CONTRACTING PTY LTD |  | 36 months | No
enclosure - turret | 2 | Approved | 325727 | Turret Fuse Panel Melamine - Blank (492 x 205) | MELAMINE PANEL, FOR URD TURRET SERVICE FUSES, 495 MM LG, 205 MM W BLANK | N/A | HAMMER CONTRACTING PTY LTD | HAMMER CONTRACTING PTY LTD |  | 36 months | No
fuses | 2 | Approved | 222425 | Fuse Cartridge 100amp ferrule 30.2mm dia | 100 A,440 V,FERRULE TYPE,30.2 MM DIA,57 MM LG,TO AS 2005 | RHLF100 | TIRH | IPD GROUP LTD |  | 12 months | No
fuses | 2 | Approved | 222933 | Fuse Cartridge 10A 415V Offset NS10 | 10A,415V,STAGGERED OFFSET TAG,HRC,CLIPFIXING,13.9MM DIA,58.7MM LG,TO AS 2005 | NSD10 | BUSSMANN | ADAPT AUSTRALIA PTY LTD |  | 12 months | No
fuses | 2 | Approved | 222423 | Fuse Cartridge 60amp ferrule 30.2mm dia | 60A,440V,FERRULE TYPE,30.2MM DIA,57MM LG,TO AS 2005 | RHLF60 | TIRH | IPD GROUP LTD |  | 12 months | No
fuses | 2 | Approved | 222932 | Fuse Cartridge 6A 415V Offset NSD6 | 6A,415V,STAGGERED OFFSET TAG,HRC,CLIPFIXING,13.9 MM DIA,58.7 MM LG,TO AS 2005 | NSD6 | BUSSMANN | ADAPT AUSTRALIA PTY LTD |  | 12 months | No
fuses | 2 | Approved | 222424 | Fuse Cartridge 80amp ferrule 30.2mm dia | 80A,440V,FERRULE TYPE,30.2MM DIA,57MM LG,TO AS 2005 | RHLF80 | TIRH | IPD GROUP LTD |  | 12 months | No
fuses | 2 | Approved | 220665 | Fuseholder 100A 440V Front Connect | 100 A,440 V,MOULDED,FRONT CONNECTION,SHROUDED,TO AS 2005,35 SQMM MAX COND | S71002BFW | JANDA | IPD GROUP LTD |  | 12 months | No
fuses | 2 | Approved | 220594 | Streetlight Fuseholder, base and carrier | 32A,415V,SHROUDED,CLIP IN TYPE, BUSBAR CONNECTED,BLACK, A S2005 | SC32BH | GE | IPD GROUP LTD |  | 12 months | No
fuses | 2 | Approved | 222374 | Streetlight fuse link, cartridge | 6 A,MIDGET,13/32 IN DIA,1-1/2 LG,LITTELFUSE KLK 6 | ATM6 | MERSEN | FUSECO POWER SOLUTIONS PTY LTD |  | 12 months | No
fuses | 2 | Approved | 222375 | Streetlight Fuse holder | IN-LINE,W/PROOF,MOULDED,FOR 6 & 10 AMPMIDGET FUSE SIZE 13/32 DIA X1-1/2 LGTH, | LEBAAS | BUSSMANN | FUSECO POWER SOLUTIONS PTY LTD |  | 12 months | No
fuses | 2 | Approved | 220590 | Fuseholder 32A 415V Front Connect | 32 A,415 V,SHROUDED,CLIP-INTYPE,FRONT CONNECTION,BLACK,TO AS 2005 | SC32H | JANDA | IPD GROUP LTD |  | 12 months | No
heatshrink | 2 | Approved | 168077 | Breakout Boot 185 & 240mm2 11 & 22kV | HEAT SHRINK,MOULDED SHAPE,3 WAY,FOR 3C185 & 240SQMM, XLPE,11 & 22KV CABLES | 402W526/S(S5) | RAYCHEM | TYCO ELECTRONICS - ENERGY DIV. |  | 24 months | No
heatshrink | 2 | Approved | 168085 | Breakout Boot 4 Way 185 to 400mm2 LV | HEAT SHRINK,4 WAY,MOULDED SHAPE,LOWVOLTAGE,ADHESIVE,185 TO 400 SQMM CABLE | 502K026/S(S5) | RAYCHEM | TYCO ELECTRONICS - ENERGY DIV. |  | 24 months | No
heatshrink | 2 | Approved | 168081 | Breakout Boot 4 Way 4 to 35mm2 LV | HEAT SHRINK,4 WAY,MOULDED SHAPE,LOWVOLTAGE,ADHESIVE,4 TO 35 SQMM CABLE | 502K033-53/42 | RAYCHEM | TYCO ELECTRONICS - ENERGY DIV. |  | 24 months | No
heatshrink | 2 | Approved | 168083 | Breakout Boot 4 Way 70 to 150mm2 LV | HEAT SHRINK,4 WAY,MOULDED SHAPE,LOWVOLTAGE,ADHESIVE,70 TO 150 SQMM | 502K016/S(S5) | RAYCHEM | TYCO ELECTRONICS - ENERGY DIV. |  | 24 months | No
heatshrink | 2 | Approved | 169840 | Cable Id Heatshrink Sleeve RWB 25mm x 25mm long | HEAT-SHRINKABLE TYPE,RED,BLUE & WHITE,1 IN,3 X 25 MM LG,PHASE IDENTIFICATION | 781002-001+COLOUR-CODING-1 | RAYCHEM | TYCO ELECTRONICS - ENERGY DIV. |  | 24 months | No
heatshrink | 2 | Approved | 169841 | Cable Id Heatshrink Sleeve RWB 38mm x 25mm long | HEAT-SHRINKABLE TYPE TUBING, RED, BLUE & WHITE,1-1/2 IN,3 X 25 MM LG, | COLOUR-CODING-1-1/2 | RAYCHEM | TYCO ELECTRONICS - ENERGY DIV. |  | 24 months | No
heatshrink | 2 | Approved | 169842 | Cable Id Heatshrink Sleeve RWB 50mm x 25mm long | HEAT-SHRINKABLE TYPE,RED,BLUE & WHITE,2 IN,3 X 25 MM LG,PHASE IDENTIFICATION | COLOUR-CODING-2 | RAYCHEM | TYCO ELECTRONICS - ENERGY DIV. |  | 24 months | No
heatshrink | 2 | Approved | 169558 | Cable Sleeve ATUM 12/4 1200 LV | HEAT SHRINK,BLACK,INTERNAL ADHESIVECOATING,1200 MM LG,12 MM NOMINAL DIA. | ATUM-12/4-0-STK | RAYCHEM | TYCO ELECTRONICS - ENERGY DIV. |  | 24 months | No
heatshrink | 2 | Approved | 168955 | Cable Sleeve CRSM 107/29 1500/232 | LOW VOLTAGE,WATERPROOF,THICK WALL,1500MM LG,FOR 35MM TO 55MM CABLE REPAIR TYCO 'CRSM' TYPE | 107/29-1500/239(B10) | RAYCHEM | TYCO ELECTRONICS - ENERGY DIV. |  | 24 months | No
heatshrink | 2 | Approved | 168954 | Cable Sleeve CRSM 84/20 1500/172 | LOW VOLTAGE,WATERPROOF,THICK WALL,1500MM LG,FOR 25MM TO 40MM CABLE REPAIR TYCO 'CRSM' TYPE | 84/20-1500/239(B15) | RAYCHEM | TYCO ELECTRONICS - ENERGY DIV. |  | 24 months | No
heatshrink | 2 | Approved | 168448 | Cable Sleeve MWTM 10/3 1200mm (Med Wall Mastic) | HEAT SHRINKABLE TYPE,TUBING BLACK,ADHESIVE SEALANT COAT,MED WALL,1200 MM LG, 10 MM TO 3 MM | MWTM-10/3-1200/S(S25 | RAYCHEM | TYCO ELECTRONICS - ENERGY DIV. |  | 24 months | No
heatshrink | 2 | Approved | 168450 | Cable Sleeve MWTM 160/50 1000mm (Heavy Wall Mastic) | HEAVY WALL INSULATION & OUTER SEALING SLEEVE, HEAT - SHRINKABLEWSCM 160/50 | WCSM-160/50-1000/S(S5) | RAYCHEM | TYCO ELECTRONICS - ENERGY DIV. |  | 24 months | No
heatshrink | 2 | Approved | 168420 | Cable Sleeve MWTM 25/8 1200mm (Med Wall Mastic) | HEAT SHRINK,TUBING,BLACK,ADHESIVE SEALANT COAT,MED WALL, 25 MM TO 8 MM,1200 MM LG | MWTM-25/8-1200/S(S10 | RAYCHEM | TYCO ELECTRONICS - ENERGY DIV. |  | 24 months | No
heatshrink | 2 | Approved | 168426 | Cable Sleeve MWTM 35/12 1200mm (Med Wall Mastic) | HEAT SHRINK TUBING ,BLACK,ADHESIVE SEALANT COAT, MED WALL,1200 MM LG,LV 35/12 TUBE | MWTM 35/12-1200/172 | RAYCHEM | TYCO ELECTRONICS - ENERGY DIV. |  | 24 months | No
heatshrink | 2 | Approved | 168446 | Cable Sleeve MWTM 50/16 1200mm (Med Wall Mastic) | HEAT SHRINKABLE TYPE,TUBING, BLACK,ADHESIVE SEALANT COAT,50/16 LV TUBE, MED WALL,1200 MM LG,50 MM TO 16 MM | MWTM-50/16-1200S(S10 | RAYCHEM | TYCO ELECTRONICS - ENERGY DIV. |  | 24 months | No
heatshrink | 2 | Approved | 169019 | Cable Sleeve MWTM 50/16 25m Roll (Med Wall Uncoated) | HEAT SHRINK TUBING, BLACK,UNCOATED,MED WALL,50 MM TO 16 MM,25 M SPOOL | MWTM-50/16-A/U-4(S25 | RAYCHEM | TYCO ELECTRONICS - ENERGY DIV. |  | 24 months | No
heatshrink | 2 | Approved | 168444 | Cable Sleeve MWTM 85/25 1200mm (Med Wall Mastic) | HEAT SHRINK,TUBING,BLACK,ADHESIVE COATED 1200 MM LG,85 MM EXP ID | MWTM-85/25-1200/S(S5 | RAYCHEM | TYCO ELECTRONICS - ENERGY DIV. |  | 24 months | No
heatshrink | 2 | Approved | 168442 | Cable Sleeve MWTM 95/29 1200mm (Med Wall Mastic) | HEAT SHRINK,TUBING,BLACK,ADHESIVE SEALANT COAT MED WALL,1200 MM LG, 95 MM TO 29 MM | MWTM-95/29-1200/S(S5 | RAYCHEM | TYCO ELECTRONICS - ENERGY DIV. |  | 24 months | No
heatshrink | 2 | Approved | 169090 | Cable Sleeve RNF100 12/6 1200mm (Thin Wall Uncoated) | POLYOLEFIN,BLACK,LOW VOLT,FLAME RETARD,INDOOR,THIN WALL,1.2M LG, 12.7MM TO 6.4MM, | RNF100-1/2-0-BLK-STK | RAYCHEM | TYCO ELECTRONICS - ENERGY DIV. |  | 24 months | No
heatshrink | 2 | Approved | 169091 | Cable Sleeve RNF100 19/9 1200mm (Thin Wall Uncoated) | POLYOLEFIN,BLACK,LOW VOLT,FLAME RETARD,INDOOR,THIN WALL,1.2M LG, 19.1MM TO 9.5MM, | RNF100-3/4-0-BLK-STK | RAYCHEM | TYCO ELECTRONICS - ENERGY DIV. |  | 24 months | No
heatshrink | 2 | Approved | 169092 | Cable Sleeve RNF100 25/12 1200mm (Thin Wall Uncoated) | HEAT SHRINKABLE TYPE,POLYOLEFIN, BLACK,LOW VOLT FLAME RETARDED, INDOOR, THIN WALL | RNF100-1-0-BLK-STK | RAYCHEM | TYCO ELECTRONICS - ENERGY DIV. |  | 24 months | No
heatshrink | 2 | Approved | 169093 | Cable Sleeve RNF100 38/19 1200mm (Thin Wall Uncoated) | HEAT SHRINKABLE TYPE, POLYOLEFIN, BLACK,LOW VOLT FLAME RETARDED, INDOOR,THIN WALL | RNF100-1-1/2-0BKSTK | RAYCHEM | TYCO ELECTRONICS - ENERGY DIV. |  | 24 months | No
heatshrink | 2 | Approved | 169094 | Cable Sleeve RNF100 50/25 1200mm (Thin Wall Uncoated) | HEAT SHRINKABLE TYPE, POLYOLEFIN,BLACK.LOW VOLT FLAME RETARDED,INDOOR,THIN WALL, | RNF100-2-0 BLACK-STK | RAYCHEM | TYCO ELECTRONICS - ENERGY DIV. |  | 24 months | No
heatshrink | 2 | Approved | 169095 | Cable Sleeve RNF100 76/38 1200mm (Thin Wall Uncoated) | HEAT SHRINKABLE TYPE,POLYOLEFIN, BLACK,LOW VOLT.FLAME RETARDED, INDOOR,THIN WALL | RNF100-3-0-BLACK-STK | RAYCHEM | TYCO ELECTRONICS - ENERGY DIV. |  | 24 months | No
heatshrink | 2 | Approved | 169158 | Cable Sleeve Thin Walled Unlined (13-6mm) - BLACK | HEAT SHRINK,THIN WALLED,UNLINED,13-6MM,BLACK,50M ROLL | XLP13BK | CABACC | REXEL |  | 12 months | No
heatshrink | 2 | Approved | 169157 | Cable Sleeve Thin Walled Unlined (13-6mm) - BLUE | HEAT SHRINK,THIN WALLED,UNLINED,13-6MM,BLUE,25M ROLL | XLP13BL | CABACC | REXEL |  | 12 months | No
heatshrink | 2 | Approved | 169159 | Cable Sleeve Thin Walled Unlined (13-6mm) - GREEN/YELLOW | HEAT SHRINK,THIN WALLED,UNLINED,13-6MM,GREEN/YELLOW,50M ROLL | XLP13YG | CABACC | REXEL |  | 12 months | No
heatshrink | 2 | Approved | 169155 | Cable Sleeve Thin Walled Unlined (13-6mm) - RED | HEAT SHRINK,THIN WALLED,UNLINED,13-6MM,RED,50M ROLL | XLP13RD | CABACC | REXEL |  | 12 months | No
heatshrink | 2 | Approved | 169156 | Cable Sleeve Thin Walled Unlined (13-6mm) - WHITE | HEAT SHRINK,THIN WALLED,UNLINED,13-6MM,WHITE,25M ROLL | XLP13WH | CABACC | REXEL |  | 12 months | No
heatshrink | 2 | Approved | 169148 | Cable Sleeve Thin Walled Unlined (25-12mm) - BLACK | HEAT SHRINK,THIN WALLED,UNLINED,25-12MM,BLACK,50M ROLL | XLP25BK-CAB | CABACC | REXEL |  | 12 months | No
heatshrink | 2 | Approved | 169147 | Cable Sleeve Thin Walled Unlined (25-12mm) - BLUE | HEAT SHRINK,THIN WALLED,UNLINED,25-12MM,BLUE,50M ROLL | XLP25BL-CAB | CABACC | REXEL |  | 12 months | No
heatshrink | 2 | Approved | 169149 | Cable Sleeve Thin Walled Unlined (25-12mm) - GREEN/YELLOW | HEAT SHRINK,THIN WALLED,UNLINED,25-12MM,GREEN/YELLOW,50M ROLL | XLP25YG-CAB | CABACC | REXEL |  | 12 months | No
heatshrink | 2 | Approved | 169145 | Cable Sleeve Thin Walled Unlined (25-12mm) - RED | HEAT SHRINK,THIN WALLED,UNLINED,25-12MM,RED,50M ROLL | XLP25RD-CAB | CABACC | REXEL |  | 12 months | No
heatshrink | 2 | Approved | 169146 | Cable Sleeve Thin Walled Unlined (25-12mm) - WHITE | HEAT SHRINK,THIN WALLED,UNLINED,25-12MM,WHITE,50M ROLL | XLP25WH-CAB | CABACC | REXEL |  | 12 months | No
heatshrink | 2 | Approved | 169153 | Cable Sleeve Thin Walled Unlined (38-19mm) - BLACK | HEAT SHRINK,THIN WALLED,UNLINED,38-19MM,BLACK,25M ROLL | XLP38-BLACK | CABACC | REXEL |  | 12 months | No
heatshrink | 2 | Approved | 169152 | Cable Sleeve Thin Walled Unlined (38-19mm) - BLUE | HEAT SHRINK,THIN WALLED,UNLINED,38-19MM,BLUE,25M ROLL | XLP38-BLUE | CABACC | REXEL |  | 12 months | No
heatshrink | 2 | Approved | 169150 | Cable Sleeve Thin Walled Unlined (38-19mm) - RED | HEAT SHRINK,THIN WALLED,UNLINED,38-19MM,RED,25M ROLL | XLP38-RED | CABACC | REXEL |  | 12 months | No
heatshrink | 2 | Approved | 169151 | Cable Sleeve Thin Walled Unlined (38-19mm) - WHITE | HEAT SHRINK,THIN WALLED,UNLINED,38-19MM,WHITE,25M ROLL | XLP38-WHITE | CABACC | REXEL |  | 12 months | No
heatshrink | 2 | Approved | 168741 | Cable Sleeve WCSM 130/36 1200mm (Heavy Wall Mastic) | HEAT SHRINK,TUBING,BLACK,ADHESIVE COATED 1200 MM LG,130 MM EXP ID, 130mm-36mm | WCSM130/35-1200/S(S5 | RAYCHEM | TYCO ELECTRONICS - ENERGY DIV. |  | 24 months | No
heatshrink | 2 | Approved | 168745 | Cable Sleeve WCSM 51/16 1200mm (Heavy Wall Mastic) | HEATSHRINK TUBING,BLACK,ADHESIVE SEALANT COAT,THICK WALL,1200 MM LG 51 MM TO 16 MM | WCSM56/16-1200/S(S10 | RAYCHEM | TYCO ELECTRONICS - ENERGY DIV. |  | 24 months | No
heatshrink | 2 | Approved | 168733 | Cable Sleeve WCSM 70/21 1200mm (Heavy Wall Mastic) | HEAT SHRINK,TUBING,BLACK,ADHESIVE COATED 1200 MM LG ,68 MM EXP ID, | WCSM70/20-1200/S(S10 | RAYCHEM | TYCO ELECTRONICS - ENERGY DIV. |  | 24 months | No
heatshrink | 2 | Approved | 168017 | End Cap No.2 8/17mm dia heatshrink | HEAT SHRINKABLE TYPE, 8-17 MM DIA RANGE 55 MM LG,20 MM EXPANDED ID | 102L022/S(S100) | RAYCHEM | TYCO ELECTRONICS - ENERGY DIV. |  | 24 months | No
heatshrink | 2 | Approved | 168019 | End Cap No.3 17/30mm dia heatshrink | HEAT SHRINKABLE TYPE: 17-30 MM DIA RANGE,110 MM LG,35 MM EXPANDED ID | 102L033/S(S100) | RAYCHEM | TYCO ELECTRONICS - ENERGY DIV. |  | 24 months | No
heatshrink | 2 | Approved | 168021 | End Cap No.4 30/45mm dia heatshrink | HEAT SHRINKABLE TYPE 30-45 MM DIA RANGE,143 MM LG EXPANDED ID | 102L044/S(S50) | RAYCHEM | TYCO ELECTRONICS - ENERGY DIV. |  | 24 months | No
heatshrink | 2 | Approved | 168026 | End Cap No.5 65/95mm dia heatshrink | HEAT SHRINKABLE TYPE, 65-95 MM DIA RANGE,145 MM LG,100 MM EXPANDED ID, | 102L055/S(S10) | RAYCHEM | TYCO ELECTRONICS - ENERGY DIV. |  | 24 months | No
heatshrink | 2 | Approved | 168028 | End Cap No.6 95/115mm dia heatshrink | 95-115 MM DIA RANGE,145 MM LG,120 MM,EXPANDED ID,70 MM RECOVERED ID | 102L066/S(S10) | RAYCHEM | TYCO ELECTRONICS - ENERGY DIV. |  | 24 months | No
HV accessories | 2 | Approved | 168040 | Dead End Plug 22kV for MiniPad Spare Bushings (K400DR-B) | 22kV RATED INSULATING CAP,FOR USE ON MINI PADP/No K400DRB | (K)(M)400DR-B | EUROMOLD | AUSTRALMOLD PTY LTD |  | 24 months | No
HV accessories | 2 | Approved | 165280 | Elbow Kit 11/22kV 3c Set | ELBOW SET,90 DEG,SUIT DIN SERIES 400ABOLTED TERMINATION,11/24KV XLPE CABLE,3 PHASE, | RSTI-5854 | RAYCHEM | TYCO ELECTRONICS - ENERGY DIV. |  | 24 months | Yes
HV accessories | 2 | Approved | 144144 | Joint Kit 11kV S/T 3c 240 400 XLPE (Tyco MXSU-3341) cw Shear Bolts | STRAIGHT THROUGH,12-17 KV 3 CORE XLPE12KV 240-400 SQ MM,17.5KV 185- 300 SQ MM, | MXSU-3341 | RAYCHEM | TYCO ELECTRONICS - ENERGY DIV. |  | 24 months | Yes
HV accessories | 2 | Approved | 144148 | Joint Kit 11kV S/T 3c 95 240 XLPE (Tyco MXSU-3331) cw Shear Bolts | STRAIGHT THROUGH,11KV 3 CORE XLPE95-240 SQ MM,C/W MECHANICAL CONNECTORS | MXSU-3331 | RAYCHEM | TYCO ELECTRONICS - ENERGY DIV. |  | 24 months | Yes
HV accessories | 2 | Approved | 144146 | Joint Kit 22kV S/T 3c 95 240 XLPE (Tyco MXSU-5331) cw Shear Bolts | STRAIGHT THROUGH TYPE,FOR 22 KV XLPECABLE 95 TO 240 SQMM, | MXSU-5331 | RAYCHEM | TYCO ELECTRONICS - ENERGY DIV. |  | 24 months | Yes
HV accessories | 2 | Approved | 144149 | Joint Kit LV S/T 3/4c 120 240 XLPE (Tyco AUST-HY33) | STRAIGHT THROUGH TYPE,FOR 3 OR 4 CORELV CABLE,XLPE/PVC 120-240MMRAYCHEM AUST-HY33 | AUST-HY33 | RAYCHEM | TYCO ELECTRONICS - ENERGY DIV. |  | 24 months | Yes
HV accessories | 3 | Consumables | 144099 | Resin for Joint Boxes (7.5 ltr) | POLYURETHANE COMPOUND - TO SUIT PARALLEL BRANCH, 11 KV JOINT BOXES, (ITEMS 144094,144097,144098), 7.5LTR, 3-PART | 53536-75 |  | IPD GROUP LTD |  | 24 months | No
HV accessories | 2 | Approved | 167340 | Term Kit indoor 22kV 35 70mm 1c XLPE (IXSU-F5121) | INDOOR,25-70 SQMM,1 CORE SCREENED,XLPE INSULATED CABLE,12.7/22 KV, | IXSU-F5121 | RAYCHEM | TYCO ELECTRONICS - ENERGY DIV. |  | 24 months | Yes
HV accessories | 2 | Approved | 165278 | Term Kit indoor 22kV 50 300mm 3x1c Tx Boot Kit HY22 | HEAT-SHRINKABLE,12.7/22 KV,FOR 50-300 SQMM CABLE, SET OF 3, RIGHT ANGLE, SUITED FOR | AUST-HY22 | RAYCHEM | TYCO ELECTRONICS - ENERGY DIV. |  | 24 months | Yes
HV accessories | 2 | Approved | 167344 | Term Kit indoor 22kV 70 185mm 3c XLPE | INDOOR,70-185 SQMM CONDUCTOR,TO SUIT 3 CORE XLPE SCREENED INSULATED CABLE, | IXSU-F5332 | RAYCHEM | TYCO ELECTRONICS - ENERGY DIV. |  | 24 months | Yes
HV accessories | 2 | Approved | 167346 | Term Kit outdoor 22kV 185 400mm 3c XLPE | OUTDOOR,240-300 SQMM CONDUCTOR, TO SUIT 22KV,3 CORE XLPE SCREENED INSULATED CABLE | OXSU-F5344 | RAYCHEM | TYCO ELECTRONICS - ENERGY DIV. |  | 24 months | Yes
HV accessories | 2 | Approved | 169738 | Tubing 11kV Heavy Wall 185/240mm2 Black XLPE (per m - 30m Coil) | BLACK,FLEXIBLE,HV,185 & 240SQMM 11KVXLPE CABLE,HEAVY WALL,UNCOATED,14M COIL | NT-1-1/2-0 | RAYCHEM | TYCO ELECTRONICS - ENERGY DIV. |  | 24 months | No
HV accessories | 2 | Approved | 169736 | Tubing 22kV Heavy Wall 185/240mm2 Black XLPE (per m - 22m Coil) | BLACK,FLEXIBLE,HV,185 & 240SQMM 22KVXLPE CABLE,HEAVY WALL,UNCOATED,22Mtr per COIL | NT-2-0 | RAYCHEM | TYCO ELECTRONICS - ENERGY DIV. |  | 24 months | No
HV accessories | 2 | Approved | 990903 | Voltage Presence Indicator - 11kV for Schneider RM6 & SM6 Switchgear | 11KV VOLTAGE PRESENCE INDICATOR, FOR SCHNEIDERHV SWITCHGEAR | VPI62406 | SCHIEDER ELECTRIC (AUST) PTY LTD | SCHNEIDER ELECTRIC PTY LTD |  | 12 months | No
HV accessories | 2 | Approved | 990902 | Voltage Presence Indicator - 22kV for Schneider RM6 & SM6 Switchgear | 22KV VOLTAGE PRESENCE INDICATOR, FOR SCHNEIDERHV SWITCHGEAR | VPI62408 | SCHIEDER ELECTRIC (AUST) PTY LTD | SCHNEIDER ELECTRIC PTY LTD |  | 12 months | No
lock | 1 | Prescribed | NA | cabinet locks - place order with TasNetworks | LOCK AS PER DWG UG-6xx, AREA SPECIFIC |  | TASNETWORKS | TASNETWORKS |  | 12 months | No
lock | 2 | Approved | 071457 | Padlocking Device for 100/160/250A Schneider/Merlin Gerin LV CB’s | FIXED TOGGLE TYPE,FOR 1 TO 3 PADLOCKS,SUITS MERLIN GERIN COMPACT NS100/160/250 CIRCUIT BREAKERS | 29371 | SCHIEDER ELECTRIC (AUST) PTY LTD | SCHNEIDER ELECTRIC PTY LTD |  | 12 months | No
lock | 2 | Approved | 071458 | Padlocking Device for 400/630/1600A Schneider/Merlin Gerin LV CB’s | FIXED TOGGLE TYPE,FOR 1 TO 3 PADLOCKS,SUITS MERLIN GERIN COMPACT NS400/630/1600 CIRCUIT BREAKERS | 32631 | SCHIEDER ELECTRIC (AUST) PTY LTD | SCHNEIDER ELECTRIC PTY LTD |  | 12 months | No
lock | 1 | Prescribed | NA | Substation Locks - place order with TasNetworks | LARGE PADLOCK - AREA SPECIFIC |  | TASNETWORKS | TASNETWORKS |  | 12 months | No
lock | 1 | Prescribed | NA | Switchgear Locks - place order with TasNetworks | SMALL PADLOCK - AREA SPECIFIC |  | TASNETWORKS | TASNETWORKS |  | 12 months | No
LV switchgear | 2 | Approved | 226613 | Circuit Breaker LV 250A Schneider/MG (to 185mm2 Cables) - NSX250N (Micrologic 2.2) | 250 A,185 SQMM CU TERMINALS & COVERS,ELECTRONIC (THERMAL & MAGNETIC) TRIP INCLUDE LOCKOUT DEVICE SI 071457 | MG 31630+29259+29323 | SCHIEDER ELECTRIC (AUST) PTY LTD | SCHNEIDER ELECTRIC PTY LTD |  | 5 years | No
LV switchgear | 2 | Approved | 226612 | Circuit Breaker LV 400A Schneider/MG (to 240mm2 Cables) - NSX400N (Micrologic 2.3) | 400 A,240 SQMM CU TERMINALS & COVERSELECTRONIC (THERMAL & MAGNETIC) TRIP INCLUDE LOCKOUT DEVICE SI 071458 | MG 32695+32479+32564 | SCHIEDER ELECTRIC (AUST) PTY LTD | SCHNEIDER ELECTRIC PTY LTD |  | 5 years | No
LV switchgear | 2 | Approved | 233671 | Switch Toggle 3-ph 440V 300A | SURFACE MTG 440V, 300A, 1 GANG, TP, FRONT WIRING c/w2 x LV432481 & 2 x LV432594 | INS-320 3P | SCHIEDER ELECTRIC (AUST) PTY LTD | REXEL |  | 12 months | No
miscellaneous | 2 | Approved | 077561 | Cable Cover Polymeric Orange 300mm x 5mm (per m on 15m Roll) | POLYMERIC,300MM W X 5MM TH,15 M ROLL,ORANGE,DANGER- ELECTRIC CABLE BELOW, TO AS4702 | OSC300/15 | Astron Plastics | REXEL |  | 12 months | No
miscellaneous | 3 | Consumables | 072222 | Concrete Quick Mix 20kg | RAPID SET,13 MPA STRENGTH AFTER 28 DAYS,20 KG BAG,TO AS 2758 | 885292 | CEMENT AUSTRALIA | BLACKWOODS | AS2758 | 12 months | No
miscellaneous | 3 | Consumables | 116026 | Conduit Glue | UPVC PIPE,METHYL ETHYL KETONE BASE,BLUE,LIQUID,250 ML CONTAINER | 82432 | VINIDEX | BLACKWOODS | AS3879 | 12 months | No
miscellaneous | 3 | Consumables | 117733 | Corrosion Prevention Compound - Aluminium Conductor/Connector 280mL | LIQUID TYPE,ALUMINIUM CONDUCTOR-CONNECTOR LUGS,280 ML SQUEEZE BOTTLE | 2253053 | BURNDY | BLACKWOODS | AS1231 | 12 months | No
miscellaneous | 2 | Approved | 117815 | Denso Tape 75mm x 10m Roll | PETROLEUM BASE IMPREGNATED & COATEDSYNTHETIC FABRIC,75 MM W,10 M ROLL | 7923435 | DENSO | BLACKWOODS |  | 12 months | No
miscellaneous | 3 | Consumables | 212063 | Lubricant (Cable Pulling) | CABLE PULLING LUBRICANT,1 LITRE BOTTLE | SWP1 | Slegers | REXEL |  | 12 months | No
miscellaneous | 2 | Approved | 402998 | Screwdriver - Turret D bolt | HEX DRIVE,DIA 25 ALLOY STEEL BAR,D BOLT TO AS14444/ X9931-U OR EQUIVALENT, OIL DIPPED FINISH, TO DWG D-UG |  | 0 | DYNAMIC WELDING & ENGINEERING |  | 12 months | No
miscellaneous | 3 | Consumables | 141690 | Tag - Cable ID 100x2.5mm | IDENTIFICATION TIE, NATURAL, TYPE IT18RT-NT,FOR UNDERGROUND CABLES | HTYIT18RT-NT | HellermannTyton | REXEL |  | 12 months | No
miscellaneous | 3 | Consumables | 141691 | Tag - Cable ID 3 Leg Tie | IDENTIFICATION TIE, NATURAL, TYPE IT50RT-NT,FOR UNDERGROUND CABLES | HTIT50RT-NT | HellermannTyton | REXEL |  | 12 months | No
miscellaneous | 3 | Consumables | 141692 | Tag - Cable ID 65x90mm White (pkt 25) | COLOUR CODED PLASTIC - WHITE, EYELET TOP CENTRE, | 46980 | Brady Australia | BLACKWOODS |  | 12 months | No
miscellaneous | 2 | Approved | 348630 | Tape Caution Buried Electric Cable Below 150mm (per 500m Roll) | LEGEND - `CAUTION-BURIED ELECTRIC CABLE BELOW',PLASTIC TAPE,150 MM X 500M | UGWT150-500 | Omega Power | BLACKWOODS | AS2648 | 12 months | No
neutral/earth | 2 | Approved | 141291 | Neutral Link 350A 7 Hole with cover Clipsal BP350/7 | 350 A,500 V,C/W BLACK BASE & COVER,7 WAY. | BP350/7 | CLIPSAL | REXEL |  | 12 months | No
neutral/earth | 2 | Approved | 141298 | Neutral Link Brass Alloy (19 x 19mm) - Uncovered | BRASS ALLOY,19X19,TO AS 1567-385 | AUR10NLV2 | JANDA | IPD GROUP LTD |  | 12 months | No
neutral/earth | 2 | Approved | 141296 | Neutral Link Brass Alloy (19 x 19mm) with 50x6 Cu Busbar & 2xM12 Brass Studs & Backing Plate | INCLUDES NEUTRAL LINK TASNETWORKS ITEM 141298 & 50 X 6 CU BUSBAR,2 X M12 BRASS STUDS AND BACKING PLATE | D-UG1-3.3/7 | KOSSMANN BROS PTY LTD | KOSSMANN BROS PTY LTD |  | 12 months | No
neutral/earth | 2 | Approved | 141294 | Neutral Link100A 3 x 6.3mm & 5 x 5.8mm Holes (for URD St Lt Poles) | 500V,100A,3 HOLES 6.3MM DIAMETER, 5 HOLES 5.8MM,URD ROADLIGHTING POLES,D-SLI-2.4/2 | L8 | CLIPSAL | REXEL |  | 12 months | No
sign | 2 | Approved | 325521 | Designation Plate "0" - Black on Reflectorised Background | ALUMINIUM,LEGEND - 0,BLACK LEGEND,GREY/WHITE REFLECTORISED BACKGROUND | 02416626 | Australian Graphics | BLACKWOODS |  | 12 months | No
sign | 2 | Approved | 325512 | Designation Plate "1" - Black on Reflectorised Background | ALUMINIUM,LEGEND - 1,BLACK LEGEND,GREY/WHITE REFLECTORISED BACKGROUND | 02416473 | Australian Graphics | BLACKWOODS |  | 12 months | No
sign | 2 | Approved | 325513 | Designation Plate "2" - Black on Reflectorised Background | ALUMINIUM,LEGEND - 2,BLACK LEGEND,GREY/WHITE REFLECTORISED BACKGROUND | 02416490 | Australian Graphics | BLACKWOODS |  | 12 months | No
sign | 2 | Approved | 325514 | Designation Plate "3" - Black on Reflectorised Background | ALUMINIUM,LEGEND - 3,BLACK LEGEND,GREY/WHITE REFLECTORISED BACKGROUND | 02416507 | Australian Graphics | BLACKWOODS |  | 12 months | No
sign | 2 | Approved | 325515 | Designation Plate "4" - Black on Reflectorised Background | ALUMINIUM,LEGEND - 4,BLACK LEGEND,GREY/WHITE REFLECTORISED BACKGROUND | 02416524 | Australian Graphics | BLACKWOODS |  | 12 months | No
sign | 2 | Approved | 325516 | Designation Plate "5" - Black on Reflectorised Background | ALUMINIUM,LEGEND - 5,BLACK LEGEND,GREY/WHITE REFLECTORISED BACKGROUND | 02416541 | Australian Graphics | BLACKWOODS |  | 12 months | No
sign | 2 | Approved | 325517 | Designation Plate "6" - Black on Reflectorised Background | ALUMINIUM,LEGEND - 6,BLACK LEGEND,GREY/WHITE REFLECTORISED BACKGROUND | 02416558 | Australian Graphics | BLACKWOODS |  | 12 months | No
sign | 2 | Approved | 325518 | Designation Plate "7" - Black on Reflectorised Background | ALUMINIUM,LEGEND - 7,BLACK LEGEND,GREY/WHITE REFLECTORISED BACKGROUND | 02416575 | Australian Graphics | BLACKWOODS |  | 12 months | No
sign | 2 | Approved | 325519 | Designation Plate "8" - Black on Reflectorised Background | ALUMINIUM,LEGEND - 8,BLACK LEGENDGREY/WHITE REFLECTORISED BACKGROUND | 02416592 | Australian Graphics | BLACKWOODS |  | 12 months | No
sign | 2 | Approved | 325520 | Designation Plate "9" - Black on Reflectorised Background | ALUMINIUM,LEGEND - 9,BLACK LEGEND,GREY/WHITE REFLECTORISED BACKGROUND | 02416609 | Australian Graphics | BLACKWOODS |  | 12 months | No
sign | 2 | Approved | 325522 | Designation Plate "A" - Black on Reflectorised Background | ALUMINIUM,LEGEND - A,BLACK LEGEND,GREY/WHITE REFLECTORISED BACKGROUND | 02416643 | Australian Graphics | BLACKWOODS |  | 12 months | No
sign | 2 | Approved | 325523 | Designation Plate "B" - Black on Reflectorised Background | ALUMINIUM,LEGEND - B,BLACK LEGEND,GREY/WHITE REFLECTORISED BACKGROUND | 02416898 | Australian Graphics | BLACKWOODS |  | 12 months | No
sign | 2 | Approved | 325535 | Designation Plate "P" - Black on Reflectorised Background | ALUMINIUM,LEGEND - P,BLACK LEGEND,GREY/WHITE REFLECTORISED BACKGROUND | 02416677 | Australian Graphics | BLACKWOODS |  | 12 months | No
sign | 2 | Approved | 325536 | Designation Plate "S" - Black on Reflectorised Background | ALUMINIUM,LEGEND - S,BLACK LEGEND,GREY/WHITE REFLECTORISED BACKGROUND | 02416694 | Australian Graphics | BLACKWOODS |  | 12 months | No
sign | 2 | Approved | 348412 | Guide Post White Powder Coated predrilled for Danger Signs | ROAD MARKER,POWDER COATED,WHITE,FOR DANGER SIGN,4 x PREDRILLED HOLES | HTS1500POSTW | RONDO | BLACKWOODS |  | 12 months | No
sign | 1 | Prescribed | 325540 | Pole Tag with 6 Digit ID Number - place order with TasNetworks |  |  | TASNETWORKS | TASNETWORKS |  | 12 months | No
sign | 2 | Approved | 348531 | Sign Customers Main Earth | LEGEND - 'CUSTOMERS MAIN EARTH DO NOTDISCONNECT,125 MM LG X 63 MM W X 4 MM TH | 2416847 | EYE SPY | BLACKWOODS |  | 12 months | No
sign | 2 | Approved | 348359 | Sign Danger 415 Volts Euipment Authorised Persons Only 600x450mm | LEGEND - 'DANGER - 415 VOLT EQUIPMENTAUTHORISED PERSONS ONLY',STEEL,600X450MM | 03200495 | EYE SPY | BLACKWOODS |  | 12 months | No
sign | 2 | Approved | 348452 | Sign Danger High Voltage Cables - Aluminium 305x255mm | "DANGER - HIGH VOLTAGE CABLES", ALUMINIUM, MK3 FORMAT, 305 x 255mm BLACK/RED/WHITE, LANDSCAPE ORIENTATION | AG19071203 | Australian Graphics | BLACKWOODS |  | 12 months | No
sign | 2 | Approved | 348370 | Sign Danger High Voltage Euipment - Aluminium 600x450mm | LEGEND - `DANGER-HIGH VOLTAGE EQUIPMENT'ALUMINIUM,600MM X 450MM,BAKED ENAMEL,DWG D-SS1-5.1/5 TYPE 1 | DHVE AL 60 | EYE SPY | BLACKWOODS |  | 12 months | No
sign | 2 | Approved | 348325 | Sign Danger High Voltage Euipment Authorised Persons only - Colourbond | LEGEND - 'DANGER HIGH VOLTAGE EQUIPMENT AUTHORISED PERSONNEL ONLY',METAL,1.6MM,COLOURBOND | 02416745 | Australian Graphics | BLACKWOODS |  | 12 months | No
sign | 2 | Approved | 348371 | Sign Danger High Voltage Euipment Authorised Persons only - Zinc Steel | LEGEND - `DANGER-HIGH VOLTAGE EQUIPMENTAUTHORISED PERSONS ONLY',ZINC STEEL | 32002291 | Australian Graphics | BLACKWOODS |  | 12 months | No
sign | 2 | Approved | 348411 | Sign Danger High Voltage for installation on Guide Posts | LEGEND - 'DIAL BEFORE YOU DIG', AURORA LOGO SCREEN PRINTED, PREDRILLED,150 MM X 100 MM,4 x PREDRILLED HOLES | DANSIGUNDGRCAB | PRATTS | BLACKWOODS |  | 12 months | No
sign | 2 | Approved | 348401 | Sticker "Caution Test Before Touching Insulated Luminaire May Be Energised" | LEGEND - 'CAUTION TEST BEFORE TOUCHING LUMINAIRE MAY BE ENERGISED',STICKER | 2416796 | EYE SPY | BLACKWOODS |  | 12 months | No
sign | 1 | Prescribed | 325580 | Substation Number Plate - place order with TasNetworks |  |  | TASNETWORKS | TASNETWORKS |  | 12 months | No
streetlight | 2 | Approved | 324994 | Decorative Column 5.5m Silhouette (for Bottom entry roadlight fitting) | STREETLIGHT,5.5M,SILHOUETTE DECORATIVE POLE FOR USE WITH BOTTOM ENTRY ROADLIGHT FITTING | Silhouette Bottom entry | ARTCRAFT URBAN GROUP PTY LTD | ARTCRAFT URBAN GROUP PTY LTD |  | 12 months | Yes
streetlight | 2 | Approved | 324992 | Decorative Column 5.5m Silhouette (for Side entry roadlight fitting) | STREETLIGHT,5.5M,SILHOUETTE DECORATIVE POLE FOR USE WITH SIDE ENTRY ROADLIGHT FITTING | Silhouette Side entry | ARTCRAFT URBAN GROUP PTY LTD | ARTCRAFT URBAN GROUP PTY LTD |  | 12 months | Yes
streetlight | 2 | Approved | 324993 | Decorative Column 5.5m Silhouette (for Top entry roadlight fitting) | STREETLIGHT,5.5M,SILHOUETTE DECORATIVE POLE FOR USE WITH TOP ENTRY ROADLIGHT FITTING | Silhouette Top entry | ARTCRAFT URBAN GROUP PTY LTD | ARTCRAFT URBAN GROUP PTY LTD |  | 12 months | Yes
streetlight | 2 | Approved | 324971 | Steel Column 7.5m with 2m outreach | 7.5H, SLIP JOINT, 2M CURVED OUTREACH ARM, GALV, OCT TUBULAR TAPPERED URD RIGID, PIPE SPIGOT, PER DWG GA5746 | SAL75G/S20 | INGAL EPS | INGAL EPS |  | 12 months | Yes
streetlight | 2 | Approved | 325092 | Steel Column 7m with 0.6m outreach | STEEL,TUBULAR,TAPERED,SLIP JOINT,7 M,OCTC/W 600 MM OUTREACH ARM, GALV | HEC/FSL60G/XSA600 | INGAL EPS | INGAL EPS |  | 12 months | Yes
Streetlight | 2 | Approved | 324972 | Steel Column 7.5m with 2m outreach | GALV, OCT TAPPERED, RIGID, MAIN RD, 7.5M HSLIP JOINT, F/MOUNTED, 2M CURVED O/ARM | SAL90F/S20 | RIVERTON | INGAL EPS |  | 12 Months | Yes
Streetlight | 2 | Approved | 324973 | Steel Column 9m with 2m outreach | GALV, OCT TAPPERED, RIGID, MAIN RD, 9M HSLIP JOINT, F/MOUNTED, 2M CURVED O/ARM | SAL90F/S20 | RIVERTON | INGAL EPS |  | 12 Months | Yes
Streetlight | 2 | Approved | 324974 | Steel Column 9m with 3m outreach | GALV, OCT TAPPERED, RIDGID, MAIN RD, 9M HSLIP JOINT, F/MOUNTED, 3M CURVED O/ARM | SAL90F/S30 | RIVERTON | INGAL EPS |  | 12 Months | Yes
Streetlight | 2 | Approved | 324975 | Steel Column 10.5m with 2m outreach | GALV, OCT TAPPERED, RIGID, MAIN RD,10.5MSLIP JOINT, F/MOUNTED, 2M CURVED O/ARM | SAL105F/S20 | RIVERTON | INGAL EPS |  | 12 Months | Yes
Streetlight | 2 | Approved | 324976 | Steel Column 10.5m with 3m outreach | GALV, OCT TAPPERED, RIGID, MAIN RD,10.5MSLIP JOINT, F/MOUNTED, 3M CURVED O/ARM | SAL105F/S30 | RIVERTON | INGAL EPS |  | 12 Months | Yes
Streetlight | 2 | Approved | 324977 | Steel Column 10.5m with 4.5m outreach | GALV, OCT TAPPERED, RIGID, MAIN RD,10.5MSLIP JOINT, F/MOUNTED, 4.5M CURVED O/ARM | SFL105F/S45 | RIVERTON | INGAL EPS |  | 12 Months | Yes
Streetlight | 2 | Approved | 324978 | Steel Column 12m with 4.5m outreach | GALV, OCT TAPPERED, RIGID, MAIN RD, 12 MSLIP JOINT, F/MOUNTED, 4.5M CURVED O/ARM | SFL12F/S45 | RIVERTON | INGAL EPS |  | 12 Months | Yes
Streetlight | 2 | Approved | 324980 | Steel Column Frangible 9m 3m outreach | GALV,OCT TAPPERED,IMPACT ABSORBING, 9M HSLIP JOINT, F/MUNTED, 3M CURVED O/ARM | SFL90FIA/S30 | RIVERTON | INGAL EPS |  | 12 Months | Yes
Streetlight | 2 | Approved | 324981 | Steel Column Frangible 10.5m 2m outreach | GALV,OCT TAPPERED,IMPACT ABSORBING,10.5MSLIP JOINT, F/MOUNTED, 2M CURVED O/ARM | SFL105FIA/S20 | RIVERTON | INGAL EPS |  | 12 Months | Yes
Streetlight | 2 | Approved | 324982 | Steel Column Frangible 10.5m 3m outreach | GALV,OCT TAPPERED,IMPACT ABSORBING,10.5MSLIP JOINT, F/MOUNTED, 3M CURVED O/ARM | SFL105FIA/S30 | RIVERTON | INGAL EPS |  | 12 Months | Yes
Streetlight | 2 | Approved | 324983 | Steel Column Frangible 12m 3m outreach | GALV,OCT TAPPERED,IMPACT ABSORBING,12M HSLIP JOINT, F/MOUNTED, 3M CURVED O/ARM | SFL12FIA/S30 | RIVERTON | INGAL EPS |  | 12 Months | Yes
Streetlight | 2 | Approved | 324985 | Steel Column SeeSaw 18m for 4 Solarfloods | GALV,18M, SEE SAW MAST | HPL18F | RIVERTON | INGAL EPS |  | 12 Months | Yes
Streetlight | 2 | Approved | 231249 | PE CELL NEMA TYPE | NEMA TYPE, MAJOR ROAD LIGHTING, 30 LUX ON, 20 LUX OFF, ELECTRONIC, CAT V STREETLIGHT | Z15217 | TYCO | GERARD LIGHTING PTY LTD |  | 12 Months | No
Streetlight | 2 | Approved | 231246 | PE CELL BASE | PHOTO ELECTRIC CELL BASE, 240V, ROUND NEMA TYPE, BRACKET TO SUIT | Z15212 | SYLVANIA | GERARD LIGHTING PTY LTD |  | 12 Months | No
Streetlight | 2 | Approved | 226741 | Main Contactor | 60 A,660 V,TP,50 HZ WITH 240 V COIL,AC3, AC1,18.5kW, TO AS 1029, DIN MOUNTING. | LC1D65U7 | SCHNEID | REXEL |  | 12 months | No
Streetlight | 2 | Approved | 226112 | Change Over Switch | 1 POLE,690 V RATED INSULATION VOLTAGE,MOTOR SWITCH,FOR ISOLATIION ON STREETLIGHT CIRCUITRY | 75GN25/D51/U | CLIPSAL | REXEL |  | 12 months | No

## Assemblies
Assembly Code | Unit Assembly | Stock Item | Description | Qty
CTS/11P/185X3 | Cable Term Plug In 11kV 185 XLPE 3c | 168077 | Breakout Boot 185 & 240mm2 11 & 22kV | 1
CTS/11P/185X3 | Cable Term Plug In 11kV 185 XLPE 3c | 165280 | Elbow Kit 11/22kV 3c Set | 1
CTS/11P/185X3 | Cable Term Plug In 11kV 185 XLPE 3c | 169738 | Tubing 11kV Heavy Wall 185/240mm2 Black XLPE (per m - 30m Coil) | 15
CTS/11P/240X3 | Cable Term Plug In 11kV 240 XLPE 3c | 168077 | Breakout Boot 185 & 240mm2 11 & 22kV | 1
CTS/11P/240X3 | Cable Term Plug In 11kV 240 XLPE 3c | 165280 | Elbow Kit 11/22kV 3c Set | 1
CTS/11P/240X3 | Cable Term Plug In 11kV 240 XLPE 3c | 169738 | Tubing 11kV Heavy Wall 185/240mm2 Black XLPE (per m - 30m Coil) | 15
CTS/22P/185X3 | Cable Term Plug In 22kV 185 XLPE 3c | 168077 | Breakout Boot 185 & 240mm2 11 & 22kV | 1
CTS/22P/185X3 | Cable Term Plug In 22kV 185 XLPE 3c | 165280 | Elbow Kit 11/22kV Euromold KB400LB 3c Set | 1
CTS/22P/185X3 | Cable Term Plug In 22kV 185 XLPE 3c | 141356 | Lug Crimp Copper 25mm2 | 3
CTS/22P/185X3 | Cable Term Plug In 22kV 185 XLPE 3c | 169736 | Tubing 22kV Heavy Wall 185/240mm2 Black XLPE (per m - 22m Coil) | 11
CTS/22P/240X3 | Cable Term Plug In 22kV 240 XLPE 3c | 168077 | Breakout Boot 185 & 240mm2 11 & 22kV | 1
CTS/22P/240X3 | Cable Term Plug In 22kV 240 XLPE 3c | 165280 | Elbow Kit 11/22kV Euromold KB400LB 3c Set | 1
CTS/22P/240X3 | Cable Term Plug In 22kV 240 XLPE 3c | 141358 | Lug Crimp 35mm2 tinned copper M10 | 3
CTS/22P/240X3 | Cable Term Plug In 22kV 240 XLPE 3c | 169736 | Tubing 22kV Heavy Wall 185/240mm2 Black XLPE (per m - 22m Coil) | 11
CTS/LV/185X4 | Cable Term LV 185 XLPE 4c | 32212 | Bolt Hex M12 X 50 | 4
CTS/LV/185X4 | Cable Term LV 185 XLPE 4c | 168446 | Cable Sleeve MWTM 50/16 1200mm (Med Wall Mastic) | 1
CTS/LV/185X4 | Cable Term LV 185 XLPE 4c | 152492 | Lug Crimp Bimetal 185mm2 M12 4c solid Sector | 4
CTS/LV/185X4 | Cable Term LV 185 XLPE 4c | 40440 | Nut M12 | 4
CTS/LV/185X4 | Cable Term LV 185 XLPE 4c | 65615 | Washer Ns 12 | 8
CTS/LV/240X4 | Cable Term LV 240 XLPE 4c | 32212 | Bolt Hex M12 X 50 | 4
CTS/LV/240X4 | Cable Term LV 240 XLPE 4c | 168745 | Cable Sleeve WCSM 51/16 1200mm (Heavy Wall Mastic) | 1
CTS/LV/240X4 | Cable Term LV 240 XLPE 4c | 152483 | Lug Crimp Bimetal 240mm2 M12 | 4
CTS/LV/240X4 | Cable Term LV 240 XLPE 4c | 40440 | Nut M12 | 4
CTS/LV/240X4 | Cable Term LV 240 XLPE 4c | 65615 | Washer Ns 12 | 8
CTS/LV/300CuX1 | Cable Term LV 300 Cu XLPE 1x1c | 32212 | Bolt Hex M12 X 50 | 1
CTS/LV/300CuX1 | Cable Term LV 300 Cu XLPE 1x1c | 168745 | Cable Sleeve WCSM 51/16 1200mm (Heavy Wall Mastic) | 1
CTS/LV/300CuX1 | Cable Term LV 300 Cu XLPE 1x1c | 141379 | Lug Crimp Copper 300mm2 Blank | 1
CTS/LV/300CuX1 | Cable Term LV 300 Cu XLPE 1x1c | 40440 | Nut M12 | 1
CTS/LV/300CuX1 | Cable Term LV 300 Cu XLPE 1x1c | 65615 | Washer Ns 12 | 2
CTS/LV/300X4 | Cable Term LV 300 XLPE 4c | 32212 | Bolt Hex M12 X 50 | 4
CTS/LV/300X4 | Cable Term LV 300 XLPE 4c | 168745 | Cable Sleeve WCSM 51/16 1200mm (Heavy Wall Mastic) | 1
CTS/LV/300X4 | Cable Term LV 300 XLPE 4c | 152484 | Lug Crimp Bimetal 300mm2 M12 | 4
CTS/LV/300X4 | Cable Term LV 300 XLPE 4c | 40440 | Nut M12 | 4
CTS/LV/300X4 | Cable Term LV 300 XLPE 4c | 65615 | Washer Ns 12 | 8
CTS/LV/400AlX1 | Cable Term LV 400 Al XLPE 1x1c | 32212 | Bolt Hex M12 X 50 | 1
CTS/LV/400AlX1 | Cable Term LV 400 Al XLPE 1x1c | 168733 | Cable Sleeve WCSM 70/21 1200mm (Heavy Wall Mastic) | 1
CTS/LV/400AlX1 | Cable Term LV 400 Al XLPE 1x1c | 152485 | Lug Crimp Bimetal 400mm2 Blank | 1
CTS/LV/400AlX1 | Cable Term LV 400 Al XLPE 1x1c | 40440 | Nut M12 | 1
CTS/LV/400AlX1 | Cable Term LV 400 Al XLPE 1x1c | 65615 | Washer Ns 12 | 2
CTS/LV/400X4 | Cable Term LV 400 XLPE 4c | 32212 | Bolt Hex M12 X 50 | 4
CTS/LV/400X4 | Cable Term LV 400 XLPE 4c | 168733 | Cable Sleeve WCSM 70/21 1200mm (Heavy Wall Mastic) | 1
CTS/LV/400X4 | Cable Term LV 400 XLPE 4c | 152485 | Lug Crimp Bimetal 400mm2 Blank | 4
CTS/LV/400X4 | Cable Term LV 400 XLPE 4c | 40440 | Nut M12 | 4
CTS/LV/400X4 | Cable Term LV 400 XLPE 4c | 65615 | Washer Ns 12 | 8
CJS/11R/185X3 | Cable Joint Straight 11kV 185 XLPE | 144148 | Joint Kit 11kV S/T 3c 95 240 XLPE (Tyco MXSU-3331) cw Shear Bolts | 1
CJS/11R/240X3 | Cable Joint Straight 11kV 240 XLPE | 144148 | Joint Kit 11kV S/T 3c 95 240 XLPE (Tyco MXSU-3331) cw Shear Bolts | 1
CJS/22R/185X3 | Cable Joint Straight 22kV 185 XLPE | 144146 | Joint Kit 22kV S/T 3c 95 240 XLPE (Tyco MXSU-5331) cw Shear Bolts | 1
CJS/22R/240X3 | Cable Joint Straight 22kV 240 XLPE | 144146 | Joint Kit 22kV S/T 3c 95 240 XLPE (Tyco MXSU-5331) cw Shear Bolts | 1
CJS/LVR/185X3 | Cable Joint Straight LV 185 XLPE | 168741 | Cable Sleeve WCSM 130/36 1200mm (Heavy Wall Mastic) | 1
CJS/LVR/185X3 | Cable Joint Straight LV 185 XLPE | 168745 | Cable Sleeve WCSM 51/16 1200mm (Heavy Wall Mastic) | 2
CJS/LVR/185X3 | Cable Joint Straight LV 185 XLPE | 141165 | Splice Crimp Aluminium 185mm2 4c Solid Sector | 4
CJS/LVR/240X3 | Cable Joint Straight LV 240 XLPE | 168741 | Cable Sleeve WCSM 130/36 1200mm (Heavy Wall Mastic) | 1
CJS/LVR/240X3 | Cable Joint Straight LV 240 XLPE | 168745 | Cable Sleeve WCSM 51/16 1200mm (Heavy Wall Mastic) | 2
CJS/LVR/240X3 | Cable Joint Straight LV 240 XLPE | 141166 | Splice Crimp Aluminium 240mm2 4c Stranded Sector | 4
CJS/LVR/300X4 | Cable Joint Straight LV 300 XLPE | 168741 | Cable Sleeve WCSM 130/36 1200mm (Heavy Wall Mastic) | 1
CJS/LVR/300X4 | Cable Joint Straight LV 300 XLPE | 168733 | Cable Sleeve WCSM 70/21 1200mm (Heavy Wall Mastic) | 2
CJS/LVR/300X4 | Cable Joint Straight LV 300 XLPE | 141162 | Splice Crimp Aluminium 300mm2 Round | 4
CJS/LVR/400X4 | Cable Joint Straight LV 400 XLPE | 168741 | Cable Sleeve WCSM 130/36 1200mm (Heavy Wall Mastic) | 1
CJS/LVR/400X4 | Cable Joint Straight LV 400 XLPE | 168733 | Cable Sleeve WCSM 70/21 1200mm (Heavy Wall Mastic) | 2
CJS/LVR/400X4 | Cable Joint Straight LV 400 XLPE | 141163 | Splice Crimp Aluminium 400mm2 Round | 4
CTU/185/185/185X4 | UG Term 185/185/185 XLPE 4c | 32217 | Bolt Hex M12 X 75 | 4
CTU/185/185/185X4 | UG Term 185/185/185 XLPE 4c | 168446 | Cable Sleeve MWTM 50/16 1200mm (Med Wall Mastic) | 3
CTU/185/185/185X4 | UG Term 185/185/185 XLPE 4c | 168026 | End Cap No.5 65/95mm dia heatshrink | 4
CTU/185/185/185X4 | UG Term 185/185/185 XLPE 4c | 152474 | Lug Crimp Aluminium 185mm2 M12 4c solid Sector | 12
CTU/185/185/185X4 | UG Term 185/185/185 XLPE 4c | 40440 | Nut M12 | 4
CTU/185/185/185X4 | UG Term 185/185/185 XLPE 4c | 140177 | Spacer Plate aluminium | 8
CTU/185/185/185X4 | UG Term 185/185/185 XLPE 4c | 65615 | Washer Ns 12 | 8
CTU/185/185X4 | UG Term 185/185 XLPE 4c | 32212 | Bolt Hex M12 X 50 | 4
CTU/185/185X4 | UG Term 185/185 XLPE 4c | 168446 | Cable Sleeve MWTM 50/16 1200mm (Med Wall Mastic) | 2
CTU/185/185X4 | UG Term 185/185 XLPE 4c | 168026 | End Cap No.5 65/95mm dia heatshrink | 4
CTU/185/185X4 | UG Term 185/185 XLPE 4c | 152474 | Lug Crimp Aluminium 185mm2 M12 4c solid Sector | 8
CTU/185/185X4 | UG Term 185/185 XLPE 4c | 40440 | Nut M12 | 4
CTU/185/185X4 | UG Term 185/185 XLPE 4c | 65615 | Washer Ns 12 | 8
CTU/185/CB/185X4 | UG Term 185/CB/185 XLPE 4c | 32217 | Bolt Hex M12 X 75 | 4
CTU/185/CB/185X4 | UG Term 185/CB/185 XLPE 4c | 95120 | Cable LV Cu 1c 120mm2 c x pvc | 4
CTU/185/CB/185X4 | UG Term 185/CB/185 XLPE 4c | 168446 | Cable Sleeve MWTM 50/16 1200mm (Med Wall Mastic) | 3
CTU/185/CB/185X4 | UG Term 185/CB/185 XLPE 4c | 141371 | Lug Crimp 120mm2 tinned copper M12 | 4
CTU/185/CB/185X4 | UG Term 185/CB/185 XLPE 4c | 152474 | Lug Crimp Aluminium 185mm2 M12 4c solid Sector | 8
CTU/185/CB/185X4 | UG Term 185/CB/185 XLPE 4c | N/A | LV Circuit Breaker - place order with TasNetworks | 1
CTU/185/CB/185X4 | UG Term 185/CB/185 XLPE 4c | 141291 | Neutral Link 350A 7 Hole with cover Clipsal BP350/7 | 1
CTU/185/CB/185X4 | UG Term 185/CB/185 XLPE 4c | 40440 | Nut M12 | 4
CTU/185/CB/185X4 | UG Term 185/CB/185 XLPE 4c | 65615 | Washer Ns 12 | 8
CTU/185/S/185/185X4 | UG Term 185/S/185/185 XLPE 4c | 32212 | Bolt Hex M12 X 50 | 4
CTU/185/S/185/185X4 | UG Term 185/S/185/185 XLPE 4c | 95120 | Cable LV Cu 1c 120mm2 c x pvc | 6
CTU/185/S/185/185X4 | UG Term 185/S/185/185 XLPE 4c | 168446 | Cable Sleeve MWTM 50/16 1200mm (Med Wall Mastic) | 2
CTU/185/S/185/185X4 | UG Term 185/S/185/185 XLPE 4c | 168442 | Cable Sleeve MWTM 95/29 1200mm (Med Wall Mastic) | 1
CTU/185/S/185/185X4 | UG Term 185/S/185/185 XLPE 4c | 168021 | End Cap No.4 30/45mm dia heatshrink | 3
CTU/185/S/185/185X4 | UG Term 185/S/185/185 XLPE 4c | 168026 | End Cap No.5 65/95mm dia heatshrink | 1
CTU/185/S/185/185X4 | UG Term 185/S/185/185 XLPE 4c | 141371 | Lug Crimp 120mm2 tinned copper M12 | 6
CTU/185/S/185/185X4 | UG Term 185/S/185/185 XLPE 4c | 152474 | Lug Crimp Aluminium 185mm2 M12 4c solid Sector | 12
CTU/185/S/185/185X4 | UG Term 185/S/185/185 XLPE 4c | 40440 | Nut M12 | 4
CTU/185/S/185/185X4 | UG Term 185/S/185/185 XLPE 4c | 140177 | Spacer Plate aluminium | 2
CTU/185/S/185/185X4 | UG Term 185/S/185/185 XLPE 4c | 233671 | Switch Toggle 3-ph 440V 300A | 1
CTU/185/S/185/185X4 | UG Term 185/S/185/185 XLPE 4c | 65615 | Washer Ns 12 | 8
CTU/185/S/185X4 | UG Term 185/S/185 XLPE 4c | 32212 | Bolt Hex M12 X 50 | 4
CTU/185/S/185X4 | UG Term 185/S/185 XLPE 4c | 95120 | Cable LV Cu 1c 120mm2 c x pvc | 6
CTU/185/S/185X4 | UG Term 185/S/185 XLPE 4c | 168446 | Cable Sleeve MWTM 50/16 1200mm (Med Wall Mastic) | 2
CTU/185/S/185X4 | UG Term 185/S/185 XLPE 4c | 168021 | End Cap No.4 30/45mm dia heatshrink | 7
CTU/185/S/185X4 | UG Term 185/S/185 XLPE 4c | 141371 | Lug Crimp 120mm2 tinned copper M12 | 6
CTU/185/S/185X4 | UG Term 185/S/185 XLPE 4c | 152474 | Lug Crimp Aluminium 185mm2 M12 4c solid Sector | 8
CTU/185/S/185X4 | UG Term 185/S/185 XLPE 4c | 40440 | Nut M12 | 4
CTU/185/S/185X4 | UG Term 185/S/185 XLPE 4c | 233671 | Switch Toggle 3-ph 440V 300A | 1
CTU/185/S/185X4 | UG Term 185/S/185 XLPE 4c | 65615 | Washer Ns 12 | 8
CTU/185X4 | UG Term 185 XLPE 4c | 33771 | Bolt Tower M12 X 35 | 4
CTU/185X4 | UG Term 185 XLPE 4c | 168446 | Cable Sleeve MWTM 50/16 1200mm (Med Wall Mastic) | 1
CTU/185X4 | UG Term 185 XLPE 4c | 168021 | End Cap No.4 30/45mm dia heatshrink | 4
CTU/185X4 | UG Term 185 XLPE 4c | 152474 | Lug Crimp Aluminium 185mm2 M12 4c solid Sector | 4
CTU/185X4 | UG Term 185 XLPE 4c | 40440 | Nut M12 | 4
CTU/185X4 | UG Term 185 XLPE 4c | 65615 | Washer Ns 12 | 8
CTU/240/240/185X4 | UG Term 240/240/185 XLPE 4c | 32221 | Bolt Hex M12 X 100 | 4
CTU/240/240/185X4 | UG Term 240/240/185 XLPE 4c | 168446 | Cable Sleeve MWTM 50/16 1200mm (Med Wall Mastic) | 3
CTU/240/240/185X4 | UG Term 240/240/185 XLPE 4c | 168026 | End Cap No.5 65/95mm dia heatshrink | 4
CTU/240/240/185X4 | UG Term 240/240/185 XLPE 4c | 152474 | Lug Crimp Aluminium 185mm2 M12 4c solid Sector | 4
CTU/240/240/185X4 | UG Term 240/240/185 XLPE 4c | 152466 | Lug Crimp Aluminium 240mm2 M12 4c Sector | 8
CTU/240/240/185X4 | UG Term 240/240/185 XLPE 4c | 40440 | Nut M12 | 4
CTU/240/240/185X4 | UG Term 240/240/185 XLPE 4c | 140177 | Spacer Plate aluminium | 8
CTU/240/240/185X4 | UG Term 240/240/185 XLPE 4c | 65615 | Washer Ns 12 | 8
CTU/240/240/240X4 | UG Term 240/240/240 XLPE 4c | 32221 | Bolt Hex M12 X 100 | 4
CTU/240/240/240X4 | UG Term 240/240/240 XLPE 4c | 168446 | Cable Sleeve MWTM 50/16 1200mm (Med Wall Mastic) | 3
CTU/240/240/240X4 | UG Term 240/240/240 XLPE 4c | 168026 | End Cap No.5 65/95mm dia heatshrink | 4
CTU/240/240/240X4 | UG Term 240/240/240 XLPE 4c | 152466 | Lug Crimp Aluminium 240mm2 M12 4c Sector | 12
CTU/240/240/240X4 | UG Term 240/240/240 XLPE 4c | 40440 | Nut M12 | 4
CTU/240/240/240X4 | UG Term 240/240/240 XLPE 4c | 140177 | Spacer Plate aluminium | 8
CTU/240/240/240X4 | UG Term 240/240/240 XLPE 4c | 65615 | Washer Ns 12 | 8
CTU/240/240X4 | UG Term 240/240 XLPE 4c | 32212 | Bolt Hex M12 X 50 | 4
CTU/240/240X4 | UG Term 240/240 XLPE 4c | 168446 | Cable Sleeve MWTM 50/16 1200mm (Med Wall Mastic) | 2
CTU/240/240X4 | UG Term 240/240 XLPE 4c | 168026 | End Cap No.5 65/95mm dia heatshrink | 4
CTU/240/240X4 | UG Term 240/240 XLPE 4c | 152466 | Lug Crimp Aluminium 240mm2 M12 4c Sector | 8
CTU/240/240X4 | UG Term 240/240 XLPE 4c | 40440 | Nut M12 | 4
CTU/240/240X4 | UG Term 240/240 XLPE 4c | 65615 | Washer Ns 12 | 8
CTU/240/CB/240X4 | UG Term 240/CB/240 XLPE 4c | 32217 | Bolt Hex M12 X 75 | 4
CTU/240/CB/240X4 | UG Term 240/CB/240 XLPE 4c | 94195 | Cable LV Cu 1c 150mm2 c x pvc | 4
CTU/240/CB/240X4 | UG Term 240/CB/240 XLPE 4c | 168446 | Cable Sleeve MWTM 50/16 1200mm (Med Wall Mastic) | 3
CTU/240/CB/240X4 | UG Term 240/CB/240 XLPE 4c | 152466 | Lug Crimp Aluminium 240mm2 M12 4c Sector | 8
CTU/240/CB/240X4 | UG Term 240/CB/240 XLPE 4c | 141372 | Lug Crimp Copper 150mm2 | 5
CTU/240/CB/240X4 | UG Term 240/CB/240 XLPE 4c | N/A | LV Circuit Breaker - place order with TasNetworks | 1
CTU/240/CB/240X4 | UG Term 240/CB/240 XLPE 4c | 141296 | Neutral Link Brass Alloy (19 x 19mm) with 50x6 Cu Busbar & 2xM12 Brass Studs & Backing Plate | 1
CTU/240/CB/240X4 | UG Term 240/CB/240 XLPE 4c | 40440 | Nut M12 | 6
CTU/240/CB/240X4 | UG Term 240/CB/240 XLPE 4c | 65615 | Washer Ns 12 | 10
CTU/240/S/240/185X4 | UG Term 240/S/240/185 XLPE 4c | 32217 | Bolt Hex M12 X 75 | 4
CTU/240/S/240/185X4 | UG Term 240/S/240/185 XLPE 4c | 94195 | Cable LV Cu 1c 150mm2 c x pvc | 6
CTU/240/S/240/185X4 | UG Term 240/S/240/185 XLPE 4c | 168446 | Cable Sleeve MWTM 50/16 1200mm (Med Wall Mastic) | 3
CTU/240/S/240/185X4 | UG Term 240/S/240/185 XLPE 4c | 168442 | Cable Sleeve MWTM 95/29 1200mm (Med Wall Mastic) | 1
CTU/240/S/240/185X4 | UG Term 240/S/240/185 XLPE 4c | 168021 | End Cap No.4 30/45mm dia heatshrink | 3
CTU/240/S/240/185X4 | UG Term 240/S/240/185 XLPE 4c | 168026 | End Cap No.5 65/95mm dia heatshrink | 1
CTU/240/S/240/185X4 | UG Term 240/S/240/185 XLPE 4c | 152474 | Lug Crimp Aluminium 185mm2 M12 4c solid Sector | 4
CTU/240/S/240/185X4 | UG Term 240/S/240/185 XLPE 4c | 152466 | Lug Crimp Aluminium 240mm2 M12 4c Sector | 5
CTU/240/S/240/185X4 | UG Term 240/S/240/185 XLPE 4c | 141372 | Lug Crimp Copper 150mm2 | 3
CTU/240/S/240/185X4 | UG Term 240/S/240/185 XLPE 4c | 40440 | Nut M12 | 4
CTU/240/S/240/185X4 | UG Term 240/S/240/185 XLPE 4c | 140177 | Spacer Plate aluminium | 2
CTU/240/S/240/185X4 | UG Term 240/S/240/185 XLPE 4c | 141197 | Splice Crimp Bimetal 240al/150cu 4c solid Sector/Round | 3
CTU/240/S/240/185X4 | UG Term 240/S/240/185 XLPE 4c | 233671 | Switch Toggle 3-ph 440V 300A | 1
CTU/240/S/240/185X4 | UG Term 240/S/240/185 XLPE 4c | 65615 | Washer Ns 12 | 8
CTU/240/S/240/240X4 | UG Term 240/S/240/240 XLPE 4c | 32217 | Bolt Hex M12 X 75 | 4
CTU/240/S/240/240X4 | UG Term 240/S/240/240 XLPE 4c | 94195 | Cable LV Cu 1c 150mm2 c x pvc | 6
CTU/240/S/240/240X4 | UG Term 240/S/240/240 XLPE 4c | 168446 | Cable Sleeve MWTM 50/16 1200mm (Med Wall Mastic) | 2
CTU/240/S/240/240X4 | UG Term 240/S/240/240 XLPE 4c | 168442 | Cable Sleeve MWTM 95/29 1200mm (Med Wall Mastic) | 1
CTU/240/S/240/240X4 | UG Term 240/S/240/240 XLPE 4c | 168021 | End Cap No.4 30/45mm dia heatshrink | 3
CTU/240/S/240/240X4 | UG Term 240/S/240/240 XLPE 4c | 168026 | End Cap No.5 65/95mm dia heatshrink | 1
CTU/240/S/240/240X4 | UG Term 240/S/240/240 XLPE 4c | 152466 | Lug Crimp Aluminium 240mm2 M12 4c Sector | 9
CTU/240/S/240/240X4 | UG Term 240/S/240/240 XLPE 4c | 141372 | Lug Crimp Copper 150mm2 | 3
CTU/240/S/240/240X4 | UG Term 240/S/240/240 XLPE 4c | 40440 | Nut M12 | 4
CTU/240/S/240/240X4 | UG Term 240/S/240/240 XLPE 4c | 140177 | Spacer Plate aluminium | 2
CTU/240/S/240/240X4 | UG Term 240/S/240/240 XLPE 4c | 141197 | Splice Crimp Bimetal 240al/150cu 4c solid Sector/Round | 3
CTU/240/S/240/240X4 | UG Term 240/S/240/240 XLPE 4c | 233671 | Switch Toggle 3-ph 440V 300A | 1
CTU/240/S/240/240X4 | UG Term 240/S/240/240 XLPE 4c | 65615 | Washer Ns 12 | 8
CTU/240/S/240X4 | UG Term 240/S/240 XLPE 4c | 32212 | Bolt Hex M12 X 50 | 4
CTU/240/S/240X4 | UG Term 240/S/240 XLPE 4c | 94195 | Cable LV Cu 1c 150mm2 c x pvc | 6
CTU/240/S/240X4 | UG Term 240/S/240 XLPE 4c | 168446 | Cable Sleeve MWTM 50/16 1200mm (Med Wall Mastic) | 2
CTU/240/S/240X4 | UG Term 240/S/240 XLPE 4c | 168021 | End Cap No.4 30/45mm dia heatshrink | 7
CTU/240/S/240X4 | UG Term 240/S/240 XLPE 4c | 152466 | Lug Crimp Aluminium 240mm2 M12 4c Sector | 5
CTU/240/S/240X4 | UG Term 240/S/240 XLPE 4c | 141372 | Lug Crimp Copper 150mm2 | 3
CTU/240/S/240X4 | UG Term 240/S/240 XLPE 4c | 40440 | Nut M12 | 4
CTU/240/S/240X4 | UG Term 240/S/240 XLPE 4c | 141197 | Splice Crimp Bimetal 240al/150cu 4c solid Sector/Round | 3
CTU/240/S/240X4 | UG Term 240/S/240 XLPE 4c | 233671 | Switch Toggle 3-ph 440V 300A | 1
CTU/240/S/240X4 | UG Term 240/S/240 XLPE 4c | 65615 | Washer Ns 12 | 8
CTU/240X4 | UG Term 240 XLPE 4c | 33771 | Bolt Tower M12 X 35 | 4
CTU/240X4 | UG Term 240 XLPE 4c | 168446 | Cable Sleeve MWTM 50/16 1200mm (Med Wall Mastic) | 1
CTU/240X4 | UG Term 240 XLPE 4c | 168021 | End Cap No.4 30/45mm dia heatshrink | 4
CTU/240X4 | UG Term 240 XLPE 4c | 152466 | Lug Crimp Aluminium 240mm2 M12 4c Sector | 4
CTU/240X4 | UG Term 240 XLPE 4c | 40440 | Nut M12 | 4
CTU/240X4 | UG Term 240 XLPE 4c | 65615 | Washer Ns 12 | 8
CTU/300/300/185X4 | UG Term 300/300/185 XLPE 4c | 32221 | Bolt Hex M12 X 100 | 4
CTU/300/300/185X4 | UG Term 300/300/185 XLPE 4c | 168446 | Cable Sleeve MWTM 50/16 1200mm (Med Wall Mastic) | 3
CTU/300/300/185X4 | UG Term 300/300/185 XLPE 4c | 168026 | End Cap No.5 65/95mm dia heatshrink | 4
CTU/300/300/185X4 | UG Term 300/300/185 XLPE 4c | 152475 | Lug Crimp Al 300mm2 M12 | 8
CTU/300/300/185X4 | UG Term 300/300/185 XLPE 4c | 152474 | Lug Crimp Aluminium 185mm2 M12 4c solid Sector | 4
CTU/300/300/185X4 | UG Term 300/300/185 XLPE 4c | 40440 | Nut M12 | 4
CTU/300/300/185X4 | UG Term 300/300/185 XLPE 4c | 140177 | Spacer Plate aluminium | 8
CTU/300/300/185X4 | UG Term 300/300/185 XLPE 4c | 65615 | Washer Ns 12 | 8
CTU/300/300/300X4 | UG Term 300/300/300 XLPE 4c | 32221 | Bolt Hex M12 X 100 | 4
CTU/300/300/300X4 | UG Term 300/300/300 XLPE 4c | 168446 | Cable Sleeve MWTM 50/16 1200mm (Med Wall Mastic) | 3
CTU/300/300/300X4 | UG Term 300/300/300 XLPE 4c | 168028 | End Cap No.6 95/115mm dia heatshrink | 4
CTU/300/300/300X4 | UG Term 300/300/300 XLPE 4c | 152475 | Lug Crimp Al 300mm2 M12 | 12
CTU/300/300/300X4 | UG Term 300/300/300 XLPE 4c | 40440 | Nut M12 | 4
CTU/300/300/300X4 | UG Term 300/300/300 XLPE 4c | 140177 | Spacer Plate aluminium | 8
CTU/300/300/300X4 | UG Term 300/300/300 XLPE 4c | 65615 | Washer Ns 12 | 8
CTU/300/300X4 | UG Term 300/300 XLPE 4c | 32212 | Bolt Hex M12 X 50 | 4
CTU/300/300X4 | UG Term 300/300 XLPE 4c | 168446 | Cable Sleeve MWTM 50/16 1200mm (Med Wall Mastic) | 2
CTU/300/300X4 | UG Term 300/300 XLPE 4c | 168026 | End Cap No.5 65/95mm dia heatshrink | 4
CTU/300/300X4 | UG Term 300/300 XLPE 4c | 152475 | Lug Crimp Al 300mm2 M12 | 8
CTU/300/300X4 | UG Term 300/300 XLPE 4c | 40440 | Nut M12 | 4
CTU/300/300X4 | UG Term 300/300 XLPE 4c | 65615 | Washer Ns 12 | 8
CTU/300/CB/300X4 | UG Term 300/CB/300 XLPE 4c | 32217 | Bolt Hex M12 X 75 | 4
CTU/300/CB/300X4 | UG Term 300/CB/300 XLPE 4c | 95185 | Cable LV Cu 1c 185mm2 c x pvc | 4
CTU/300/CB/300X4 | UG Term 300/CB/300 XLPE 4c | 168442 | Cable Sleeve MWTM 95/29 1200mm (Med Wall Mastic) | 1
CTU/300/CB/300X4 | UG Term 300/CB/300 XLPE 4c | 168446 | Cable Sleeve MWTM 50/16 1200mm (Med Wall Mastic) | 2
CTU/300/CB/300X4 | UG Term 300/CB/300 XLPE 4c | 152475 | Lug Crimp Al 300mm2 M12 | 8
CTU/300/CB/300X4 | UG Term 300/CB/300 XLPE 4c | 141376 | Lug Crimp Copper 185mm2 M12 | 5
CTU/300/CB/300X4 | UG Term 300/CB/300 XLPE 4c | N/A | LV Circuit Breaker - place order with TasNetworks | 1
CTU/300/CB/300X4 | UG Term 300/CB/300 XLPE 4c | 141296 | Neutral Link Brass Alloy (19 x 19mm) with 50x6 Cu Busbar & 2xM12 Brass Studs & Backing Plate | 1
CTU/300/CB/300X4 | UG Term 300/CB/300 XLPE 4c | 40440 | Nut M12 | 6
CTU/300/CB/300X4 | UG Term 300/CB/300 XLPE 4c | 65615 | Washer Ns 12 | 10
CTU/300/S/300/185X4 | UG Term 300/S/300/185 XLPE 4c | 32217 | Bolt Hex M12 X 75 | 4
CTU/300/S/300/185X4 | UG Term 300/S/300/185 XLPE 4c | 95185 | Cable LV Cu 1c 185mm2 c x pvc | 6
CTU/300/S/300/185X4 | UG Term 300/S/300/185 XLPE 4c | 168446 | Cable Sleeve MWTM 50/16 1200mm (Med Wall Mastic) | 3
CTU/300/S/300/185X4 | UG Term 300/S/300/185 XLPE 4c | 168442 | Cable Sleeve MWTM 95/29 1200mm (Med Wall Mastic) | 1
CTU/300/S/300/185X4 | UG Term 300/S/300/185 XLPE 4c | 168021 | End Cap No.4 30/45mm dia heatshrink | 3
CTU/300/S/300/185X4 | UG Term 300/S/300/185 XLPE 4c | 168026 | End Cap No.5 65/95mm dia heatshrink | 1
CTU/300/S/300/185X4 | UG Term 300/S/300/185 XLPE 4c | 152475 | Lug Crimp Al 300mm2 M12 | 5
CTU/300/S/300/185X4 | UG Term 300/S/300/185 XLPE 4c | 152474 | Lug Crimp Aluminium 185mm2 M12 4c solid Sector | 4
CTU/300/S/300/185X4 | UG Term 300/S/300/185 XLPE 4c | 141376 | Lug Crimp Copper 185mm2 M12 | 3
CTU/300/S/300/185X4 | UG Term 300/S/300/185 XLPE 4c | 40440 | Nut M12 | 4
CTU/300/S/300/185X4 | UG Term 300/S/300/185 XLPE 4c | 140177 | Spacer Plate aluminium | 2
CTU/300/S/300/185X4 | UG Term 300/S/300/185 XLPE 4c | 141192 | Splice Crimp Bimetal 300al/185cu Round/Round | 3
CTU/300/S/300/185X4 | UG Term 300/S/300/185 XLPE 4c | 233671 | Switch Toggle 3-ph 440V 300A | 1
CTU/300/S/300/185X4 | UG Term 300/S/300/185 XLPE 4c | 65615 | Washer Ns 12 | 8
CTU/300/S/300/300X4 | UG Term 300/S/300/300 XLPE 4c | 32217 | Bolt Hex M12 X 75 | 4
CTU/300/S/300/300X4 | UG Term 300/S/300/300 XLPE 4c | 95185 | Cable LV Cu 1c 185mm2 c x pvc | 6
CTU/300/S/300/300X4 | UG Term 300/S/300/300 XLPE 4c | 168442 | Cable Sleeve MWTM 95/29 1200mm (Med Wall Mastic) | 1
CTU/300/S/300/300X4 | UG Term 300/S/300/300 XLPE 4c | 168446 | Cable Sleeve MWTM 50/16 1200mm (Med Wall Mastic) | 3
CTU/300/S/300/300X4 | UG Term 300/S/300/300 XLPE 4c | 168021 | End Cap No.4 30/45mm dia heatshrink | 3
CTU/300/S/300/300X4 | UG Term 300/S/300/300 XLPE 4c | 168028 | End Cap No.6 95/115mm dia heatshrink | 1
CTU/300/S/300/300X4 | UG Term 300/S/300/300 XLPE 4c | 152475 | Lug Crimp Al 300mm2 M12 | 9
CTU/300/S/300/300X4 | UG Term 300/S/300/300 XLPE 4c | 141376 | Lug Crimp Copper 185mm2 M12 | 3
CTU/300/S/300/300X4 | UG Term 300/S/300/300 XLPE 4c | 40440 | Nut M12 | 4
CTU/300/S/300/300X4 | UG Term 300/S/300/300 XLPE 4c | 140177 | Spacer Plate aluminium | 2
CTU/300/S/300/300X4 | UG Term 300/S/300/300 XLPE 4c | 141192 | Splice Crimp Bimetal 300al/185cu Round/Round | 3
CTU/300/S/300/300X4 | UG Term 300/S/300/300 XLPE 4c | 233671 | Switch Toggle 3-ph 440V 300A | 1
CTU/300/S/300/300X4 | UG Term 300/S/300/300 XLPE 4c | 65615 | Washer Ns 12 | 8
CTU/300/S/300X4 | UG Term 300/S/300 XLPE 4c | 32212 | Bolt Hex M12 X 50 | 4
CTU/300/S/300X4 | UG Term 300/S/300 XLPE 4c | 95185 | Cable LV Cu 1c 185mm2 c x pvc | 6
CTU/300/S/300X4 | UG Term 300/S/300 XLPE 4c | 168446 | Cable Sleeve MWTM 50/16 1200mm (Med Wall Mastic) | 2
CTU/300/S/300X4 | UG Term 300/S/300 XLPE 4c | 168021 | End Cap No.4 30/45mm dia heatshrink | 8
CTU/300/S/300X4 | UG Term 300/S/300 XLPE 4c | 152475 | Lug Crimp Al 300mm2 M12 | 5
CTU/300/S/300X4 | UG Term 300/S/300 XLPE 4c | 141376 | Lug Crimp Copper 185mm2 M12 | 3
CTU/300/S/300X4 | UG Term 300/S/300 XLPE 4c | 40440 | Nut M12 | 4
CTU/300/S/300X4 | UG Term 300/S/300 XLPE 4c | 141192 | Splice Crimp Bimetal 300al/185cu Round/Round | 3
CTU/300/S/300X4 | UG Term 300/S/300 XLPE 4c | 233671 | Switch Toggle 3-ph 440V 300A | 1
CTU/300/S/300X4 | UG Term 300/S/300 XLPE 4c | 65615 | Washer Ns 12 | 8
CTU/300X4 | UG Term 300 XLPE 4c | 33771 | Bolt Tower M12 X 35 | 4
CTU/300X4 | UG Term 300 XLPE 4c | 168446 | Cable Sleeve MWTM 50/16 1200mm (Med Wall Mastic) | 1
CTU/300X4 | UG Term 300 XLPE 4c | 168021 | End Cap No.4 30/45mm dia heatshrink | 4
CTU/300X4 | UG Term 300 XLPE 4c | 152475 | Lug Crimp Al 300mm2 M12 | 4
CTU/300X4 | UG Term 300 XLPE 4c | 40440 | Nut M12 | 4
CTU/300X4 | UG Term 300 XLPE 4c | 65615 | Washer Ns 12 | 8
CTU/400/400/185X4 | UG Term 400/400/185 XLPE 4c | 32221 | Bolt Hex M12 X 100 | 4
CTU/400/400/185X4 | UG Term 400/400/185 XLPE 4c | 168446 | Cable Sleeve MWTM 50/16 1200mm (Med Wall Mastic) | 3
CTU/400/400/185X4 | UG Term 400/400/185 XLPE 4c | 168028 | End Cap No.6 95/115mm dia heatshrink | 4
CTU/400/400/185X4 | UG Term 400/400/185 XLPE 4c | 152474 | Lug Crimp Aluminium 185mm2 M12 4c solid Sector | 4
CTU/400/400/185X4 | UG Term 400/400/185 XLPE 4c | 152470 | Lug Crimp Aluminium 400mm2 M12 Round | 8
CTU/400/400/185X4 | UG Term 400/400/185 XLPE 4c | 40440 | Nut M12 | 4
CTU/400/400/185X4 | UG Term 400/400/185 XLPE 4c | 140177 | Spacer Plate aluminium | 8
CTU/400/400/185X4 | UG Term 400/400/185 XLPE 4c | 65615 | Washer Ns 12 | 8
CTU/400/400/400X4 | UG Term 400/400/400 XLPE 4c | 32221 | Bolt Hex M12 X 100 | 4
CTU/400/400/400X4 | UG Term 400/400/400 XLPE 4c | 168446 | Cable Sleeve MWTM 50/16 1200mm (Med Wall Mastic) | 3
CTU/400/400/400X4 | UG Term 400/400/400 XLPE 4c | 168028 | End Cap No.6 95/115mm dia heatshrink | 4
CTU/400/400/400X4 | UG Term 400/400/400 XLPE 4c | 152470 | Lug Crimp Aluminium 400mm2 M12 Round | 12
CTU/400/400/400X4 | UG Term 400/400/400 XLPE 4c | 40440 | Nut M12 | 4
CTU/400/400/400X4 | UG Term 400/400/400 XLPE 4c | 140177 | Spacer Plate aluminium | 8
CTU/400/400/400X4 | UG Term 400/400/400 XLPE 4c | 65615 | Washer Ns 12 | 8
CTU/400/400X4 | UG Term 400/400 XLPE 4c | 32212 | Bolt Hex M12 X 50 | 4
CTU/400/400X4 | UG Term 400/400 XLPE 4c | 168446 | Cable Sleeve MWTM 50/16 1200mm (Med Wall Mastic) | 2
CTU/400/400X4 | UG Term 400/400 XLPE 4c | 168026 | End Cap No.5 65/95mm dia heatshrink | 4
CTU/400/400X4 | UG Term 400/400 XLPE 4c | 152470 | Lug Crimp Aluminium 400mm2 M12 Round | 8
CTU/400/400X4 | UG Term 400/400 XLPE 4c | 40440 | Nut M12 | 4
CTU/400/400X4 | UG Term 400/400 XLPE 4c | 65615 | Washer Ns 12 | 8
CTU/400/CB/400X4 | UG Term 400/CB/400 XLPE 4c | 32217 | Bolt Hex M12 X 75 | 4
CTU/400/CB/400X4 | UG Term 400/CB/400 XLPE 4c | 95240 | Cable LV Cu 1c 240mm2 c x pvc | 4
CTU/400/CB/400X4 | UG Term 400/CB/400 XLPE 4c | 168446 | Cable Sleeve MWTM 50/16 1200mm (Med Wall Mastic) | 2
CTU/400/CB/400X4 | UG Term 400/CB/400 XLPE 4c | 168442 | Cable Sleeve MWTM 95/29 1200mm (Med Wall Mastic) | 1
CTU/400/CB/400X4 | UG Term 400/CB/400 XLPE 4c | 152470 | Lug Crimp Aluminium 400mm2 M12 Round | 8
CTU/400/CB/400X4 | UG Term 400/CB/400 XLPE 4c | 141296 | Neutral Link Brass Alloy (19 x 19mm) with 50x6 Cu Busbar & 2xM12 Brass Studs & Backing Plate | 1
CTU/400/CB/400X4 | UG Term 400/CB/400 XLPE 4c | 141377 | Lug Crimp Copper 240mm2 Blank | 5
CTU/400/CB/400X4 | UG Term 400/CB/400 XLPE 4c | N/A | LV Circuit Breaker - place order with TasNetworks | 1
CTU/400/CB/400X4 | UG Term 400/CB/400 XLPE 4c | 40440 | Nut M12 | 6
CTU/400/CB/400X4 | UG Term 400/CB/400 XLPE 4c | 65615 | Washer Ns 12 | 10
CTU/400/S/400/185X4 | UG Term 400/S/400/185 XLPE 4c | 32212 | Bolt Hex M12 X 50 | 4
CTU/400/S/400/185X4 | UG Term 400/S/400/185 XLPE 4c | 32217 | Bolt Hex M12 X 75 | 4
CTU/400/S/400/185X4 | UG Term 400/S/400/185 XLPE 4c | 95240 | Cable LV Cu 1c 240mm2 c x pvc | 6
CTU/400/S/400/185X4 | UG Term 400/S/400/185 XLPE 4c | 168446 | Cable Sleeve MWTM 50/16 1200mm (Med Wall Mastic) | 3
CTU/400/S/400/185X4 | UG Term 400/S/400/185 XLPE 4c | 168021 | End Cap No.4 30/45mm dia heatshrink | 3
CTU/400/S/400/185X4 | UG Term 400/S/400/185 XLPE 4c | 168028 | End Cap No.6 95/115mm dia heatshrink | 1
CTU/400/S/400/185X4 | UG Term 400/S/400/185 XLPE 4c | 168442 | Cable Sleeve MWTM 95/29 1200mm (Med Wall Mastic) | 1
CTU/400/S/400/185X4 | UG Term 400/S/400/185 XLPE 4c | 152474 | Lug Crimp Aluminium 185mm2 M12 4c solid Sector | 4
CTU/400/S/400/185X4 | UG Term 400/S/400/185 XLPE 4c | 152470 | Lug Crimp Aluminium 400mm2 M12 Round | 8
CTU/400/S/400/185X4 | UG Term 400/S/400/185 XLPE 4c | 141377 | Lug Crimp Copper 240mm2 Blank | 6
CTU/400/S/400/185X4 | UG Term 400/S/400/185 XLPE 4c | 40440 | Nut M12 | 8
CTU/400/S/400/185X4 | UG Term 400/S/400/185 XLPE 4c | 140177 | Spacer Plate aluminium | 2
CTU/400/S/400/185X4 | UG Term 400/S/400/185 XLPE 4c | 233671 | Switch Toggle 3-ph 440V 300A | 1
CTU/400/S/400/185X4 | UG Term 400/S/400/185 XLPE 4c | 65615 | Washer Ns 12 | 16
CTU/400/S/400/400X4 | UG Term 400/S/400/400 XLPE 4c | 32212 | Bolt Hex M12 X 50 | 3
CTU/400/S/400/400X4 | UG Term 400/S/400/400 XLPE 4c | 32217 | Bolt Hex M12 X 75 | 4
CTU/400/S/400/400X4 | UG Term 400/S/400/400 XLPE 4c | 95240 | Cable LV Cu 1c 240mm2 c x pvc | 7
CTU/400/S/400/400X4 | UG Term 400/S/400/400 XLPE 4c | 168446 | Cable Sleeve MWTM 50/16 1200mm (Med Wall Mastic) | 3
CTU/400/S/400/400X4 | UG Term 400/S/400/400 XLPE 4c | 168442 | Cable Sleeve MWTM 95/29 1200mm (Med Wall Mastic) | 1
CTU/400/S/400/400X4 | UG Term 400/S/400/400 XLPE 4c | 168021 | End Cap No.4 30/45mm dia heatshrink | 3
CTU/400/S/400/400X4 | UG Term 400/S/400/400 XLPE 4c | 168028 | End Cap No.6 95/115mm dia heatshrink | 1
CTU/400/S/400/400X4 | UG Term 400/S/400/400 XLPE 4c | 152470 | Lug Crimp Aluminium 400mm2 M12 Round | 12
CTU/400/S/400/400X4 | UG Term 400/S/400/400 XLPE 4c | 141377 | Lug Crimp Copper 240mm2 Blank | 8
CTU/400/S/400/400X4 | UG Term 400/S/400/400 XLPE 4c | 40440 | Nut M12 | 8
CTU/400/S/400/400X4 | UG Term 400/S/400/400 XLPE 4c | 140177 | Spacer Plate aluminium | 2
CTU/400/S/400/400X4 | UG Term 400/S/400/400 XLPE 4c | 233671 | Switch Toggle 3-ph 440V 300A | 1
CTU/400/S/400/400X4 | UG Term 400/S/400/400 XLPE 4c | 65615 | Washer Ns 12 | 16
CTU/400/S/400X4 | UG Term 400/S/400 XLPE 4c | 32212 | Bolt Hex M12 X 50 | 8
CTU/400/S/400X4 | UG Term 400/S/400 XLPE 4c | 95240 | Cable LV Cu 1c 240mm2 c x pvc | 6
CTU/400/S/400X4 | UG Term 400/S/400 XLPE 4c | 168446 | Cable Sleeve MWTM 50/16 1200mm (Med Wall Mastic) | 2
CTU/400/S/400X4 | UG Term 400/S/400 XLPE 4c | 168021 | End Cap No.4 30/45mm dia heatshrink | 6
CTU/400/S/400X4 | UG Term 400/S/400 XLPE 4c | 168028 | End Cap No.6 95/115mm dia heatshrink | 1
CTU/400/S/400X4 | UG Term 400/S/400 XLPE 4c | 152470 | Lug Crimp Aluminium 400mm2 M12 Round | 8
CTU/400/S/400X4 | UG Term 400/S/400 XLPE 4c | 141377 | Lug Crimp Copper 240mm2 Blank | 6
CTU/400/S/400X4 | UG Term 400/S/400 XLPE 4c | 40440 | Nut M12 | 8
CTU/400/S/400X4 | UG Term 400/S/400 XLPE 4c | 233671 | Switch Toggle 3-ph 440V 300A | 1
CTU/400/S/400X4 | UG Term 400/S/400 XLPE 4c | 65615 | Washer Ns 12 | 16
CTU/400/S/400/CBX4 | UG Term 400/S/400/CB XLPE 4c | 32212 | Bolt Hex M12 X 50 | 7
CTU/400/S/400/CBX4 | UG Term 400/S/400/CB XLPE 4c | 95240 | Cable LV Cu 1c 240mm2 c x pvc | 10
CTU/400/S/400/CBX4 | UG Term 400/S/400/CB XLPE 4c | 168446 | Cable Sleeve MWTM 50/16 1200mm (Med Wall Mastic) | 4
CTU/400/S/400/CBX4 | UG Term 400/S/400/CB XLPE 4c | 168021 | End Cap No.4 30/45mm dia heatshrink | 3
CTU/400/S/400/CBX4 | UG Term 400/S/400/CB XLPE 4c | 152470 | Lug Crimp Aluminium 400mm2 M12 Round | 8
CTU/400/S/400/CBX4 | UG Term 400/S/400/CB XLPE 4c | 141377 | Lug Crimp Copper 240mm2 Blank | 11
CTU/400/S/400/CBX4 | UG Term 400/S/400/CB XLPE 4c | 40440 | Nut M12 | 9
CTU/400/S/400/CBX4 | UG Term 400/S/400/CB XLPE 4c | 233671 | Switch Toggle 3-ph 440V 300A | 1
CTU/400/S/400/CBX4 | UG Term 400/S/400/CB XLPE 4c | 65615 | Washer Ns 12 | 14
CTU/400/S/400/CBX4 | UG Term 400/S/400/CB XLPE 4c | 141296 | Neutral Link Brass Alloy (19 x 19mm) with 50x6 Cu Busbar & 2xM12 Brass Studs & Backing Plate | 1
CTU/400/S/400/CBX4 | UG Term 400/S/400/CB XLPE 4c | N/A | LV Circuit Breaker - place order with TasNetworks | 1
CTU/300/S/300/CBX4 | UG Term 300/S/300/CB XLPE 4c | 32212 | Bolt Hex M12 X 50 | 7
CTU/300/S/300/CBX4 | UG Term 300/S/300/CB XLPE 4c | 95185 | Cable LV Cu 1c 185mm2 c x pvc | 10
CTU/300/S/300/CBX4 | UG Term 300/S/300/CB XLPE 4c | 168446 | Cable Sleeve MWTM 50/16 1200mm (Med Wall Mastic) | 4
CTU/300/S/300/CBX4 | UG Term 300/S/300/CB XLPE 4c | 168021 | End Cap No.4 30/45mm dia heatshrink | 3
CTU/300/S/300/CBX4 | UG Term 300/S/300/CB XLPE 4c | 152475 | Lug Crimp Al 300mm2 M12 | 8
CTU/300/S/300/CBX4 | UG Term 300/S/300/CB XLPE 4c | 141376 | Lug Crimp Copper 185mm2 M12 | 11
CTU/300/S/300/CBX4 | UG Term 300/S/300/CB XLPE 4c | 40440 | Nut M12 | 9
CTU/300/S/300/CBX4 | UG Term 300/S/300/CB XLPE 4c | 233671 | Switch Toggle 3-ph 440V 300A | 1
CTU/300/S/300/CBX4 | UG Term 300/S/300/CB XLPE 4c | 65615 | Washer Ns 12 | 14
CTU/300/S/300/CBX4 | UG Term 300/S/300/CB XLPE 4c | 141296 | Neutral Link Brass Alloy (19 x 19mm) with 50x6 Cu Busbar & 2xM12 Brass Studs & Backing Plate | 1
CTU/300/S/300/CBX4 | UG Term 300/S/300/CB XLPE 4c | N/A | LV Circuit Breaker - place order with TasNetworks | 1
CTU/400X4 | UG Term 400 XLPE 4c | 33771 | Bolt Tower M12 X 35 | 4
CTU/400X4 | UG Term 400 XLPE 4c | 168446 | Cable Sleeve MWTM 50/16 1200mm (Med Wall Mastic) | 1
CTU/400X4 | UG Term 400 XLPE 4c | 168021 | End Cap No.4 30/45mm dia heatshrink | 4
CTU/400X4 | UG Term 400 XLPE 4c | 152470 | Lug Crimp Aluminium 400mm2 M12 Round | 4
CTU/400X4 | UG Term 400 XLPE 4c | 40440 | Nut M12 | 4
CTU/400X4 | UG Term 400 XLPE 4c | 65615 | Washer Ns 12 | 8
CTU/CB/185X4 | UG Term 185 XLPE 4c with LVCB | 32212 | Bolt Hex M12 X 50 | 4
CTU/CB/185X4 | UG Term 185 XLPE 4c with LVCB | 95120 | Cable LV Cu 1c 120mm2 c x pvc | 4
CTU/CB/185X4 | UG Term 185 XLPE 4c with LVCB | 168446 | Cable Sleeve MWTM 50/16 1200mm (Med Wall Mastic) | 3
CTU/CB/185X4 | UG Term 185 XLPE 4c with LVCB | 141371 | Lug Crimp 120mm2 tinned copper M12 | 4
CTU/CB/185X4 | UG Term 185 XLPE 4c with LVCB | 152474 | Lug Crimp Aluminium 185mm2 M12 4c solid Sector | 4
CTU/CB/185X4 | UG Term 185 XLPE 4c with LVCB | N/A | LV Circuit Breaker - place order with TasNetworks | 1
CTU/CB/185X4 | UG Term 185 XLPE 4c with LVCB | 141291 | Neutral Link 350A 7 Hole with cover Clipsal BP350/7 | 1
CTU/CB/185X4 | UG Term 185 XLPE 4c with LVCB | 40440 | Nut M12 | 4
CTU/CB/185X4 | UG Term 185 XLPE 4c with LVCB | 65615 | Washer Ns 12 | 8
CTU/CB/240X4 | UG Term 240 XLPE 4c with LVCB | 32212 | Bolt Hex M12 X 50 | 4
CTU/CB/240X4 | UG Term 240 XLPE 4c with LVCB | 94195 | Cable LV Cu 1c 150mm2 c x pvc | 4
CTU/CB/240X4 | UG Term 240 XLPE 4c with LVCB | 168446 | Cable Sleeve MWTM 50/16 1200mm (Med Wall Mastic) | 3
CTU/CB/240X4 | UG Term 240 XLPE 4c with LVCB | 152466 | Lug Crimp Aluminium 240mm2 M12 4c Sector | 4
CTU/CB/240X4 | UG Term 240 XLPE 4c with LVCB | 141373 | Lug Crimp Copper 150mm2 M16 | 5
CTU/CB/240X4 | UG Term 240 XLPE 4c with LVCB | N/A | LV Circuit Breaker - place order with TasNetworks | 1
CTU/CB/240X4 | UG Term 240 XLPE 4c with LVCB | 141296 | Neutral Link Brass Alloy (19 x 19mm) with 50x6 Cu Busbar & 2xM12 Brass Studs & Backing Plate | 1
CTU/CB/240X4 | UG Term 240 XLPE 4c with LVCB | 40440 | Nut M12 | 6
CTU/CB/240X4 | UG Term 240 XLPE 4c with LVCB | 65615 | Washer Ns 12 | 10
CTU/CB/300X4 | UG Term 300 XLPE 4c with LVCB | 32212 | Bolt Hex M12 X 50 | 4
CTU/CB/300X4 | UG Term 300 XLPE 4c with LVCB | 95185 | Cable LV Cu 1c 185mm2 c x pvc | 4
CTU/CB/300X4 | UG Term 300 XLPE 4c with LVCB | 168446 | Cable Sleeve MWTM 50/16 1200mm (Med Wall Mastic) | 1
CTU/CB/300X4 | UG Term 300 XLPE 4c with LVCB | 152475 | Lug Crimp Al 300mm2 M12 | 4
CTU/CB/300X4 | UG Term 300 XLPE 4c with LVCB | 141376 | Lug Crimp Copper 185mm2 M12 | 5
CTU/CB/300X4 | UG Term 300 XLPE 4c with LVCB | 141296 | Neutral Link Brass Alloy (19 x 19mm) with 50x6 Cu Busbar & 2xM12 Brass Studs & Backing Plate | 1
CTU/CB/300X4 | UG Term 300 XLPE 4c with LVCB | N/A | LV Circuit Breaker - place order with TasNetworks | 1
CTU/CB/300X4 | UG Term 300 XLPE 4c with LVCB | 40440 | Nut M12 | 6
CTU/CB/300X4 | UG Term 300 XLPE 4c with LVCB | 141192 | Splice Crimp Bimetal 300al/185cu Round/Round | 4
CTU/CB/300X4 | UG Term 300 XLPE 4c with LVCB | 65615 | Washer Ns 12 | 10
CTU/CB/400X4 | UG Term 400 XLPE 4c with LVCB | 32212 | Bolt Hex M12 X 50 | 4
CTU/CB/400X4 | UG Term 400 XLPE 4c with LVCB | 95240 | Cable LV Cu 1c 240mm2 c x pvc | 4
CTU/CB/400X4 | UG Term 400 XLPE 4c with LVCB | 168446 | Cable Sleeve MWTM 50/16 1200mm (Med Wall Mastic) | 1
CTU/CB/400X4 | UG Term 400 XLPE 4c with LVCB | 141377 | Lug Crimp Copper 240mm2 Blank | 5
CTU/CB/400X4 | UG Term 400 XLPE 4c with LVCB | N/A | LV Circuit Breaker - place order with TasNetworks | 1
CTU/CB/400X4 | UG Term 400 XLPE 4c with LVCB | 152470 | Lug Crimp Aluminium 400mm2 M12 Round | 4
CTU/CB/400X4 | UG Term 400 XLPE 4c with LVCB | 141296 | Neutral Link Brass Alloy (19 x 19mm) with 50x6 Cu Busbar & 2xM12 Brass Studs & Backing Plate | 1
CTU/CB/400X4 | UG Term 400 XLPE 4c with LVCB | 40440 | Nut M12 | 6
CTU/CB/400X4 | UG Term 400 XLPE 4c with LVCB | 65615 | Washer Ns 12 | 10
SUB/PAD/ACC | Padmount Substation Accessories | Sw Labels | Switchgear Locks - place order with TasNetworks | 3
SUB/PAD/ACC | Padmount Substation Accessories | Sw Labels | Substation Locks - place order with TasNetworks | 3
SUB/PAD/ACC | Padmount Substation Accessories | Sub Signs | Substation Number Plate - place order with TasNetworks | 1
EARTH/M_PAD/PLM | Earth KPX Substation PLM (will vary for Mini KPX or Switching Substation) | 102311 | Conductor 70mm2 Bare Cu for Earthing | 50
EARTH/M_PAD/PLM | Earth KPX Substation PLM (will vary for Mini KPX or Switching Substation) | 155134 | Earth Crimp - Rod 13-16mm to Conductor 50-70mm (YGHP29C26) | 6
EARTH/M_PAD/PLM | Earth KPX Substation PLM (will vary for Mini KPX or Switching Substation) | 155010 | Earth Electrode 1800 x 13mm Dia. (Solid Flush Coupling, Extendable) | 6
EARTH/M_PAD/PLM | Earth KPX Substation PLM (will vary for Mini KPX or Switching Substation) | 147350 | Earthing Crimp - Conductor 50-70mm to Conductor 50-70mm (CEC070) | 20
EARTH/M_PAD/PLM | Earth KPX Substation PLM (will vary for Mini KPX or Switching Substation) | 141363 | Lug Crimp 70mm2 tinned copper | 2
EARTH/M_PAD/PLM | Earth KPX Substation PLM (will vary for Mini KPX or Switching Substation) | 94240 | Wire Electrical Cu 70mm2 1c Green/Yellow | 4
EARTH/LV/CABINET | Earth LV Cabinet | 155010 | Earth Electrode 1800 x 13mm Dia. (Solid Flush Coupling, Extendable) | 1
EARTH/LV/CABINET | Earth LV Cabinet | 155132 | Earth Rod Clamp (Brass) for 10-35sq-mm Cable | 1
EARTH/LV/CABINET | Earth LV Cabinet | 94178 | Wire Electrical Cu 35mm2 1c (V-90 PVC) - Green/Yellow | 2
EARTH/LV/TURRET | Earth LV Turret | 155010 | Earth Electrode 1800 x 13mm Dia. (Solid Flush Coupling, Extendable) | 1
EARTH/LV/TURRET | Earth LV Turret | 155132 | Earth Rod Clamp (Brass) for 10-35sq-mm Cable | 1
EARTH/LV/TURRET | Earth LV Turret | 94178 | Wire Electrical Cu 35mm2 1c (V-90 PVC) - Green/Yellow | 2
STLT/A/URD/INST | St Light Installation 7.5m Aurora URD Poles | 222932 | 6A Fuse Cartridge 415V Offset NSD6 | 1
STLT/A/URD/INST | St Light Installation 7.5m Aurora URD Poles | 325540 | Pole Tag with 6 Digit ID Number | 1
STLT/A/URD/INST | St Light Installation 7.5m Aurora URD Poles | 324971 | Steel Column 7.5m with 2m outreach | 1
STLT/A/URD/INST | St Light Installation 7m Aurora URD Poles | 222932 | 6A Fuse Cartridge 415V Offset NSD6 | 1
STLT/A/URD/INST | St Light Installation 7m Aurora URD Poles | 325540 | Pole Tag with 6 Digit ID Number | 1
STLT/A/URD/INST | St Light Installation 7m Aurora URD Poles | 325092 | Steel Column 7m with 0.6m outreach | 1
SIGN/DANGER/UG | Underground Cable Marker Post & Danger Sign PLM | 72222 | Concrete Quick Mix 20kg | 1
SIGN/DANGER/UG | Underground Cable Marker Post & Danger Sign PLM | 348412 | Guide Post White Powder Coated predrilled for Danger Signs | 1
SIGN/DANGER/UG | Underground Cable Marker Post & Danger Sign PLM | 26111 | Rivet Stainless Steel 3.2mm dia x 7.9mm long | 4
SIGN/DANGER/UG | Underground Cable Marker Post & Danger Sign PLM | 348411 | Sign Danger High Voltage for installation on Guide Posts | 1
CABINET/200/INST | Install 200A Cabinet & Panel | 32177 | Bolt Hex M10 X 25 | 8
CABINET/200/INST | Install 200A Cabinet & Panel | 32178 | Bolt Hex M10 X 30 | 8
CABINET/200/INST | Install 200A Cabinet & Panel | 237370 | Cabinet, Fuse Link 200A 700x500x250 | 1
CABINET/200/INST | Install 200A Cabinet & Panel | 312051 | Insulation panel 400x400x12 for LV Fuse Cabinetsfor LV Fuse Cabinets | 1
CABINET/200/INST | Install 200A Cabinet & Panel | N/A | cabinet locks - place order with TasNetworks | 1
CABINET/200/INST | Install 200A Cabinet & Panel | 146860 | Split Bolt Clamp (for 35sq-mm Earth Leads) | 1
CABINET/200/INST | Install 200A Cabinet & Panel | 237380 | Support Frame 200 & 400amp Fuse Link Cabinet | 1
CABINET/400/3S/INST | Install 400A Cabinet cw 3 x S/Fuses | 32177 | Bolt Hex M10 X 25 | 8
CABINET/400/3S/INST | Install 400A Cabinet cw 3 x S/Fuses | 32178 | Bolt Hex M10 X 30 | 8
CABINET/400/3S/INST | Install 400A Cabinet cw 3 x S/Fuses | 237371 | Cabinet, Fuse Link 400A 1000x500x250 | 1
CABINET/400/3S/INST | Install 400A Cabinet cw 3 x S/Fuses | 169157 | Cable Sleeve Thin Walled Unlined (13-6mm) - BLUE | 1
CABINET/400/3S/INST | Install 400A Cabinet cw 3 x S/Fuses | 169156 | Cable Sleeve Thin Walled Unlined (13-6mm) - WHITE | 1
CABINET/400/3S/INST | Install 400A Cabinet cw 3 x S/Fuses | 220665 | Fuseholder 100A 440V Front Connect | 3
CABINET/400/3S/INST | Install 400A Cabinet cw 3 x S/Fuses | 312051 | Insulation panel 400x400x12 for LV Fuse Cabinetsfor LV Fuse Cabinets | 1
CABINET/400/3S/INST | Install 400A Cabinet cw 3 x S/Fuses | 141369 | Lug Crimp Copper 35mm2 M12 | 4
CABINET/400/3S/INST | Install 400A Cabinet cw 3 x S/Fuses | 141298 | Neutral Link Brass Alloy (19 x 19mm) - Uncovered | 1
CABINET/400/3S/INST | Install 400A Cabinet cw 3 x S/Fuses | 94187 | Wire Electrical Cu 35mm2 1c (V-90 PVC) - Black | 1
CABINET/400/3S/INST | Install 400A Cabinet cw 3 x S/Fuses | 146860 | Split Bolt Clamp (for 35sq-mm Earth Leads) | 1
CABINET/400/3S/INST | Install 400A Cabinet cw 3 x S/Fuses | 237380 | Support Frame 200 & 400amp Fuse Link Cabinet | 1
CABINET/400/3S/INST | Install 400A Cabinet cw 3 x S/Fuses | N/A | cabinet locks - place order with TasNetworks | 1
CABINET/400/3S/INST | Install 400A Cabinet cw 3 x S/Fuses | 94161 | Wire Electrical Cu 35mm2 1c (V-90 PVC) - Red | 3
CABINET/400/INST | Install 400A Cabinet & Panel | 32177 | Bolt Hex M10 X 25 | 8
CABINET/400/INST | Install 400A Cabinet & Panel | 32178 | Bolt Hex M10 X 30 | 8
CABINET/400/INST | Install 400A Cabinet & Panel | 237371 | Cabinet, Fuse Link 400A 1000x500x250 | 1
CABINET/400/INST | Install 400A Cabinet & Panel | 312051 | Insulation panel 400x400x12 for LV Fuse Cabinetsfor LV Fuse Cabinets | 1
CABINET/400/INST | Install 400A Cabinet & Panel | N/A | cabinet locks - place order with TasNetworks | 1
CABINET/400/INST | Install 400A Cabinet & Panel | 146860 | Split Bolt Clamp (for 35sq-mm Earth Leads) | 1
CABINET/400/INST | Install 400A Cabinet & Panel | 237380 | Support Frame 200 & 400amp Fuse Link Cabinet | 1
CABINET/400X/3S/INST | Install 400A Extra Large Cabinet cw 3 x S/Fuses | 32177 | Bolt Hex M10 X 25 | 8
CABINET/400X/3S/INST | Install 400A Extra Large Cabinet cw 3 x S/Fuses | 32178 | Bolt Hex M10 X 30 | 8
CABINET/400X/3S/INST | Install 400A Extra Large Cabinet cw 3 x S/Fuses | 237372 | Cabinet, Fuse Link 400A 1100x750x300 | 1
CABINET/400X/3S/INST | Install 400A Extra Large Cabinet cw 3 x S/Fuses | 169157 | Cable Sleeve Thin Walled Unlined (13-6mm) - BLUE | 1
CABINET/400X/3S/INST | Install 400A Extra Large Cabinet cw 3 x S/Fuses | 169156 | Cable Sleeve Thin Walled Unlined (13-6mm) - WHITE | 1
CABINET/400X/3S/INST | Install 400A Extra Large Cabinet cw 3 x S/Fuses | 220665 | Fuseholder 100A 440V Front Connect | 3
CABINET/400X/3S/INST | Install 400A Extra Large Cabinet cw 3 x S/Fuses | 312052 | Insulation panel 600x400x12 for XL LV Fuse Cabinets | 1
CABINET/400X/3S/INST | Install 400A Extra Large Cabinet cw 3 x S/Fuses | 141369 | Lug Crimp Copper 35mm2 M12 | 4
CABINET/400X/3S/INST | Install 400A Extra Large Cabinet cw 3 x S/Fuses | 141298 | Neutral Link Brass Alloy (19 x 19mm) - Uncovered | 1
CABINET/400X/3S/INST | Install 400A Extra Large Cabinet cw 3 x S/Fuses | 94187 | Wire Electrical Cu 35mm2 1c (V-90 PVC) - Black | 1
CABINET/400X/3S/INST | Install 400A Extra Large Cabinet cw 3 x S/Fuses | 146860 | Split Bolt Clamp (for 35sq-mm Earth Leads) | 1
CABINET/400X/3S/INST | Install 400A Extra Large Cabinet cw 3 x S/Fuses | N/A | cabinet locks - place order with TasNetworks | 1
CABINET/400X/3S/INST | Install 400A Extra Large Cabinet cw 3 x S/Fuses | 237373 | Support Frame extra large 400amp Fuse Link Cabinet | 1
CABINET/400X/3S/INST | Install 400A Extra Large Cabinet cw 3 x S/Fuses | 94161 | Wire Electrical Cu 35mm2 1c (V-90 PVC) - Red | 3
CABINET/400X/INST | Install 400A Extra Large Cabinet & Panel | 32177 | Bolt Hex M10 X 25 | 8
CABINET/400X/INST | Install 400A Extra Large Cabinet & Panel | 32178 | Bolt Hex M10 X 30 | 8
CABINET/400X/INST | Install 400A Extra Large Cabinet & Panel | 237372 | Cabinet, Fuse Link 400A 1100x750x300 | 1
CABINET/400X/INST | Install 400A Extra Large Cabinet & Panel | 312052 | Insulation panel 600x400x12 for XL LV Fuse Cabinets | 1
CABINET/400X/INST | Install 400A Extra Large Cabinet & Panel | N/A | cabinet locks - place order with TasNetworks | 1
CABINET/400X/INST | Install 400A Extra Large Cabinet & Panel | 146860 | Split Bolt Clamp (for 35sq-mm Earth Leads) | 1
CABINET/400X/INST | Install 400A Extra Large Cabinet & Panel | 237373 | Support Frame extra large 400amp Fuse Link Cabinet | 1
CABNT/200/3S/INST | Install 200A Cabinet cw 3 x S/Fuses | 32177 | Bolt Hex M10 X 25 | 8
CABNT/200/3S/INST | Install 200A Cabinet cw 3 x S/Fuses | 32178 | Bolt Hex M10 X 30 | 8
CABNT/200/3S/INST | Install 200A Cabinet cw 3 x S/Fuses | 237370 | Cabinet, Fuse Link 200A 700x500x250 | 1
CABNT/200/3S/INST | Install 200A Cabinet cw 3 x S/Fuses | 169157 | Cable Sleeve Thin Walled Unlined (13-6mm) - BLUE | 1
CABNT/200/3S/INST | Install 200A Cabinet cw 3 x S/Fuses | 169156 | Cable Sleeve Thin Walled Unlined (13-6mm) - WHITE | 1
CABNT/200/3S/INST | Install 200A Cabinet cw 3 x S/Fuses | 220665 | Fuseholder 100A 440V Front Connect | 3
CABNT/200/3S/INST | Install 200A Cabinet cw 3 x S/Fuses | 312051 | Insulation panel 400x400x12 for LV Fuse Cabinetsfor LV Fuse Cabinets | 1
CABNT/200/3S/INST | Install 200A Cabinet cw 3 x S/Fuses | 141369 | Lug Crimp Copper 35mm2 M12 | 4
CABNT/200/3S/INST | Install 200A Cabinet cw 3 x S/Fuses | 141298 | Neutral Link Brass Alloy (19 x 19mm) - Uncovered | 1
CABNT/200/3S/INST | Install 200A Cabinet cw 3 x S/Fuses | 94187 | Wire Electrical Cu 35mm2 1c (V-90 PVC) - Black | 1
CABNT/200/3S/INST | Install 200A Cabinet cw 3 x S/Fuses | 146860 | Split Bolt Clamp (for 35sq-mm Earth Leads) | 1
CABNT/200/3S/INST | Install 200A Cabinet cw 3 x S/Fuses | N/A | cabinet locks - place order with TasNetworks | 1
CABNT/200/3S/INST | Install 200A Cabinet cw 3 x S/Fuses | 237380 | Support Frame 200 & 400amp Fuse Link Cabinet | 1
CABNT/200/3S/INST | Install 200A Cabinet cw 3 x S/Fuses | 94161 | Wire Electrical Cu 35mm2 1c (V-90 PVC) - Red | 4
CABNT/200/3S/SL/INST | Install 200A Cabinet 3 x S/Fuse & S/Lt | 222933 | 10A Fuse Cartridge 415V Offset NS10 | 1
CABNT/200/3S/SL/INST | Install 200A Cabinet 3 x S/Fuse & S/Lt | 32177 | Bolt Hex M10 X 25 | 8
CABNT/200/3S/SL/INST | Install 200A Cabinet 3 x S/Fuse & S/Lt | 32178 | Bolt Hex M10 X 30 | 8
CABNT/200/3S/SL/INST | Install 200A Cabinet 3 x S/Fuse & S/Lt | 237370 | Cabinet, Fuse Link 200A 700x500x250 | 1
CABNT/200/3S/SL/INST | Install 200A Cabinet 3 x S/Fuse & S/Lt | 169157 | Cable Sleeve Thin Walled Unlined (13-6mm) - BLUE | 1
CABNT/200/3S/SL/INST | Install 200A Cabinet 3 x S/Fuse & S/Lt | 169156 | Cable Sleeve Thin Walled Unlined (13-6mm) - WHITE | 1
CABNT/200/3S/SL/INST | Install 200A Cabinet 3 x S/Fuse & S/Lt | 220665 | Fuseholder 100A 440V Front Connect | 3
CABNT/200/3S/SL/INST | Install 200A Cabinet 3 x S/Fuse & S/Lt | 220590 | Fuseholder 32A 415V Front Connect | 1
CABNT/200/3S/SL/INST | Install 200A Cabinet 3 x S/Fuse & S/Lt | 312051 | Insulation panel 400x400x12 for LV Fuse Cabinetsfor LV Fuse Cabinets | 1
CABNT/200/3S/SL/INST | Install 200A Cabinet 3 x S/Fuse & S/Lt | 141369 | Lug Crimp Copper 35mm2 M12 | 4
CABNT/200/3S/SL/INST | Install 200A Cabinet 3 x S/Fuse & S/Lt | 94187 | Wire Electrical Cu 35mm2 1c (V-90 PVC) - Black | 1
CABNT/200/3S/SL/INST | Install 200A Cabinet 3 x S/Fuse & S/Lt | 141298 | Neutral Link Brass Alloy (19 x 19mm) - Uncovered | 2
CABNT/200/3S/SL/INST | Install 200A Cabinet 3 x S/Fuse & S/Lt | 146860 | Split Bolt Clamp (for 35sq-mm Earth Leads) | 1
CABNT/200/3S/SL/INST | Install 200A Cabinet 3 x S/Fuse & S/Lt | 237380 | Support Frame 200 & 400amp Fuse Link Cabinet | 1
CABNT/200/3S/SL/INST | Install 200A Cabinet 3 x S/Fuse & S/Lt | N/A | cabinet locks - place order with TasNetworks | 1
CABNT/200/3S/SL/INST | Install 200A Cabinet 3 x S/Fuse & S/Lt | 94170 | Wire Electrical Cu 10mm2 1c Red | 1
CABNT/200/3S/SL/INST | Install 200A Cabinet 3 x S/Fuse & S/Lt | 94161 | Wire Electrical Cu 35mm2 1c (V-90 PVC) - Red | 4
CABNT/200/3S/SL/INST | Install 200A Cabinet 3 x S/Fuse & S/Lt | 94178 | Wire Electrical Cu 35mm2 1c (V-90 PVC) - Green/Yellow | 1
CABNT/400/3S/SL/INST | Install 400A Cabinet 3 x S/Fuse & S/Lt | 222933 | 10A Fuse Cartridge 415V Offset NS10 | 1
CABNT/400/3S/SL/INST | Install 400A Cabinet 3 x S/Fuse & S/Lt | 32177 | Bolt Hex M10 X 25 | 8
CABNT/400/3S/SL/INST | Install 400A Cabinet 3 x S/Fuse & S/Lt | 32178 | Bolt Hex M10 X 30 | 8
CABNT/400/3S/SL/INST | Install 400A Cabinet 3 x S/Fuse & S/Lt | 237371 | Cabinet, Fuse Link 400A 1000x500x250 | 1
CABNT/400/3S/SL/INST | Install 400A Cabinet 3 x S/Fuse & S/Lt | 169157 | Cable Sleeve Thin Walled Unlined (13-6mm) - BLUE | 1
CABNT/400/3S/SL/INST | Install 400A Cabinet 3 x S/Fuse & S/Lt | 169156 | Cable Sleeve Thin Walled Unlined (13-6mm) - WHITE | 1
CABNT/400/3S/SL/INST | Install 400A Cabinet 3 x S/Fuse & S/Lt | 220665 | Fuseholder 100A 440V Front Connect | 3
CABNT/400/3S/SL/INST | Install 400A Cabinet 3 x S/Fuse & S/Lt | 220590 | Fuseholder 32A 415V Front Connect | 1
CABNT/400/3S/SL/INST | Install 400A Cabinet 3 x S/Fuse & S/Lt | 312051 | Insulation panel 400x400x12 for LV Fuse Cabinetsfor LV Fuse Cabinets | 1
CABNT/400/3S/SL/INST | Install 400A Cabinet 3 x S/Fuse & S/Lt | 141369 | Lug Crimp Copper 35mm2 M12 | 4
CABNT/400/3S/SL/INST | Install 400A Cabinet 3 x S/Fuse & S/Lt | 141298 | Neutral Link Brass Alloy (19 x 19mm) - Uncovered | 2
CABNT/400/3S/SL/INST | Install 400A Cabinet 3 x S/Fuse & S/Lt | 94187 | Wire Electrical Cu 35mm2 1c (V-90 PVC) - Black | 1
CABNT/400/3S/SL/INST | Install 400A Cabinet 3 x S/Fuse & S/Lt | 94178 | Wire Electrical Cu 35mm2 1c (V-90 PVC) - Green/Yellow | 1
CABNT/400/3S/SL/INST | Install 400A Cabinet 3 x S/Fuse & S/Lt | 146860 | Split Bolt Clamp (for 35sq-mm Earth Leads) | 1
CABNT/400/3S/SL/INST | Install 400A Cabinet 3 x S/Fuse & S/Lt | N/A | cabinet locks - place order with TasNetworks | 1
CABNT/400/3S/SL/INST | Install 400A Cabinet 3 x S/Fuse & S/Lt | 237380 | Support Frame 200 & 400amp Fuse Link Cabinet | 1
CABNT/400/3S/SL/INST | Install 400A Cabinet 3 x S/Fuse & S/Lt | 94170 | Wire Electrical Cu 10mm2 1c Red | 1
CABNT/400/3S/SL/INST | Install 400A Cabinet 3 x S/Fuse & S/Lt | 94161 | Wire Electrical Cu 35mm2 1c (V-90 PVC) - Red | 4
CABNT/400X/3S/SL/INST | Install 400A Extra Large Cabinet 3 x S/Fuse & S/Lt | 222933 | 10A Fuse Cartridge 415V Offset NS10 | 1
CABNT/400X/3S/SL/INST | Install 400A Extra Large Cabinet 3 x S/Fuse & S/Lt | 32177 | Bolt Hex M10 X 25 | 8
CABNT/400X/3S/SL/INST | Install 400A Extra Large Cabinet 3 x S/Fuse & S/Lt | 32178 | Bolt Hex M10 X 30 | 8
CABNT/400X/3S/SL/INST | Install 400A Extra Large Cabinet 3 x S/Fuse & S/Lt | 237372 | Cabinet, Fuse Link 400A 1100x750x300 | 1
CABNT/400X/3S/SL/INST | Install 400A Extra Large Cabinet 3 x S/Fuse & S/Lt | 169157 | Cable Sleeve Thin Walled Unlined (13-6mm) - BLUE | 1
CABNT/400X/3S/SL/INST | Install 400A Extra Large Cabinet 3 x S/Fuse & S/Lt | 169156 | Cable Sleeve Thin Walled Unlined (13-6mm) - WHITE | 1
CABNT/400X/3S/SL/INST | Install 400A Extra Large Cabinet 3 x S/Fuse & S/Lt | 220665 | Fuseholder 100A 440V Front Connect | 3
CABNT/400X/3S/SL/INST | Install 400A Extra Large Cabinet 3 x S/Fuse & S/Lt | 220590 | Fuseholder 32A 415V Front Connect | 1
CABNT/400X/3S/SL/INST | Install 400A Extra Large Cabinet 3 x S/Fuse & S/Lt | 312052 | Insulation panel 600x400x12 for XL LV Fuse Cabinets | 1
CABNT/400X/3S/SL/INST | Install 400A Extra Large Cabinet 3 x S/Fuse & S/Lt | 141369 | Lug Crimp Copper 35mm2 M12 | 4
CABNT/400X/3S/SL/INST | Install 400A Extra Large Cabinet 3 x S/Fuse & S/Lt | 141298 | Neutral Link Brass Alloy (19 x 19mm) - Uncovered | 2
CABNT/400X/3S/SL/INST | Install 400A Extra Large Cabinet 3 x S/Fuse & S/Lt | 94187 | Wire Electrical Cu 35mm2 1c (V-90 PVC) - Black | 1
CABNT/400X/3S/SL/INST | Install 400A Extra Large Cabinet 3 x S/Fuse & S/Lt | 146860 | Split Bolt Clamp (for 35sq-mm Earth Leads) | 1
CABNT/400X/3S/SL/INST | Install 400A Extra Large Cabinet 3 x S/Fuse & S/Lt | N/A | cabinet locks - place order with TasNetworks | 1
CABNT/400X/3S/SL/INST | Install 400A Extra Large Cabinet 3 x S/Fuse & S/Lt | 237373 | Support Frame extra large 400amp Fuse Link Cabinet | 1
CABNT/400X/3S/SL/INST | Install 400A Extra Large Cabinet 3 x S/Fuse & S/Lt | 94170 | Wire Electrical Cu 10mm2 1c Red | 1
CABNT/400X/3S/SL/INST | Install 400A Extra Large Cabinet 3 x S/Fuse & S/Lt | 94161 | Wire Electrical Cu 35mm2 1c (V-90 PVC) - Red | 4
CABNT/400X/3S/SL/INST | Install 400A Extra Large Cabinet 3 x S/Fuse & S/Lt | 94178 | Wire Electrical Cu 35mm2 1c (V-90 PVC) - Green/Yellow | 1
TURRET/3S/SL/INST | Install Turret 3 x S/Fuse & S/Lt | 222933 | 10A Fuse Cartridge 415V Offset NS10 | 1
TURRET/3S/SL/INST | Install Turret 3 x S/Fuse & S/Lt | 325742 | Turret Base (Series 2) | 1
TURRET/3S/SL/INST | Install Turret 3 x S/Fuse & S/Lt | 325745 | Turret Cover | 1
TURRET/3S/SL/INST | Install Turret 3 x S/Fuse & S/Lt | 141298 | Neutral Link Brass Alloy (19 x 19mm) - Uncovered | 1
TURRET/3S/SL/INST | Install Turret 3 x S/Fuse & S/Lt | 325730 | Turret Fuse Panel Melamine - 3 x S/Fuses + S/L & N/Link | 1
TURRET/6S/SL/INST | Install Turret 6 x S/Fuse & S/Lt | 222933 | 10A Fuse Cartridge 415V Offset NS10 | 1
TURRET/6S/SL/INST | Install Turret 6 x S/Fuse & S/Lt | 325742 | Turret Base (Series 2) | 1
TURRET/6S/SL/INST | Install Turret 6 x S/Fuse & S/Lt | 325745 | Turret Cover | 1
TURRET/6S/SL/INST | Install Turret 6 x S/Fuse & S/Lt | 325729 | Turret Fuse Panel Melamine - 6 x S/Fuses + S/L & N/Link | 1
TURRET/INST | Install Turret & Panel | 325742 | Turret Base (Series 2) | 1
TURRET/INST | Install Turret & Panel | 325745 | Turret Cover | 1
TURRET/INST | Install Turret & Panel | 325727 | Turret Fuse Panel Melamine - Blank (492 x 205) | 1
TURRET/XL/3S/SL/INST | Install Turret (XL) 3 x S/Fuse & S/Lt | 222933 | 10A Fuse Cartridge 415V Offset NS10 | 1
TURRET/XL/3S/SL/INST | Install Turret (XL) 3 x S/Fuse & S/Lt | 32896 | Pan HD M10 X 35 Tamper proof | 4
TURRET/XL/3S/SL/INST | Install Turret (XL) 3 x S/Fuse & S/Lt | 325754 | Turret Base (XL) - 300H x 330W x 530D | 1
TURRET/XL/3S/SL/INST | Install Turret (XL) 3 x S/Fuse & S/Lt | 325753 | Turret Cover (XL) - 600H x 325W x 330D | 1
TURRET/XL/3S/SL/INST | Install Turret (XL) 3 x S/Fuse & S/Lt | 325730 | Turret Fuse Panel Melamine - 3 x S/Fuses + S/L & N/Link | 1
TURRET/XL/3S/SL/INST | Install Turret (XL) 3 x S/Fuse & S/Lt | 141298 | Neutral Link Brass Alloy (19 x 19mm) - Uncovered | 1
TURRET/XL/6S/SL/INST | Install Turret (XL) 6 x S/Fuse & S/Lt | 222933 | 10A Fuse Cartridge 415V Offset NS10 | 1
TURRET/XL/6S/SL/INST | Install Turret (XL) 6 x S/Fuse & S/Lt | 32896 | Pan HD M10 X 35 Tamper proof | 4
TURRET/XL/6S/SL/INST | Install Turret (XL) 6 x S/Fuse & S/Lt | 325754 | Turret Base (XL) - 300H x 330W x 530D | 1
TURRET/XL/6S/SL/INST | Install Turret (XL) 6 x S/Fuse & S/Lt | 325753 | Turret Cover (XL) - 600H x 325W x 330D | 1
TURRET/XL/6S/SL/INST | Install Turret (XL) 6 x S/Fuse & S/Lt | 325729 | Turret Fuse Panel Melamine - 6 x S/Fuses + S/L & N/Link | 1
TURRET/XL/6S/SL/INST | Install Turret (XL) 6 x S/Fuse & S/Lt | 141298 | Neutral Link Brass Alloy (19 x 19mm) - Uncovered | 1
TURRET/XL/INST | Install Turret (XL) & Panel | 32896 | Pan HD M10 X 35 Tamper proof | 4
TURRET/XL/INST | Install Turret (XL) & Panel | 325754 | Turret Base (XL) - 300H x 330W x 530D | 1
TURRET/XL/INST | Install Turret (XL) & Panel | 325753 | Turret Cover (XL) - 600H x 325W x 330D | 1
TURRET/XL/INST | Install Turret (XL) & Panel | 325727 | Turret Fuse Panel Melamine - Blank (492 x 205) | 1