## Disclaimer
TasNetworks – Annual Planning Report 2023 – Supplementary Information
This information contained in this file forms part of TasNetworks Annual Planning Report 2023.
This Annual Planning Report (APR) has been prepared and published by Tasmanian Networks Pty Ltd (TasNetworks) solely for the purposes of TasNetworks’ compliance with regulatory obligations, including sections 5.12.2 and 5.13.2 of the National Electricity Rules and our transmission licence. The APR sets out network planning proposals, scenarios and forecasts as at the date of publication, which may change at any time or not eventuate. It has been prepared in good faith, including information and assumptions provided by third parties without further verification. It may not contain all information on the subject matter. Nothing in this APR should be taken as a recommendation in respect of any possible investment. Anyone considering using the information contained in this document should independently verify the currency, reliability, accuracy and completeness of the information. Accordingly, reliance should not be placed on the information contained in this document and TasNetworks makes no representation or warranty as to the reliability, accuracy or completeness of the information, or its suitability for any purpose other than the purpose for which it has been prepared. To the maximum extent permitted by law, TasNetworks, its employees, agents and consultants will have no liability for any loss or damage arising out of, or in connection with, the statements, opinions or other information in this document (including liability by reason of negligence or negligent misstatement).

## Assumptions + methodology
Tx-Dx connection points | Zone subs & sub-trans lines | Substation and sub-transmission line capacity - The substation (total or firm) capacity is generally the capacity of the supply transformers, however may be limited by substation terminal equipment. Generally, for transmission substations the short-term rating is the four-hour rating of the transformers. For zone substation supply transformers and sub-transmission lines we apply generic short-term overload capabilities of 30% and 20%, respectively. Maximum demand forecast - The methodology and assumptions used in developing the forecasts is presented in Appendix A.3.2 of this APR. We do not forecast reactive power and power factor values - our forecast model uses the actual value from the preceeding year. As all zone substations are radially supplied, the zone substation maximum demand forecasts also apply to the sub-transmission lines supplying them. Hours exceeding - We forecast future load profiles by taking the preceeding year's load profile and growing it by the ratio of the forecast maximum demand of that profile to the recorded maximum demand of that profile. That is, if the maximum demand is forecast to grow at 1.1%pa, the energy is multiplied by 1.1%pa also. As all points on the load profile are forecast to grow at the same rate, the value of hours exceeding 95% of peak load will not grow over the forecast period (as that value also grows at the maximum demand growth rate). Load transfer capacity - The load transfer capacities show the capability of the distribution network for the load transer. They do not taken in account the capability of loading beyond the continuous rating of the supply transformer(s) at any given site and do not indicate long term period transfers but for periods of about one day. The analysis uses (in some cases) data from 2009, winter peak loadings, operational knowledge of past successful transfers, and medium-voltage limits (~6 per cent) tolerances. We do not currently forecast load transfer capacities unless for a specific study. Embedded generation capacity - The values provided are for known existing embedded generation. We do not currently forecast embedded generation capacity at connection point, sub-transmission or zone substation level. Individual embedded generating units over 0.5 MW are detailed in Appendix C of this APR.
Distribution line max. demand |  | The methodology and assumptions used in developing the distribution line maximum demand forecasts are detailed in Appendix A.3.2 of this APR.
Updated 3 December 2021

## Tx-Dx connection points
[5 empty] | Planning area |  |  |  | Kingston-South
| Transmission-distribution connection point: |  |  |  | Supplying |  |  |  | Distribution lines
| Electrona |  |  |  | Voltage |  |  |  | 110/11 kV
[5 empty] | Number of transformers |  |  |  | 2
[5 empty] | Peaking season |  |  |  | Winter
Forecast | Parameter |  |  | 2021 (Actual) | 2022 (Actuals) | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
Substation capacity (winter and summer) (MVA) | Total | Substation capacity (winter and summer) (MVA) | ELSubstation capacity (winter and summer) (MVA)Total | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
| Firm delivery | Substation capacity (winter and summer) (MVA) | ELSubstation capacity (winter and summer) (MVA)Firm delivery | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
| Short-term firm delivery | Substation capacity (winter and summer) (MVA) | ELSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
Maximum demand forecast | Maximum demand (MW) | Maximum demand forecast(peak season) | ELMaximum demand forecast(peak season)Maximum demand (MW) | 16.0874 | 16.2653 | 16.205 | 15.9122 | 15.7101 | 15.622 | 15.7743 | 15.891 | 16.0744 | 16.2706 | 16.7059 | 17.003
| Reactive power (coincident) (MVAr) | Maximum demand forecast(peak season) | ELMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 0.94702 | 0.95749 | 0.95394 | 0.93671 | 0.92481 | 0.91963 | 0.92859 | 0.93546 | 0.94626 | 0.9578 | 0.98343 | 1.0009
(Winter peak) | Maximum demand (MVA) | Maximum demand forecast(peak season) | ELMaximum demand forecast(peak season)Maximum demand (MVA) | 16.1153 | 16.2935 | 16.2331 | 15.9397 | 15.7373 | 15.6491 | 15.8016 | 15.9185 | 16.1023 | 16.2988 | 16.7348 | 17.0325
| Power factor (coincident) | Maximum demand forecast(peak season) | ELMaximum demand forecast(peak season)Power factor (coincident) | 0.99827 | 0.99827 | 0.99827 | 0.99827 | 0.99827 | 0.99827 | 0.99827 | 0.99827 | 0.99827 | 0.99827 | 0.99827 | 0.99827
Maximum demand forecast | Maximum demand (MW) | Maximum demand forecast(non-peak season) | ELMaximum demand forecast(non-peak season)Maximum demand (MW) | 9.827 | 10.0548 | 9.7736 | 9.6649 | 9.5295 | 9.5216 | 9.631 | 9.73 | 9.8688 | 10.0693 | 10.3078 | 10.5518
(Summer) | Reactive power (coincident) (MVAr) | Maximum demand forecast(non-peak season) | ELMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 0.52975 | 0.54204 | 0.52688 | 0.52102 | 0.51372 | 0.51329 | 0.51919 | 0.52452 | 0.53201 | 0.54282 | 0.55567 | 0.56883
Hours exceeding | 95% of maximum demand | Hours exceeding | ELHours exceeding95% of maximum demand | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
Regional diversity factor | Summer | Regional diversity factor | ELRegional diversity factorSummer | 0.78257 | 0.78257 | 0.78257 | 0.78257 | 0.78257 | 0.78257 | 0.78257 | 0.78257 | 0.78257 | 0.78257 | 0.78257 | 0.78257
| Winter | Regional diversity factor | ELRegional diversity factorWinter | 0.88141 | 0.88141 | 0.88141 | 0.88141 | 0.88141 | 0.88141 | 0.88141 | 0.88141 | 0.88141 | 0.88141 | 0.88141 | 0.88141
Load transfer capacity (MVA) | Kingston | Load transfer capacity (MVA)1 | ELLoad transfer capacity (MVA)1 | 8
| Knights Road | Load transfer capacity (MVA)2 | ELLoad transfer capacity (MVA)2 | 3
|  | Load transfer capacity (MVA)3 | ELLoad transfer capacity (MVA)3
|  | Load transfer capacity (MVA)4 | ELLoad transfer capacity (MVA)4
|  | Load transfer capacity (MVA)5 | ELLoad transfer capacity (MVA)5
Embedded generation capacity (MVA) | Units less than 100 kVA | Embedded generation capacity (MVA) | ELEmbedded generation capacity (MVA)Units less than 100 kVA | 8.7161
| Units greater than 100 kVA | Embedded generation capacity (MVA) | ELEmbedded generation capacity (MVA)Units greater than 100 kVA | 0.1298
| Forecast average day DER generation contribution | Embedded generation forecast capacity (MVA) | ELEmbedded generation forecast capacity (MVA) |  |  | 0.46804 | 0.52105 | 0.56432 | 0.60568 | 0.64542 | 0.68239 | 0.71697 | 0.74946 | 0.77939 | 0.80702
| Forecast average day max generation impact | Embedded generation forecast capacity (MVA) | ELEmbedded generation forecast capacity (MVA) |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Notes
[14 empty] | 2031 | 2032
[14 empty] | 25 | 25
[14 empty] | 30 | 30
[14 empty] | 16.7348 | 17.0325

## T-D data (hidden)
[6 empty] | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 13 | 14
[6 empty] | 2021 (Actual) | 2022 (Actuals) | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | Load transfer point | Non-peaking season | Substation | Planning area | Supplying | Voltage | Number of transformers | Peaking season | Substation | Comment | Sub | hours above 95% load
Arthurs Lake[1] | AL | AL | Substation capacity (winter and summer) (MVA) | Total | ALSubstation capacity (winter and summer) (MVA)Total | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  |  | Arthurs Lake[1] | Central | Distribution lines | 110/6.6 kV | 1 | Winter | Arthurs Lake[1] | [1] Arthurs Lake Substation supplies both distribution and generation-pump load customers. The distribution component only is shown for load forecast and hours exceeding 95% of peak load. Total substation load is used for hours exceeding firm capacity. | AL | 4.5
Avoca | AV | AL | Substation capacity (winter and summer) (MVA) | Firm delivery | ALSubstation capacity (winter and summer) (MVA)Firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Avoca | Eastern | Distribution lines | 110/22 kV | 1 | Summer | Burnie | [1] We propose to replace the supply transformers due to asset condition in 2025 with new units of standard size, as detailed in Section 4.9 of this APR. | AV | 4
Bridgewater | BW | AL | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | ALSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Bridgewater | Greater Hobart | Distribution lines | 110/11 kV | 2 | Winter | Knights Road | [1] We propose to replace the supply transformers due to asset condition in 2030 with new units of standard size, as detailed in Section 4.9 of this APR. | BU | 11.5
Burnie | BU | AL | Maximum demand forecast(peak season) | Maximum demand (MW) | ALMaximum demand forecast(peak season)Maximum demand (MW) | 0.020627 | 0.022525 | 0.022649 | 0.022229 | 0.022022 | 0.021991 | 0.022292 | 0.022498 | 0.022733 | 0.02287 | 0.023295 | 0.0235 |  |  | Burnie | North West | Distribution lines | 110/22 kV | 2 | Winter |  |  | BW | 7.5
Chapel Street | CS | AL | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | ALMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 0.0008164 | 0.00089154 | 0.00089643 | 0.00087983 | 0.00087161 | 0.0008704 | 0.00088229 | 0.00089047 | 0.00089976 | 0.00090519 | 0.000922 | 0.00093013 |  |  | Chapel Street | Greater Hobart | Distribution lines | 110/11 kV | 2 | Winter | Port Latta[1] | [1] Port Latta Substation supplies both distribution and transmission-connected customers. For reasons of confidentiality, the distribution component only is shown for load forecast and hours exceeding 95% of peak load. Total substation load is used for hours exceeding firm capacity. [2] We propose to replace the supply transformers due to condition in 2027, with new standard units, as detailed in Section 4.9 of this APR. | CR | 1
Creek Road | CR | AL | Maximum demand forecast(peak season) | Maximum demand (MVA) | ALMaximum demand forecast(peak season)Maximum demand (MVA) | 0.020643 | 0.022543 | 0.022667 | 0.022247 | 0.022039 | 0.022008 | 0.022309 | 0.022516 | 0.022751 | 0.022888 | 0.023313 | 0.023519 |  |  | Creek Road | Greater Hobart | Sub-transmission lines | 110/33 kV | 3 | Winter | Railton | [1] From summer 2022, load is forecast to exceed the firm rating of the substation, however will be addressed by the connection point at Sheffield Substation. Note: AEMO did not prepare a forecast for the proposed connection point. | CS | 2
Derby | DE | AL | Maximum demand forecast(peak season) | Power factor (coincident) | ALMaximum demand forecast(peak season)Power factor (coincident) | 0.99922 | 0.99922 | 0.99922 | 0.99922 | 0.99922 | 0.99922 | 0.99922 | 0.99922 | 0.99922 | 0.99922 | 0.99922 | 0.99922 |  |  | Derby | Northern | Distribution lines | 110/22 kV | 1 | Summer | Rosebery (44 kV)[1] | [1] Rosebery Substation supplies both distribution and transmission-connected customers. For reasons of confidentiality, the distribution component only is shown for load forecast and hours exceeding 95% of peak load. Total substation load is used for hours exceeding firm capacity. | DB | 0.5
Derwent Bridge | DB | AL | Maximum demand forecast(non-peak season) | Maximum demand (MW) | ALMaximum demand forecast(non-peak season)Maximum demand (MW) | 0.37194 | 0.5246 | 0.51661 | 0.50951 | 0.50378 | 0.50571 | 0.51336 | 0.51894 | 0.52549 | 0.53153 | 0.5372 | 0.54298 |  | Summer | Derwent Bridge | Central | Distribution lines | 110/22 kV | 1 | Winter | Savage River[1] | [1] Savage River Substation supplies both distribution and transmission-connected customers. For reasons of confidentiality, the distribution component only is shown for load forecast and hours exceeding 95% of peak load. Total substation load is used for hours exceeding firm capacity. [2] We propose to replace the supply transformers due to condition in 2029, with new standard units, as detailed in Section 4.9 of this APR. | DE | 1.5
Devonport | DP | AL | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | ALMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 0.014721 | 0.020763 | 0.020447 | 0.020166 | 0.019939 | 0.020016 | 0.020318 | 0.020539 | 0.020798 | 0.021038 | 0.021262 | 0.021491 |  | Summer | Devonport | North West | Distribution lines | 110/22 kV | 3 | Winter | St Marys | [1] Load exceeds substation firm rating, as detailed in Section 4.6.2 of this APR. However, we propose to replace the supply transformers due to condition in 2027, with new standard units providing sufficient capacity for the substation forecast load, detailed in Section 4.9 of this APR. | DP | 4.5
Electrona | EL | AL | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | ALMaximum demand forecast(non-peak season)Maximum demand (MVA) | 0.37223 | 0.52501 | 0.51701 | 0.50991 | 0.50418 | 0.50611 | 0.51376 | 0.51934 | 0.5259 | 0.53195 | 0.53762 | 0.5434 |  | Summer | Electrona | Kingston-South | Distribution lines | 110/11 kV | 2 | Winter | Tungatinah | [1] Supply transformer is rated to 25 MVA, but substation is limited to 13 MVA by bay conductor. | EB | 7.5
Emu Bay | EB | AL | Hours exceeding | 95% of maximum demand | ALHours exceeding95% of maximum demand | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 |  |  | Emu Bay | North West | Distribution lines | 110/11 kV | 2 | Winter | Waddamana | [1] Waddamana transformer rated to 5 MVA, but substation is limited to 3.8 MVA by 22 kV combined voltage-current transformer. [2] We propose to replace the supply transformer due to asset condition in 2029 with new units of standard size, as detailed in Section 4.9 of this APR. | EL | 2
George Town | GT | AL | Hours exceeding | Firm capacity (continuous rating) | ALHours exceedingFirm capacity (continuous rating) | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 |  |  | George Town | Northern | Distribution lines | 110/22 kV | 2 | Winter | Rosebery (44 kV)[1] | [1] We propose to replace the supply transformers due to asset condition in 2029 with new units of standard size, as detailed in Section 4.9 of this APR. | GT | 6
Hadspen | HA | AL | Hours exceeding | Firm capacity (short-term rating) | ALHours exceedingFirm capacity (short-term rating) | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 |  |  | Hadspen | Northern | Distribution lines | 110/22 kV | 2 | Winter |  |  | HA | 9
Huon River | HR | AL | Regional diversity factor | Summer | ALRegional diversity factorSummer | 0.80435 | 0.80435 | 0.80435 | 0.80435 | 0.80435 | 0.80435 | 0.80435 | 0.80435 | 0.80435 | 0.80435 | 0.80435 | 0.80435 |  |  | Huon River | Kingston-South | Distribution lines | 110/11 kV | 1 | Winter |  |  | HR | 0.5
Kermandie | KE | AL | Regional diversity factor | Winter | ALRegional diversity factorWinter | 0.5974 | 0.5974 | 0.5974 | 0.5974 | 0.5974 | 0.5974 | 0.5974 | 0.5974 | 0.5974 | 0.5974 | 0.5974 | 0.5974 |  |  | Kermandie | Kingston-South | Distribution lines | 110/11 kV | 2 | Winter |  |  | KE | 2
Kingston (11 kV) | KI11 | AL | Load transfer capacity (MVA) | 1 | ALLoad transfer capacity (MVA)1 | 0.1 | [11 empty] | Wayatinah |  | Kingston (11 kV) | Kingston-South | Distribution lines | 110/11 kV | 2 | Winter |  |  | KI11 | 2
Kingston (33 kV) | KI33 | AL | Load transfer capacity (MVA) | 2 | ALLoad transfer capacity (MVA)2 | [14 empty] | Kingston (33 kV) | Kingston-South | Sub-transmission lines | 110/33 kV | 2 | Winter |  |  | KI33 | 2
Knights Road | KR | AL | Load transfer capacity (MVA) | 3 | ALLoad transfer capacity (MVA)3 | [14 empty] | Knights Road | Kingston-South | Distribution lines | 110/11 kV | 2 | Winter |  |  | KR | 10
Lindisfarne | LF | AL | Load transfer capacity (MVA) | 4 | ALLoad transfer capacity (MVA)4 | [14 empty] | Lindisfarne | Greater Hobart | Sub-transmission lines | 110/33 kV | 2 | Winter |  |  | LF | 2
Meadowbank | MB | AL | Load transfer capacity (MVA) | 5 | ALLoad transfer capacity (MVA)5 | [14 empty] | Meadowbank | Central | Distribution lines | 110/22 kV | 1 | Summer |  |  | MB | 10.5
Mornington | MT | AL | Embedded generation capacity (MVA) | Units less than 100 kVA | ALEmbedded generation capacity (MVA)Units less than 100 kVA | 0.36324 | [13 empty] | Mornington | Greater Hobart | Sub-transmission lines | 110/33 kV | 2 | Winter |  |  | MT | 2
Mowbray | MY | AL | Embedded generation capacity (MVA) | Units greater than 100 kVA | ALEmbedded generation capacity (MVA)Units greater than 100 kVA | 1.6 | [13 empty] | Mowbray | Northern | Distribution lines | 110/22 kV | 2 | Winter |  |  | MY | 13
New Norfolk | NN | AV | Substation capacity (winter and summer) (MVA) | Total | AVSubstation capacity (winter and summer) (MVA)Total | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  |  | New Norfolk | Central | Distribution lines | 110/22 kV | 2 | Winter |  |  | NH | 17.5
Newton | NT | AV | Substation capacity (winter and summer) (MVA) | Firm delivery | AVSubstation capacity (winter and summer) (MVA)Firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Newton | West Cost | Distribution lines | 110/22 kV | 1 | Summer |  |  | NN | 6
North Hobart | NH | AV | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | AVSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | North Hobart | Greater Hobart | Distribution lines | 110/11 kV | 2 | Winter |  |  | NT | 15
Norwood | NW | AV | Maximum demand forecast(peak season) | Maximum demand (MW) | AVMaximum demand forecast(peak season)Maximum demand (MW) | 7.2563 | 8.1132 | 8.3348 | 8.2368 | 8.2241 | 8.2535 | 8.442 | 8.5969 | 8.7927 | 8.9491 | 9.2263 | 9.4476 |  |  | Norwood | Northern | Distribution lines | 110/22 kV | 2 | Winter |  |  | NW | 4
Palmerston | PM | AV | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | AVMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 1.2544 | 1.4025 | 1.4408 | 1.4239 | 1.4217 | 1.4267 | 1.4593 | 1.4861 | 1.52 | 1.547 | 1.5949 | 1.6332 |  |  | Palmerston | Northern | Distribution lines | 110/22 kV | 2 | Summer |  |  | PL | 5.5
Port Latta[1] | PL | AV | Maximum demand forecast(peak season) | Maximum demand (MVA) | AVMaximum demand forecast(peak season)Maximum demand (MVA) | 7.3639 | 8.2335 | 8.4584 | 8.359 | 8.3461 | 8.3759 | 8.5672 | 8.7244 | 8.9231 | 9.0819 | 9.3631 | 9.5878 |  |  | Port Latta[1] | North West | Distribution lines and transmission-connected customer | 110/22 kV | 2 | Summer |  |  | PM | 14
Queenstown | QT | AV | Maximum demand forecast(peak season) | Power factor (coincident) | AVMaximum demand forecast(peak season)Power factor (coincident) | 0.98539 | 0.98539 | 0.98539 | 0.98539 | 0.98539 | 0.98539 | 0.98539 | 0.98539 | 0.98539 | 0.98539 | 0.98539 | 0.98539 |  |  | Queenstown | West Coast | Distribution lines | 110/22 kV | 2 | Winter |  |  | QT | 7
Railton | RA | AV | Maximum demand forecast(non-peak season) | Maximum demand (MW) | AVMaximum demand forecast(non-peak season)Maximum demand (MW) | 10.1753 | 13.1041 | 13.1487 | 12.9878 | 12.8867 | 12.9506 | 13.2171 | 13.4291 | 13.697 | 13.9455 | 14.1959 | 14.5025 |  | Summer | Railton | North West | Distribution lines | 110/22 kV | 2 | Summer |  |  | RA | 13.5
Risdon | RI | AV | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | AVMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 1.759 | 2.2653 | 2.273 | 2.2451 | 2.2277 | 2.2387 | 2.2848 | 2.3214 | 2.3677 | 2.4107 | 2.454 | 2.507 |  | Summer | Risdon | Greater Hobart | Sub-transmission lines | 110/33 kV | 3 | Winter |  |  | RB22 | 1.5
Rokeby | RK | AV | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | AVMaximum demand forecast(non-peak season)Maximum demand (MVA) | 10.3262 | 13.2985 | 13.3437 | 13.1804 | 13.0778 | 13.1427 | 13.4131 | 13.6283 | 13.9001 | 14.1524 | 14.4064 | 14.7176 |  | Summer | Rokeby | Greater Hobart | Distribution lines | 110/11 kV | 2 | Winter |  |  | RB44 | 154
Rosebery (22 kV) | RB22 | AV | Hours exceeding | 95% of maximum demand | AVHours exceeding95% of maximum demand | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 |  |  | Rosebery (22 kV) | West Coast | Distribution lines | 44/22 kV | 2 | Winter |  |  | RI | 23.5
Rosebery (44 kV)[1] | RB44 | AV | Hours exceeding | Firm capacity (continuous rating) | AVHours exceedingFirm capacity (continuous rating) | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 |  |  | Rosebery (44 kV)[1] | West Coast | Distribution lines and transmission-connected customer | 110/44 kV | 2 | Winter |  |  | RK | 1.5
Savage River[1] | SR | AV | Hours exceeding | Firm capacity (short-term rating) | AVHours exceedingFirm capacity (short-term rating) | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 |  |  | Savage River[1] | West Coast | Distribution lines and transmission-connected customer | 110/22 kV | 2 | Winter |  |  | SD | 20
Scottsdale | SD | AV | Regional diversity factor | Summer | AVRegional diversity factorSummer | 0.43165 | 0.43165 | 0.43165 | 0.43165 | 0.43165 | 0.43165 | 0.43165 | 0.43165 | 0.43165 | 0.43165 | 0.43165 | 0.43165 |  |  | Scottsdale | Northern | Distribution lines | 110/22 kV | 2 | Summer |  |  | SL | 5.5
Smithton | ST | AV | Regional diversity factor | Winter | AVRegional diversity factorWinter | 0.73008 | 0.73008 | 0.73008 | 0.73008 | 0.73008 | 0.73008 | 0.73008 | 0.73008 | 0.73008 | 0.73008 | 0.73008 | 0.73008 |  |  | Smithton | North West | Distribution lines | 110/22 kV | 2 | Winter |  |  | SM | 6
Sorell | SO | AV | Load transfer capacity (MVA) | 1 | AVLoad transfer capacity (MVA)1 | 4.6 | [11 empty] | Palmerston |  | Sorell | Eastern | Distribution lines | 110/22 kV | 2 | Winter |  |  | SO | 1.5
St Leonards | SL | AV | Load transfer capacity (MVA) | 2 | AVLoad transfer capacity (MVA)2 | 4.6 | [11 empty] | St Marys |  | St Leonards | Northern | Distribution lines | 110/22 kV | 2 | Winter |  |  | SR | 3
St Marys | SM | AV | Load transfer capacity (MVA) | 3 | AVLoad transfer capacity (MVA)3 | [14 empty] | St Marys | Eastern | Distribution lines | 110/22 kV | 2 | Winter |  |  | ST | 5.5
Trevallyn | TR | AV | Load transfer capacity (MVA) | 4 | AVLoad transfer capacity (MVA)4 | [14 empty] | Trevallyn | Northern | Distribution lines | 110/22 kV | 3 | Winter |  |  | TB | 1.5
Triabunna | TB | AV | Load transfer capacity (MVA) | 5 | AVLoad transfer capacity (MVA)5 | [14 empty] | Triabunna | Eastern | Distribution lines | 110/22 kV | 2 | Winter |  |  | TR | 13.5
Tungatinah | TU | AV | Embedded generation capacity (MVA) | Units less than 100 kVA | AVEmbedded generation capacity (MVA)Units less than 100 kVA | 1.2114 | [13 empty] | Tungatinah | Central | Distribution lines | 110/22 kV | 1 | Winter |  |  | TU | 11.5
Ulverstone | UL | AV | Embedded generation capacity (MVA) | Units greater than 100 kVA | AVEmbedded generation capacity (MVA)Units greater than 100 kVA | 5 | [13 empty] | Ulverstone | North West | Distribution lines | 110/22 kV | 2 | Winter |  |  | UL | 2.5
Waddamana | WA | BU | Substation capacity (winter and summer) (MVA) | Total | BUSubstation capacity (winter and summer) (MVA)Total | 120 | 120 | 120 | 120 | 120 | 120[1] | 120 | 120 | 120 | 120 | 120 | 120 |  |  | Waddamana | Central | Distribution lines | 110/22 kV | 1 | Winter |  |  | WA | 1.5
Wesley Vale | WV | BU | Substation capacity (winter and summer) (MVA) | Firm delivery | BUSubstation capacity (winter and summer) (MVA)Firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  |  | Wesley Vale | North West | Distribution lines | 110/22 kV [1] | 2 | Winter |  |  | WV | 9
|  | BU | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | BUSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72
|  | BU | Maximum demand forecast(peak season) | Maximum demand (MW) | BUMaximum demand forecast(peak season)Maximum demand (MW) | 57.4354 | 58.0471 | 57.8226 | 56.6683 | 56.073 | 56.1517 | 56.8869 | 57.4787 | 58.3254 | 59.0435 | 60.6729 | 61.7615
|  | BU | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | BUMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 3.0105 | 3.0425 | 3.0308 | 2.9703 | 2.9391 | 2.9432 | 2.9817 | 3.0127 | 3.0571 | 3.0948 | 3.1802 | 3.2372
|  | BU | Maximum demand forecast(peak season) | Maximum demand (MVA) | BUMaximum demand forecast(peak season)Maximum demand (MVA) | 57.5142 | 58.1268 | 57.902 | 56.7461 | 56.15 | 56.2288 | 56.965 | 57.5576 | 58.4054 | 59.1245 | 60.7562 | 61.8463
|  | BU | Maximum demand forecast(peak season) | Power factor (coincident) | BUMaximum demand forecast(peak season)Power factor (coincident) | 0.99863 | 0.99863 | 0.99863 | 0.99863 | 0.99863 | 0.99863 | 0.99863 | 0.99863 | 0.99863 | 0.99863 | 0.99863 | 0.99863
|  | BU | Maximum demand forecast(non-peak season) | Maximum demand (MW) | BUMaximum demand forecast(non-peak season)Maximum demand (MW) | 44.3258 | 41.7593 | 40.7875 | 40.1281 | 39.6015 | 39.8603 | 40.4257 | 40.9142 | 41.5669 | 42.3158 | 43.1897 | 44.0995 |  | Summer
|  | BU | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | BUMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 2.2776 | 2.1457 | 2.0958 | 2.0619 | 2.0349 | 2.0482 | 2.0772 | 2.1023 | 2.1359 | 2.1743 | 2.2193 | 2.266 |  | Summer
|  | BU | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | BUMaximum demand forecast(non-peak season)Maximum demand (MVA) | 44.3842 | 41.8144 | 40.8413 | 40.1811 | 39.6538 | 39.9128 | 40.479 | 40.9682 | 41.6218 | 42.3717 | 43.2467 | 44.1577 |  | Summer
|  | BU | Hours exceeding | 95% of maximum demand | BUHours exceeding95% of maximum demand | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5
|  | BU | Hours exceeding | Firm capacity (continuous rating) | BUHours exceedingFirm capacity (continuous rating)
|  | BU | Hours exceeding | Firm capacity (short-term rating) | BUHours exceedingFirm capacity (short-term rating)
|  | BU | Regional diversity factor | Summer | BURegional diversity factorSummer | 0.93437 | 0.93437 | 0.93437 | 0.93437 | 0.93437 | 0.93437 | 0.93437 | 0.93437 | 0.93437 | 0.93437 | 0.93437 | 0.93437
|  | BU | Regional diversity factor | Winter | BURegional diversity factorWinter | 0.92899 | 0.92899 | 0.92899 | 0.92899 | 0.92899 | 0.92899 | 0.92899 | 0.92899 | 0.92899 | 0.92899 | 0.92899 | 0.92899
|  | BU | Load transfer capacity (MVA) | 1 | BULoad transfer capacity (MVA)1 | 8.8 | [11 empty] | Port Latta
|  | BU | Load transfer capacity (MVA) | 2 | BULoad transfer capacity (MVA)2 | 8.8 | [11 empty] | Ulverstone
|  | BU | Load transfer capacity (MVA) | 3 | BULoad transfer capacity (MVA)3
|  | BU | Load transfer capacity (MVA) | 4 | BULoad transfer capacity (MVA)4
|  | BU | Load transfer capacity (MVA) | 5 | BULoad transfer capacity (MVA)5
|  | BU | Embedded generation capacity (MVA) | Units less than 100 kVA | BUEmbedded generation capacity (MVA)Units less than 100 kVA | 13.9754
|  | BU | Embedded generation capacity (MVA) | Units greater than 100 kVA | BUEmbedded generation capacity (MVA)Units greater than 100 kVA | 4.1353
|  | BW | Substation capacity (winter and summer) (MVA) | Total | BWSubstation capacity (winter and summer) (MVA)Total | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
|  | BW | Substation capacity (winter and summer) (MVA) | Firm delivery | BWSubstation capacity (winter and summer) (MVA)Firm delivery | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
|  | BW | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | BWSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42
|  | BW | Maximum demand forecast(peak season) | Maximum demand (MW) | BWMaximum demand forecast(peak season)Maximum demand (MW) | 36.4709 | 34.8762 | 35.1435 | 35.4779 | 35.6844 | 35.9142 | 36.592 | 37.1173 | 37.7611 | 38.3755 | 39.5143 | 40.3534
|  | BW | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | BWMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 1.1976 | 1.1452 | 1.154 | 1.165 | 1.1717 | 1.1793 | 1.2015 | 1.2188 | 1.2399 | 1.2601 | 1.2975 | 1.3251
|  | BW | Maximum demand forecast(peak season) | Maximum demand (MVA) | BWMaximum demand forecast(peak season)Maximum demand (MVA) | 36.4906 | 34.895 | 35.1625 | 35.497 | 35.7037 | 35.9336 | 36.6117 | 37.1373 | 37.7814 | 38.3962 | 39.5356 | 40.3752
|  | BW | Maximum demand forecast(peak season) | Power factor (coincident) | BWMaximum demand forecast(peak season)Power factor (coincident) | 0.99946 | 0.99946 | 0.99946 | 0.99946 | 0.99946 | 0.99946 | 0.99946 | 0.99946 | 0.99946 | 0.99946 | 0.99946 | 0.99946
|  | BW | Maximum demand forecast(non-peak season) | Maximum demand (MW) | BWMaximum demand forecast(non-peak season)Maximum demand (MW) | 21.0301 | 19.0942 | 18.4872 | 18.9033 | 18.9778 | 19.0747 | 19.3216 | 19.5041 | 19.7735 | 20.1687 | 20.6391 | 21.1614 |  | Summer
|  | BW | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | BWMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 0.29066 | 0.2639 | 0.25551 | 0.26126 | 0.26229 | 0.26363 | 0.26704 | 0.26957 | 0.27329 | 0.27875 | 0.28525 | 0.29247 |  | Summer
|  | BW | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | BWMaximum demand forecast(non-peak season)Maximum demand (MVA) | 21.0321 | 19.096 | 18.489 | 18.9051 | 18.9796 | 19.0765 | 19.3234 | 19.506 | 19.7753 | 20.1706 | 20.6411 | 21.1634 |  | Summer
|  | BW | Hours exceeding | 95% of maximum demand | BWHours exceeding95% of maximum demand | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
|  | BW | Hours exceeding | Firm capacity (continuous rating) | BWHours exceedingFirm capacity (continuous rating)
|  | BW | Hours exceeding | Firm capacity (short-term rating) | BWHours exceedingFirm capacity (short-term rating)
|  | BW | Regional diversity factor | Summer | BWRegional diversity factorSummer | 0.86038 | 0.86038 | 0.86038 | 0.86038 | 0.86038 | 0.86038 | 0.86038 | 0.86038 | 0.86038 | 0.86038 | 0.86038 | 0.86038
|  | BW | Regional diversity factor | Winter | BWRegional diversity factorWinter | 0.93665 | 0.93665 | 0.93665 | 0.93665 | 0.93665 | 0.93665 | 0.93665 | 0.93665 | 0.93665 | 0.93665 | 0.93665 | 0.93665
|  | BW | Load transfer capacity (MVA) | 1 | BWLoad transfer capacity (MVA)1 | 4.6 | [11 empty] | Claremont
|  | BW | Load transfer capacity (MVA) | 2 | BWLoad transfer capacity (MVA)2 | 3.1 | [11 empty] | Derwent Park
|  | BW | Load transfer capacity (MVA) | 3 | BWLoad transfer capacity (MVA)3 | 1.5 | [11 empty] | New Norfolk
|  | BW | Load transfer capacity (MVA) | 4 | BWLoad transfer capacity (MVA)4
|  | BW | Load transfer capacity (MVA) | 5 | BWLoad transfer capacity (MVA)5
|  | BW | Embedded generation capacity (MVA) | Units less than 100 kVA | BWEmbedded generation capacity (MVA)Units less than 100 kVA | 10.2075
|  | BW | Embedded generation capacity (MVA) | Units greater than 100 kVA | BWEmbedded generation capacity (MVA)Units greater than 100 kVA | 0.32
|  | CR | Substation capacity (winter and summer) (MVA) | Total | CRSubstation capacity (winter and summer) (MVA)Total | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180
|  | CR | Substation capacity (winter and summer) (MVA) | Firm delivery | CRSubstation capacity (winter and summer) (MVA)Firm delivery | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
|  | CR | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | CRSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144
|  | CR | Maximum demand forecast(peak season) | Maximum demand (MW) | CRMaximum demand forecast(peak season)Maximum demand (MW) | 86.5984 | 88.1581 | 88.995 | 88.141 | 87.7071 | 87.9496 | 89.5877 | 91.1007 | 93.0601 | 95.0457 | 98.3181 | 100.8998
|  | CR | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | CRMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 12.6073 | 12.8344 | 12.9562 | 12.8319 | 12.7687 | 12.804 | 13.0425 | 13.2628 | 13.548 | 13.8371 | 14.3135 | 14.6894
|  | CR | Maximum demand forecast(peak season) | Maximum demand (MVA) | CRMaximum demand forecast(peak season)Maximum demand (MVA) | 87.5113 | 89.0875 | 89.9332 | 89.0702 | 88.6317 | 88.8768 | 90.5321 | 92.0611 | 94.0411 | 96.0477 | 99.3545 | 101.9634
|  | CR | Maximum demand forecast(peak season) | Power factor (coincident) | CRMaximum demand forecast(peak season)Power factor (coincident) | 0.98957 | 0.98957 | 0.98957 | 0.98957 | 0.98957 | 0.98957 | 0.98957 | 0.98957 | 0.98957 | 0.98957 | 0.98957 | 0.98957
|  | CR | Maximum demand forecast(non-peak season) | Maximum demand (MW) | CRMaximum demand forecast(non-peak season)Maximum demand (MW) | 56.2826 | 51.8759 | 50.9611 | 50.6185 | 50.071 | 50.1966 | 50.9306 | 51.6422 | 52.5594 | 53.7816 | 55.1235 | 56.5724 |  | Summer
|  | CR | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | CRMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 3.2277 | 2.975 | 2.9225 | 2.9029 | 2.8715 | 2.8787 | 2.9208 | 2.9616 | 3.0142 | 3.0843 | 3.1612 | 3.2443 |  | Summer
|  | CR | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | CRMaximum demand forecast(non-peak season)Maximum demand (MVA) | 56.3751 | 51.9611 | 51.0448 | 50.7017 | 50.1533 | 50.279 | 51.0143 | 51.7271 | 52.6457 | 53.87 | 55.2141 | 56.6653 |  | Summer
|  | CR | Hours exceeding | 95% of maximum demand | CRHours exceeding95% of maximum demand | 1 | 1 | bar: 4 2023 to 13 2032
|  | CR | Hours exceeding | Firm capacity (continuous rating) | CRHours exceedingFirm capacity (continuous rating)
|  | CR | Hours exceeding | Firm capacity (short-term rating) | CRHours exceedingFirm capacity (short-term rating)
|  | CR | Regional diversity factor | Summer | CRRegional diversity factorSummer | 0.8873 | 0.8873 | 0.8873 | 0.8873 | 0.8873 | 0.8873 | 0.8873 | 0.8873 | 0.8873 | 0.8873 | 0.8873 | 0.8873
|  | CR | Regional diversity factor | Winter | CRRegional diversity factorWinter | 0.9452 | 0.9452 | 0.9452 | 0.9452 | 0.9452 | 0.9452 | 0.9452 | 0.9452 | 0.9452 | 0.9452 | 0.9452 | 0.9452
|  | CR | Load transfer capacity (MVA) | 1 | CRLoad transfer capacity (MVA)1 | 13 | [11 empty] | Claremont
|  | CR | Load transfer capacity (MVA) | 2 | CRLoad transfer capacity (MVA)2 | 13 | [11 empty] | Derwent Park
|  | CR | Load transfer capacity (MVA) | 3 | CRLoad transfer capacity (MVA)3 | 3.7 | [11 empty] | New Town
|  | CR | Load transfer capacity (MVA) | 4 | CRLoad transfer capacity (MVA)4 | 7.4 | [11 empty] | North Hobart
|  | CR | Load transfer capacity (MVA) | 5 | CRLoad transfer capacity (MVA)5
|  | CR | Embedded generation capacity (MVA) | Units less than 100 kVA | CREmbedded generation capacity (MVA)Units less than 100 kVA | 15.6436
|  | CR | Embedded generation capacity (MVA) | Units greater than 100 kVA | CREmbedded generation capacity (MVA)Units greater than 100 kVA | 1.065
|  | CS | Substation capacity (winter and summer) (MVA) | Total | CSSubstation capacity (winter and summer) (MVA)Total | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
|  | CS | Substation capacity (winter and summer) (MVA) | Firm delivery | CSSubstation capacity (winter and summer) (MVA)Firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  | CS | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | CSSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  | CS | Maximum demand forecast(peak season) | Maximum demand (MW) | CSMaximum demand forecast(peak season)Maximum demand (MW) | 39.3337 | 38.7499 | 39.2587 | 38.7101 | 38.6727 | 38.926 | 39.8255 | 40.6439 | 41.6456 | 42.6303 | 44.1872 | 45.4008
|  | CS | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | CSMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 0.85382 | 0.84114 | 0.85219 | 0.84028 | 0.83947 | 0.84496 | 0.86449 | 0.88226 | 0.904 | 0.92537 | 0.95917 | 0.98551
|  | CS | Maximum demand forecast(peak season) | Maximum demand (MVA) | CSMaximum demand forecast(peak season)Maximum demand (MVA) | 39.343 | 38.759 | 39.268 | 38.7192 | 38.6818 | 38.9351 | 39.8349 | 40.6535 | 41.6554 | 42.6403 | 44.1976 | 45.4115
|  | CS | Maximum demand forecast(peak season) | Power factor (coincident) | CSMaximum demand forecast(peak season)Power factor (coincident) | 0.99976 | 0.99976 | 0.99976 | 0.99976 | 0.99976 | 0.99976 | 0.99976 | 0.99976 | 0.99976 | 0.99976 | 0.99976 | 0.99976
|  | CS | Maximum demand forecast(non-peak season) | Maximum demand (MW) | CSMaximum demand forecast(non-peak season)Maximum demand (MW) | 21.6881 | 20.2012 | 19.8779 | 19.4818 | 19.3476 | 19.5381 | 20.01 | 20.505 | 21.1027 | 21.9167 | 22.8124 | 23.7824 |  | Summer
|  | CS | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | CSMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 0.036861 | 0.034334 | 0.033785 | 0.033112 | 0.032884 | 0.033207 | 0.034009 | 0.034851 | 0.035867 | 0.03725 | 0.038772 | 0.040421 |  | Summer
|  | CS | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | CSMaximum demand forecast(non-peak season)Maximum demand (MVA) | 21.6881 | 20.2013 | 19.8779 | 19.4818 | 19.3476 | 19.5381 | 20.01 | 20.505 | 21.1028 | 21.9167 | 22.8124 | 23.7825 |  | Summer
|  | CS | Hours exceeding | 95% of maximum demand | CSHours exceeding95% of maximum demand | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  | CS | Hours exceeding | Firm capacity (continuous rating) | CSHours exceedingFirm capacity (continuous rating)
|  | CS | Hours exceeding | Firm capacity (short-term rating) | CSHours exceedingFirm capacity (short-term rating)
|  | CS | Regional diversity factor | Summer | CSRegional diversity factorSummer | 0.92902 | 0.92902 | 0.92902 | 0.92902 | 0.92902 | 0.92902 | 0.92902 | 0.92902 | 0.92902 | 0.92902 | 0.92902 | 0.92902
|  | CS | Regional diversity factor | Winter | CSRegional diversity factorWinter | 0.90185 | 0.90185 | 0.90185 | 0.90185 | 0.90185 | 0.90185 | 0.90185 | 0.90185 | 0.90185 | 0.90185 | 0.90185 | 0.90185
|  | CS | Load transfer capacity (MVA) | 1 | CSLoad transfer capacity (MVA)1 | 13 | [11 empty] | Claremont
|  | CS | Load transfer capacity (MVA) | 2 | CSLoad transfer capacity (MVA)2 | 13 | [11 empty] | Derwent Park
|  | CS | Load transfer capacity (MVA) | 3 | CSLoad transfer capacity (MVA)3 | 3.7 | [11 empty] | New Town
|  | CS | Load transfer capacity (MVA) | 4 | CSLoad transfer capacity (MVA)4 | 7.4 | [11 empty] | North Hobart
|  | CS | Load transfer capacity (MVA) | 5 | CSLoad transfer capacity (MVA)5
|  | CS | Embedded generation capacity (MVA) | Units less than 100 kVA | CSEmbedded generation capacity (MVA)Units less than 100 kVA | 7.4504
|  | CS | Embedded generation capacity (MVA) | Units greater than 100 kVA | CSEmbedded generation capacity (MVA)Units greater than 100 kVA | 1.69
|  | DB | Substation capacity (winter and summer) (MVA) | Total | DBSubstation capacity (winter and summer) (MVA)Total | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
|  | DB | Substation capacity (winter and summer) (MVA) | Firm delivery | DBSubstation capacity (winter and summer) (MVA)Firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | DB | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | DBSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | DB | Maximum demand forecast(peak season) | Maximum demand (MW) | DBMaximum demand forecast(peak season)Maximum demand (MW) | 0.30972 | 0.3331 | 0.33849 | 0.33413 | 0.33272 | 0.33375 | 0.34023 | 0.34529 | 0.35103 | 0.35541 | 0.36434 | 0.37057
|  | DB | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | DBMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 0.032602 | 0.035064 | 0.03563 | 0.035171 | 0.035023 | 0.035131 | 0.035814 | 0.036347 | 0.036951 | 0.037412 | 0.038352 | 0.039007
|  | DB | Maximum demand forecast(peak season) | Maximum demand (MVA) | DBMaximum demand forecast(peak season)Maximum demand (MVA) | 0.31143 | 0.33494 | 0.34036 | 0.33598 | 0.33456 | 0.33559 | 0.34211 | 0.3472 | 0.35297 | 0.35737 | 0.36635 | 0.37262
|  | DB | Maximum demand forecast(peak season) | Power factor (coincident) | DBMaximum demand forecast(peak season)Power factor (coincident) | 0.99451 | 0.99451 | 0.99451 | 0.99451 | 0.99451 | 0.99451 | 0.99451 | 0.99451 | 0.99451 | 0.99451 | 0.99451 | 0.99451
|  | DB | Maximum demand forecast(non-peak season) | Maximum demand (MW) | DBMaximum demand forecast(non-peak season)Maximum demand (MW) | 0.31536 | 0.28429 | 0.2809 | 0.27729 | 0.27455 | 0.27574 | 0.28052 | 0.28424 | 0.28875 | 0.29309 | 0.29747 | 0.30235 |  | Summer
|  | DB | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | DBMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 0.045051 | 0.040613 | 0.040129 | 0.039613 | 0.039221 | 0.039392 | 0.040075 | 0.040605 | 0.04125 | 0.04187 | 0.042495 | 0.043193 |  | Summer
|  | DB | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | DBMaximum demand forecast(non-peak season)Maximum demand (MVA) | 0.31856 | 0.28717 | 0.28375 | 0.28011 | 0.27733 | 0.27854 | 0.28337 | 0.28712 | 0.29168 | 0.29607 | 0.30049 | 0.30542 |  | Summer
|  | DB | Hours exceeding | 95% of maximum demand | DBHours exceeding95% of maximum demand | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  | DB | Hours exceeding | Firm capacity (continuous rating) | DBHours exceedingFirm capacity (continuous rating) | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760
|  | DB | Hours exceeding | Firm capacity (short-term rating) | DBHours exceedingFirm capacity (short-term rating) | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760
|  | DB | Regional diversity factor | Summer | DBRegional diversity factorSummer | 0.76923 | 0.76923 | 0.76923 | 0.76923 | 0.76923 | 0.76923 | 0.76923 | 0.76923 | 0.76923 | 0.76923 | 0.76923 | 0.76923
|  | DB | Regional diversity factor | Winter | DBRegional diversity factorWinter | 0.71875 | 0.71875 | 0.71875 | 0.71875 | 0.71875 | 0.71875 | 0.71875 | 0.71875 | 0.71875 | 0.71875 | 0.71875 | 0.71875
|  | DB | Load transfer capacity (MVA) | 1 | DBLoad transfer capacity (MVA)1
|  | DB | Load transfer capacity (MVA) | 2 | DBLoad transfer capacity (MVA)2
|  | DB | Load transfer capacity (MVA) | 3 | DBLoad transfer capacity (MVA)3
|  | DB | Load transfer capacity (MVA) | 4 | DBLoad transfer capacity (MVA)4
|  | DB | Load transfer capacity (MVA) | 5 | DBLoad transfer capacity (MVA)5
|  | DB | Embedded generation capacity (MVA) | Units less than 100 kVA | DBEmbedded generation capacity (MVA)Units less than 100 kVA | 0
|  | DB | Embedded generation capacity (MVA) | Units greater than 100 kVA | DBEmbedded generation capacity (MVA)Units greater than 100 kVA | 0
|  | DE | Substation capacity (winter and summer) (MVA) | Total | DESubstation capacity (winter and summer) (MVA)Total | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
|  | DE | Substation capacity (winter and summer) (MVA) | Firm delivery | DESubstation capacity (winter and summer) (MVA)Firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | DE | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | DESubstation capacity (winter and summer) (MVA)Short-term firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | DE | Maximum demand forecast(peak season) | Maximum demand (MW) | DEMaximum demand forecast(peak season)Maximum demand (MW) | 7.9292 | 7.8119 | 7.6317 | 7.4588 | 7.3244 | 7.3998 | 7.476 | 7.5271 | 7.6123 | 7.6899 | 7.7809 | 7.8923
|  | DE | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | DEMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 0.5001 | 0.4927 | 0.48134 | 0.47043 | 0.46195 | 0.46671 | 0.47151 | 0.47473 | 0.48011 | 0.485 | 0.49074 | 0.49777
|  | DE | Maximum demand forecast(peak season) | Maximum demand (MVA) | DEMaximum demand forecast(peak season)Maximum demand (MVA) | 7.9449 | 7.8275 | 7.6469 | 7.4737 | 7.3389 | 7.4145 | 7.4909 | 7.542 | 7.6274 | 7.7051 | 7.7963 | 7.908
|  | DE | Maximum demand forecast(peak season) | Power factor (coincident) | DEMaximum demand forecast(peak season)Power factor (coincident) | 0.99802 | 0.99802 | 0.99802 | 0.99802 | 0.99802 | 0.99802 | 0.99802 | 0.99802 | 0.99802 | 0.99802 | 0.99802 | 0.99802
|  | DE | Maximum demand forecast(non-peak season) | Maximum demand (MW) | DEMaximum demand forecast(non-peak season)Maximum demand (MW) | 6.0029 | 7.0036 | 6.9744 | 6.8194 | 6.7424 | 6.7791 | 6.8636 | 6.9236 | 7.0138 | 7.0676 | 7.2318 | 7.3299 |  | Winter
|  | DE | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | DEMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 0.0082942 | 0.0096769 | 0.0096365 | 0.0094223 | 0.0093159 | 0.0093667 | 0.0094833 | 0.0095662 | 0.0096909 | 0.0097653 | 0.0099921 | 0.010128 |  | Winter
|  | DE | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | DEMaximum demand forecast(non-peak season)Maximum demand (MVA) | 6.0029 | 7.0036 | 6.9744 | 6.8194 | 6.7424 | 6.7791 | 6.8636 | 6.9236 | 7.0138 | 7.0676 | 7.2318 | 7.3299 |  | Winter
|  | DE | Hours exceeding | 95% of maximum demand | DEHours exceeding95% of maximum demand | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
|  | DE | Hours exceeding | Firm capacity (continuous rating) | DEHours exceedingFirm capacity (continuous rating) | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760
|  | DE | Hours exceeding | Firm capacity (short-term rating) | DEHours exceedingFirm capacity (short-term rating) | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760
|  | DE | Regional diversity factor | Summer | DERegional diversity factorSummer | 0.71111 | 0.71111 | 0.71111 | 0.71111 | 0.71111 | 0.71111 | 0.71111 | 0.71111 | 0.71111 | 0.71111 | 0.71111 | 0.71111
|  | DE | Regional diversity factor | Winter | DERegional diversity factorWinter | 0.32805 | 0.32805 | 0.32805 | 0.32805 | 0.32805 | 0.32805 | 0.32805 | 0.32805 | 0.32805 | 0.32805 | 0.32805 | 0.32805
|  | DE | Load transfer capacity (MVA) | 1 | DELoad transfer capacity (MVA)1 | 5.3 | [11 empty] | Scottsdale
|  | DE | Load transfer capacity (MVA) | 2 | DELoad transfer capacity (MVA)2 | 1.6 | [11 empty] | St Marys
|  | DE | Load transfer capacity (MVA) | 3 | DELoad transfer capacity (MVA)3
|  | DE | Load transfer capacity (MVA) | 4 | DELoad transfer capacity (MVA)4
|  | DE | Load transfer capacity (MVA) | 5 | DELoad transfer capacity (MVA)5
|  | DE | Embedded generation capacity (MVA) | Units less than 100 kVA | DEEmbedded generation capacity (MVA)Units less than 100 kVA | 1.3562
|  | DE | Embedded generation capacity (MVA) | Units greater than 100 kVA | DEEmbedded generation capacity (MVA)Units greater than 100 kVA | 2.02
|  | DP | Substation capacity (winter and summer) (MVA) | Total | DPSubstation capacity (winter and summer) (MVA)Total | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110
|  | DP | Substation capacity (winter and summer) (MVA) | Firm delivery | DPSubstation capacity (winter and summer) (MVA)Firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  | DP | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | DPSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72
|  | DP | Maximum demand forecast(peak season) | Maximum demand (MW) | DPMaximum demand forecast(peak season)Maximum demand (MW) | 56.2284 | 52.3995 | 53.5572 | 53.548 | 53.471 | 53.5263 | 54.3196 | 54.9155 | 55.6405 | 56.102 | 57.3802 | 58.0795
|  | DP | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | DPMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 3.7344 | 3.4801 | 3.557 | 3.5564 | 3.5513 | 3.555 | 3.6076 | 3.6472 | 3.6954 | 3.726 | 3.8109 | 3.8574
|  | DP | Maximum demand forecast(peak season) | Maximum demand (MVA) | DPMaximum demand forecast(peak season)Maximum demand (MVA) | 56.3522 | 52.515 | 53.6751 | 53.666 | 53.5888 | 53.6442 | 54.4392 | 55.0365 | 55.7631 | 56.2256 | 57.5066 | 58.2075
|  | DP | Maximum demand forecast(peak season) | Power factor (coincident) | DPMaximum demand forecast(peak season)Power factor (coincident) | 0.9978 | 0.9978 | 0.9978 | 0.9978 | 0.9978 | 0.9978 | 0.9978 | 0.9978 | 0.9978 | 0.9978 | 0.9978 | 0.9978
|  | DP | Maximum demand forecast(non-peak season) | Maximum demand (MW) | DPMaximum demand forecast(non-peak season)Maximum demand (MW) | 39.1338 | 35.708 | 35.6908 | 35.8374 | 35.5571 | 35.5457 | 35.8956 | 36.145 | 36.5098 | 36.8684 | 37.3279 | 37.7604 |  | Summer
|  | DP | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | DPMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 5.1013 | 4.6548 | 4.6525 | 4.6716 | 4.6351 | 4.6336 | 4.6792 | 4.7117 | 4.7593 | 4.806 | 4.8659 | 4.9223 |  | Summer
|  | DP | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | DPMaximum demand forecast(non-peak season)Maximum demand (MVA) | 39.4649 | 36.0101 | 35.9928 | 36.1406 | 35.8579 | 35.8464 | 36.1993 | 36.4508 | 36.8187 | 37.1803 | 37.6438 | 38.0799 |  | Summer
|  | DP | Hours exceeding | 95% of maximum demand | DPHours exceeding95% of maximum demand | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5
|  | DP | Hours exceeding | Firm capacity (continuous rating) | DPHours exceedingFirm capacity (continuous rating)
|  | DP | Hours exceeding | Firm capacity (short-term rating) | DPHours exceedingFirm capacity (short-term rating)
|  | DP | Regional diversity factor | Summer | DPRegional diversity factorSummer | 0.86328 | 0.86328 | 0.86328 | 0.86328 | 0.86328 | 0.86328 | 0.86328 | 0.86328 | 0.86328 | 0.86328 | 0.86328 | 0.86328
|  | DP | Regional diversity factor | Winter | DPRegional diversity factorWinter | 0.95374 | 0.95374 | 0.95374 | 0.95374 | 0.95374 | 0.95374 | 0.95374 | 0.95374 | 0.95374 | 0.95374 | 0.95374 | 0.95374
|  | DP | Load transfer capacity (MVA) | 1 | DPLoad transfer capacity (MVA)1 | 5.1 | [11 empty] | Railton
|  | DP | Load transfer capacity (MVA) | 2 | DPLoad transfer capacity (MVA)2 | 6.3 | [11 empty] | Ulverstone
|  | DP | Load transfer capacity (MVA) | 3 | DPLoad transfer capacity (MVA)3
|  | DP | Load transfer capacity (MVA) | 4 | DPLoad transfer capacity (MVA)4
|  | DP | Load transfer capacity (MVA) | 5 | DPLoad transfer capacity (MVA)5
|  | DP | Embedded generation capacity (MVA) | Units less than 100 kVA | DPEmbedded generation capacity (MVA)Units less than 100 kVA | 11.2123
|  | DP | Embedded generation capacity (MVA) | Units greater than 100 kVA | DPEmbedded generation capacity (MVA)Units greater than 100 kVA | 0.95333
|  | EB | Substation capacity (winter and summer) (MVA) | Total | EBSubstation capacity (winter and summer) (MVA)Total | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76
|  | EB | Substation capacity (winter and summer) (MVA) | Firm delivery | EBSubstation capacity (winter and summer) (MVA)Firm delivery | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38
|  | EB | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | EBSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38
|  | EB | Maximum demand forecast(peak season) | Maximum demand (MW) | EBMaximum demand forecast(peak season)Maximum demand (MW) | 9.1076 | 8.7073 | 8.7104 | 8.6985 | 8.6863 | 8.6344 | 8.7169 | 8.7632 | 8.8379 | 8.8305 | 8.9664 | 8.94
|  | EB | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | EBMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 2.6529 | 2.5363 | 2.5372 | 2.5337 | 2.5302 | 2.5151 | 2.5391 | 2.5526 | 2.5743 | 2.5722 | 2.6118 | 2.6041
|  | EB | Maximum demand forecast(peak season) | Maximum demand (MVA) | EBMaximum demand forecast(peak season)Maximum demand (MVA) | 9.4861 | 9.0691 | 9.0724 | 9.06 | 9.0473 | 8.9932 | 9.0792 | 9.1274 | 9.2052 | 9.1975 | 9.3391 | 9.3116
|  | EB | Maximum demand forecast(peak season) | Power factor (coincident) | EBMaximum demand forecast(peak season)Power factor (coincident) | 0.9601 | 0.9601 | 0.9601 | 0.9601 | 0.9601 | 0.9601 | 0.9601 | 0.9601 | 0.9601 | 0.9601 | 0.9601 | 0.9601
|  | EB | Maximum demand forecast(non-peak season) | Maximum demand (MW) | EBMaximum demand forecast(non-peak season)Maximum demand (MW) | 7.3936 | 7.4866 | 7.343 | 7.3727 | 7.3429 | 7.3261 | 7.3939 | 7.4328 | 7.5005 | 7.5249 | 7.573 | 7.557 |  | Summer
|  | EB | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | EBMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 2.2586 | 2.287 | 2.2431 | 2.2522 | 2.2431 | 2.238 | 2.2587 | 2.2706 | 2.2912 | 2.2987 | 2.3134 | 2.3085 |  | Summer
|  | EB | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | EBMaximum demand forecast(non-peak season)Maximum demand (MVA) | 7.7309 | 7.8282 | 7.678 | 7.709 | 7.6779 | 7.6603 | 7.7312 | 7.7719 | 7.8427 | 7.8681 | 7.9185 | 7.9017 |  | Summer
|  | EB | Hours exceeding | 95% of maximum demand | EBHours exceeding95% of maximum demand | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
|  | EB | Hours exceeding | Firm capacity (continuous rating) | EBHours exceedingFirm capacity (continuous rating)
|  | EB | Hours exceeding | Firm capacity (short-term rating) | EBHours exceedingFirm capacity (short-term rating)
|  | EB | Regional diversity factor | Summer | EBRegional diversity factorSummer | 0.76111 | 0.76111 | 0.76111 | 0.76111 | 0.76111 | 0.76111 | 0.76111 | 0.76111 | 0.76111 | 0.76111 | 0.76111 | 0.76111
|  | EB | Regional diversity factor | Winter | EBRegional diversity factorWinter | 0.8838 | 0.8838 | 0.8838 | 0.8838 | 0.8838 | 0.8838 | 0.8838 | 0.8838 | 0.8838 | 0.8838 | 0.8838 | 0.8838
|  | EB | Load transfer capacity (MVA) | 1 | EBLoad transfer capacity (MVA)1
|  | EB | Load transfer capacity (MVA) | 2 | EBLoad transfer capacity (MVA)2
|  | EB | Load transfer capacity (MVA) | 3 | EBLoad transfer capacity (MVA)3
|  | EB | Load transfer capacity (MVA) | 4 | EBLoad transfer capacity (MVA)4
|  | EB | Load transfer capacity (MVA) | 5 | EBLoad transfer capacity (MVA)5
|  | EB | Embedded generation capacity (MVA) | Units less than 100 kVA | EBEmbedded generation capacity (MVA)Units less than 100 kVA | 0.70338
|  | EB | Embedded generation capacity (MVA) | Units greater than 100 kVA | EBEmbedded generation capacity (MVA)Units greater than 100 kVA | 0
|  | EL | Substation capacity (winter and summer) (MVA) | Total | ELSubstation capacity (winter and summer) (MVA)Total | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
|  | EL | Substation capacity (winter and summer) (MVA) | Firm delivery | ELSubstation capacity (winter and summer) (MVA)Firm delivery | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
|  | EL | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | ELSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
|  | EL | Maximum demand forecast(peak season) | Maximum demand (MW) | ELMaximum demand forecast(peak season)Maximum demand (MW) | 16.0874 | 16.2653 | 16.205 | 15.9122 | 15.7101 | 15.622 | 15.7743 | 15.891 | 16.0744 | 16.2706 | 16.7059 | 17.003
|  | EL | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | ELMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 0.94702 | 0.95749 | 0.95394 | 0.93671 | 0.92481 | 0.91963 | 0.92859 | 0.93546 | 0.94626 | 0.9578 | 0.98343 | 1.0009
|  | EL | Maximum demand forecast(peak season) | Maximum demand (MVA) | ELMaximum demand forecast(peak season)Maximum demand (MVA) | 16.1153 | 16.2935 | 16.2331 | 15.9397 | 15.7373 | 15.6491 | 15.8016 | 15.9185 | 16.1023 | 16.2988 | 16.7348 | 17.0325
|  | EL | Maximum demand forecast(peak season) | Power factor (coincident) | ELMaximum demand forecast(peak season)Power factor (coincident) | 0.99827 | 0.99827 | 0.99827 | 0.99827 | 0.99827 | 0.99827 | 0.99827 | 0.99827 | 0.99827 | 0.99827 | 0.99827 | 0.99827
|  | EL | Maximum demand forecast(non-peak season) | Maximum demand (MW) | ELMaximum demand forecast(non-peak season)Maximum demand (MW) | 9.827 | 10.0548 | 9.7736 | 9.6649 | 9.5295 | 9.5216 | 9.631 | 9.73 | 9.8688 | 10.0693 | 10.3078 | 10.5518 |  | Summer
|  | EL | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | ELMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 0.52975 | 0.54204 | 0.52688 | 0.52102 | 0.51372 | 0.51329 | 0.51919 | 0.52452 | 0.53201 | 0.54282 | 0.55567 | 0.56883 |  | Summer
|  | EL | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | ELMaximum demand forecast(non-peak season)Maximum demand (MVA) | 9.8412 | 10.0694 | 9.7878 | 9.679 | 9.5433 | 9.5355 | 9.645 | 9.7441 | 9.8831 | 10.0839 | 10.3227 | 10.5671 |  | Summer
|  | EL | Hours exceeding | 95% of maximum demand | ELHours exceeding95% of maximum demand | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  | EL | Hours exceeding | Firm capacity (continuous rating) | ELHours exceedingFirm capacity (continuous rating)
|  | EL | Hours exceeding | Firm capacity (short-term rating) | ELHours exceedingFirm capacity (short-term rating)
|  | EL | Regional diversity factor | Summer | ELRegional diversity factorSummer | 0.78257 | 0.78257 | 0.78257 | 0.78257 | 0.78257 | 0.78257 | 0.78257 | 0.78257 | 0.78257 | 0.78257 | 0.78257 | 0.78257
|  | EL | Regional diversity factor | Winter | ELRegional diversity factorWinter | 0.88141 | 0.88141 | 0.88141 | 0.88141 | 0.88141 | 0.88141 | 0.88141 | 0.88141 | 0.88141 | 0.88141 | 0.88141 | 0.88141
|  | EL | Load transfer capacity (MVA) | 1 | ELLoad transfer capacity (MVA)1 | 8 | [11 empty] | Kingston
|  | EL | Load transfer capacity (MVA) | 2 | ELLoad transfer capacity (MVA)2 | 3 | [11 empty] | Knights Road
|  | EL | Load transfer capacity (MVA) | 3 | ELLoad transfer capacity (MVA)3
|  | EL | Load transfer capacity (MVA) | 4 | ELLoad transfer capacity (MVA)4
|  | EL | Load transfer capacity (MVA) | 5 | ELLoad transfer capacity (MVA)5
|  | EL | Embedded generation capacity (MVA) | Units less than 100 kVA | ELEmbedded generation capacity (MVA)Units less than 100 kVA | 8.7161
|  | EL | Embedded generation capacity (MVA) | Units greater than 100 kVA | ELEmbedded generation capacity (MVA)Units greater than 100 kVA | 0.1298
|  | GT | Substation capacity (winter and summer) (MVA) | Total | GTSubstation capacity (winter and summer) (MVA)Total | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96
|  | GT | Substation capacity (winter and summer) (MVA) | Firm delivery | GTSubstation capacity (winter and summer) (MVA)Firm delivery | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
|  | GT | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | GTSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
|  | GT | Maximum demand forecast(peak season) | Maximum demand (MW) | GTMaximum demand forecast(peak season)Maximum demand (MW) | 20.6986 | 19.5394 | 20.2216 | 22.5501 | 23.5938 | 24.2594 | 24.5553 | 24.6574 | 24.849 | 24.936 | 25.4017 | 25.6159
|  | GT | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | GTMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 0.31238 | 0.29489 | 0.30518 | 0.34032 | 0.35608 | 0.36612 | 0.37059 | 0.37213 | 0.37502 | 0.37633 | 0.38336 | 0.38659
|  | GT | Maximum demand forecast(peak season) | Maximum demand (MVA) | GTMaximum demand forecast(peak season)Maximum demand (MVA) | 20.701 | 19.5416 | 20.2239 | 22.5526 | 23.5964 | 24.2622 | 24.5581 | 24.6602 | 24.8518 | 24.9389 | 25.4046 | 25.6188
|  | GT | Maximum demand forecast(peak season) | Power factor (coincident) | GTMaximum demand forecast(peak season)Power factor (coincident) | 0.99989 | 0.99989 | 0.99989 | 0.99989 | 0.99989 | 0.99989 | 0.99989 | 0.99989 | 0.99989 | 0.99989 | 0.99989 | 0.99989
|  | GT | Maximum demand forecast(non-peak season) | Maximum demand (MW) | GTMaximum demand forecast(non-peak season)Maximum demand (MW) | 13.4267 | 12.828 | 13.4576 | 16.1599 | 17.3779 | 18.1518 | 18.5072 | 18.6852 | 18.9243 | 19.1438 | 19.3937 | 19.629 |  | Summer
|  | GT | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | GTMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 1.8356 | 1.7538 | 1.8398 | 2.2093 | 2.3758 | 2.4816 | 2.5302 | 2.5545 | 2.5872 | 2.6172 | 2.6514 | 2.6835 |  | Summer
|  | GT | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | GTMaximum demand forecast(non-peak season)Maximum demand (MVA) | 13.5516 | 12.9473 | 13.5827 | 16.3103 | 17.5396 | 18.3206 | 18.6793 | 18.859 | 19.1004 | 19.3219 | 19.5741 | 19.8116 |  | Summer
|  | GT | Hours exceeding | 95% of maximum demand | GTHours exceeding95% of maximum demand | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
|  | GT | Hours exceeding | Firm capacity (continuous rating) | GTHours exceedingFirm capacity (continuous rating)
|  | GT | Hours exceeding | Firm capacity (short-term rating) | GTHours exceedingFirm capacity (short-term rating)
|  | GT | Regional diversity factor | Summer | GTRegional diversity factorSummer | 0.91086 | 0.91086 | 0.91086 | 0.91086 | 0.91086 | 0.91086 | 0.91086 | 0.91086 | 0.91086 | 0.91086 | 0.91086 | 0.91086
|  | GT | Regional diversity factor | Winter | GTRegional diversity factorWinter | 0.77669 | 0.77669 | 0.77669 | 0.77669 | 0.77669 | 0.77669 | 0.77669 | 0.77669 | 0.77669 | 0.77669 | 0.77669 | 0.77669
|  | GT | Load transfer capacity (MVA) | 1 | GTLoad transfer capacity (MVA)1 | 2.1 | [11 empty] | Mowbray
|  | GT | Load transfer capacity (MVA) | 2 | GTLoad transfer capacity (MVA)2 | 2.1 | [11 empty] | Scottsdale
|  | GT | Load transfer capacity (MVA) | 3 | GTLoad transfer capacity (MVA)3 | 2.1 | [11 empty] | Trevallyn
|  | GT | Load transfer capacity (MVA) | 4 | GTLoad transfer capacity (MVA)4
|  | GT | Load transfer capacity (MVA) | 5 | GTLoad transfer capacity (MVA)5
|  | GT | Embedded generation capacity (MVA) | Units less than 100 kVA | GTEmbedded generation capacity (MVA)Units less than 100 kVA | 7.5015
|  | GT | Embedded generation capacity (MVA) | Units greater than 100 kVA | GTEmbedded generation capacity (MVA)Units greater than 100 kVA | 0.30292
|  | HA | Substation capacity (winter and summer) (MVA) | Total | HASubstation capacity (winter and summer) (MVA)Total | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
|  | HA | Substation capacity (winter and summer) (MVA) | Firm delivery | HASubstation capacity (winter and summer) (MVA)Firm delivery | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
|  | HA | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | HASubstation capacity (winter and summer) (MVA)Short-term firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  | HA | Maximum demand forecast(peak season) | Maximum demand (MW) | HAMaximum demand forecast(peak season)Maximum demand (MW) | 55.8609 | 54.975 | 55.7482 | 53.8243 | 54.2845 | 54.6636 | 55.6489 | 56.3473 | 57.1757 | 57.762 | 59.1153 | 59.977
|  | HA | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | HAMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 0.45114 | 0.44399 | 0.45023 | 0.43469 | 0.43841 | 0.44147 | 0.44943 | 0.45507 | 0.46176 | 0.4665 | 0.47743 | 0.48439
|  | HA | Maximum demand forecast(peak season) | Maximum demand (MVA) | HAMaximum demand forecast(peak season)Maximum demand (MVA) | 55.8628 | 54.9768 | 55.75 | 53.8261 | 54.2863 | 54.6654 | 55.6507 | 56.3492 | 57.1776 | 57.7639 | 59.1172 | 59.979
|  | HA | Maximum demand forecast(peak season) | Power factor (coincident) | HAMaximum demand forecast(peak season)Power factor (coincident) | 0.99997 | 0.99997 | 0.99997 | 0.99997 | 0.99997 | 0.99997 | 0.99997 | 0.99997 | 0.99997 | 0.99997 | 0.99997 | 0.99997
|  | HA | Maximum demand forecast(non-peak season) | Maximum demand (MW) | HAMaximum demand forecast(non-peak season)Maximum demand (MW) | 38.3217 | 40.4237 | 39.6969 | 37.8152 | 37.6279 | 37.599 | 37.8426 | 37.9462 | 38.1938 | 38.5556 | 39.0114 | 39.5861 |  | Summer
|  | HA | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | HAMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 0.02057 | 0.021698 | 0.021308 | 0.020298 | 0.020197 | 0.020182 | 0.020313 | 0.020368 | 0.020501 | 0.020695 | 0.02094 | 0.021248 |  | Summer
|  | HA | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | HAMaximum demand forecast(non-peak season)Maximum demand (MVA) | 38.3217 | 40.4237 | 39.6969 | 37.8152 | 37.6279 | 37.599 | 37.8427 | 37.9462 | 38.1938 | 38.5556 | 39.0114 | 39.5861 |  | Summer
|  | HA | Hours exceeding | 95% of maximum demand | HAHours exceeding95% of maximum demand | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
|  | HA | Hours exceeding | Firm capacity (continuous rating) | HAHours exceedingFirm capacity (continuous rating)
|  | HA | Hours exceeding | Firm capacity (short-term rating) | HAHours exceedingFirm capacity (short-term rating)
|  | HA | Regional diversity factor | Summer | HARegional diversity factorSummer | 0.93747 | 0.93747 | 0.93747 | 0.93747 | 0.93747 | 0.93747 | 0.93747 | 0.93747 | 0.93747 | 0.93747 | 0.93747 | 0.93747
|  | HA | Regional diversity factor | Winter | HARegional diversity factorWinter | 0.93765 | 0.93765 | 0.93765 | 0.93765 | 0.93765 | 0.93765 | 0.93765 | 0.93765 | 0.93765 | 0.93765 | 0.93765 | 0.93765
|  | HA | Load transfer capacity (MVA) | 1 | HALoad transfer capacity (MVA)1 | 13.4 | [11 empty] | Norwood
|  | HA | Load transfer capacity (MVA) | 2 | HALoad transfer capacity (MVA)2 | 5.3 | [11 empty] | Palmerston
|  | HA | Load transfer capacity (MVA) | 3 | HALoad transfer capacity (MVA)3 | 5.3 | [11 empty] | Railton
|  | HA | Load transfer capacity (MVA) | 4 | HALoad transfer capacity (MVA)4 | 26.7 | [11 empty] | Trevallyn
|  | HA | Load transfer capacity (MVA) | 5 | HALoad transfer capacity (MVA)5
|  | HA | Embedded generation capacity (MVA) | Units less than 100 kVA | HAEmbedded generation capacity (MVA)Units less than 100 kVA | 15.1834
|  | HA | Embedded generation capacity (MVA) | Units greater than 100 kVA | HAEmbedded generation capacity (MVA)Units greater than 100 kVA | 1.0487
|  | HR | Substation capacity (winter and summer) (MVA) | Total | HRSubstation capacity (winter and summer) (MVA)Total | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
|  | HR | Substation capacity (winter and summer) (MVA) | Firm delivery | HRSubstation capacity (winter and summer) (MVA)Firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | HR | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | HRSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | HR | Maximum demand forecast(peak season) | Maximum demand (MW) | HRMaximum demand forecast(peak season)Maximum demand (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | HR | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | HRMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 1.7871 | 0.55446 | 0.53171 | 0.5234 | 0.51743 | 0.51561 | 0.52083 | 0.52409 | 0.52919 | 0.53096 | 0.53416 | 0.53275
|  | HR | Maximum demand forecast(peak season) | Maximum demand (MVA) | HRMaximum demand forecast(peak season)Maximum demand (MVA) | 1.7871 | 0.55446 | 0.53171 | 0.5234 | 0.51743 | 0.51561 | 0.52083 | 0.52409 | 0.52919 | 0.53096 | 0.53416 | 0.53275
|  | HR | Maximum demand forecast(peak season) | Power factor (coincident) | HRMaximum demand forecast(peak season)Power factor (coincident) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | HR | Maximum demand forecast(non-peak season) | Maximum demand (MW) | HRMaximum demand forecast(non-peak season)Maximum demand (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Winter
|  | HR | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | HRMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 0.81762 | 0.92276 | 0.9037 | 0.88566 | 0.87757 | 0.87019 | 0.87801 | 0.88234 | 0.88926 | 0.8876 | 0.90014 | 0.89621 |  | Winter
|  | HR | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | HRMaximum demand forecast(non-peak season)Maximum demand (MVA) | 0.81762 | 0.92276 | 0.9037 | 0.88566 | 0.87757 | 0.87019 | 0.87801 | 0.88234 | 0.88926 | 0.8876 | 0.90014 | 0.89621 |  | Winter
|  | HR | Hours exceeding | 95% of maximum demand | HRHours exceeding95% of maximum demand | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  | HR | Hours exceeding | Firm capacity (continuous rating) | HRHours exceedingFirm capacity (continuous rating) | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760
|  | HR | Hours exceeding | Firm capacity (short-term rating) | HRHours exceedingFirm capacity (short-term rating) | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760
|  | HR | Regional diversity factor | Summer | HRRegional diversity factorSummer | 0.83333 | 0.83333 | 0.83333 | 0.83333 | 0.83333 | 0.83333 | 0.83333 | 0.83333 | 0.83333 | 0.83333 | 0.83333 | 0.83333
|  | HR | Regional diversity factor | Winter | HRRegional diversity factorWinter | 0.81818 | 0.81818 | 0.81818 | 0.81818 | 0.81818 | 0.81818 | 0.81818 | 0.81818 | 0.81818 | 0.81818 | 0.81818 | 0.81818
|  | HR | Load transfer capacity (MVA) | 1 | HRLoad transfer capacity (MVA)1
|  | HR | Load transfer capacity (MVA) | 2 | HRLoad transfer capacity (MVA)2
|  | HR | Load transfer capacity (MVA) | 3 | HRLoad transfer capacity (MVA)3
|  | HR | Load transfer capacity (MVA) | 4 | HRLoad transfer capacity (MVA)4
|  | HR | Load transfer capacity (MVA) | 5 | HRLoad transfer capacity (MVA)5
|  | HR | Embedded generation capacity (MVA) | Units less than 100 kVA | HREmbedded generation capacity (MVA)Units less than 100 kVA | 0.01525
|  | HR | Embedded generation capacity (MVA) | Units greater than 100 kVA | HREmbedded generation capacity (MVA)Units greater than 100 kVA | 0
|  | KE | Substation capacity (winter and summer) (MVA) | Total | KESubstation capacity (winter and summer) (MVA)Total | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
|  | KE | Substation capacity (winter and summer) (MVA) | Firm delivery | KESubstation capacity (winter and summer) (MVA)Firm delivery | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
|  | KE | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | KESubstation capacity (winter and summer) (MVA)Short-term firm delivery | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
|  | KE | Maximum demand forecast(peak season) | Maximum demand (MW) | KEMaximum demand forecast(peak season)Maximum demand (MW) | 8.3881 | 8.6287 | 8.7233 | 8.5636 | 8.4966 | 8.4852 | 8.6235 | 8.7235 | 8.8508 | 8.9483 | 9.1695 | 9.3321
|  | KE | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | KEMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 0.97992 | 1.008 | 1.0191 | 1.0004 | 0.9926 | 0.99127 | 1.0074 | 1.0191 | 1.034 | 1.0454 | 1.0712 | 1.0902
|  | KE | Maximum demand forecast(peak season) | Maximum demand (MVA) | KEMaximum demand forecast(peak season)Maximum demand (MVA) | 8.4451 | 8.6874 | 8.7826 | 8.6219 | 8.5544 | 8.5429 | 8.6822 | 8.7829 | 8.911 | 9.0092 | 9.2319 | 9.3955
|  | KE | Maximum demand forecast(peak season) | Power factor (coincident) | KEMaximum demand forecast(peak season)Power factor (coincident) | 0.99325 | 0.99325 | 0.99325 | 0.99325 | 0.99325 | 0.99325 | 0.99325 | 0.99325 | 0.99325 | 0.99325 | 0.99325 | 0.99325
|  | KE | Maximum demand forecast(non-peak season) | Maximum demand (MW) | KEMaximum demand forecast(non-peak season)Maximum demand (MW) | 6.3527 | 6.2073 | 6.062 | 5.929 | 5.8286 | 5.8061 | 5.8696 | 5.9113 | 5.975 | 6.0367 | 6.1108 | 6.191 |  | Summer
|  | KE | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | KEMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 0.73551 | 0.71868 | 0.70186 | 0.68646 | 0.67484 | 0.67223 | 0.67958 | 0.68441 | 0.69178 | 0.69893 | 0.70751 | 0.71679 |  | Summer
|  | KE | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | KEMaximum demand forecast(non-peak season)Maximum demand (MVA) | 6.3951 | 6.2488 | 6.1025 | 5.9686 | 5.8676 | 5.8449 | 5.9088 | 5.9508 | 6.0149 | 6.077 | 6.1516 | 6.2323 |  | Summer
|  | KE | Hours exceeding | 95% of maximum demand | KEHours exceeding95% of maximum demand | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  | KE | Hours exceeding | Firm capacity (continuous rating) | KEHours exceedingFirm capacity (continuous rating)
|  | KE | Hours exceeding | Firm capacity (short-term rating) | KEHours exceedingFirm capacity (short-term rating)
|  | KE | Regional diversity factor | Summer | KERegional diversity factorSummer | 0.86854 | 0.86854 | 0.86854 | 0.86854 | 0.86854 | 0.86854 | 0.86854 | 0.86854 | 0.86854 | 0.86854 | 0.86854 | 0.86854
|  | KE | Regional diversity factor | Winter | KERegional diversity factorWinter | 0.91347 | 0.91347 | 0.91347 | 0.91347 | 0.91347 | 0.91347 | 0.91347 | 0.91347 | 0.91347 | 0.91347 | 0.91347 | 0.91347
|  | KE | Load transfer capacity (MVA) | 1 | KELoad transfer capacity (MVA)1 | 4.4 | [11 empty] | Knights Road
|  | KE | Load transfer capacity (MVA) | 2 | KELoad transfer capacity (MVA)2
|  | KE | Load transfer capacity (MVA) | 3 | KELoad transfer capacity (MVA)3
|  | KE | Load transfer capacity (MVA) | 4 | KELoad transfer capacity (MVA)4
|  | KE | Load transfer capacity (MVA) | 5 | KELoad transfer capacity (MVA)5
|  | KE | Embedded generation capacity (MVA) | Units less than 100 kVA | KEEmbedded generation capacity (MVA)Units less than 100 kVA | 3.2869
|  | KE | Embedded generation capacity (MVA) | Units greater than 100 kVA | KEEmbedded generation capacity (MVA)Units greater than 100 kVA | 0
|  | KI11 | Substation capacity (winter and summer) (MVA) | Total | KI11Substation capacity (winter and summer) (MVA)Total | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
|  | KI11 | Substation capacity (winter and summer) (MVA) | Firm delivery | KI11Substation capacity (winter and summer) (MVA)Firm delivery | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
|  | KI11 | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | KI11Substation capacity (winter and summer) (MVA)Short-term firm delivery | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42
|  | KI11 | Maximum demand forecast(peak season) | Maximum demand (MW) | KI11Maximum demand forecast(peak season)Maximum demand (MW) | 27.7733 | 27.5402 | 27.7016 | 27.1939 | 26.8776 | 26.8272 | 27.2101 | 27.5601 | 28.0308 | 28.5199 | 29.4314 | 30.1038
|  | KI11 | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | KI11Maximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 0.034332 | 0.034044 | 0.034244 | 0.033616 | 0.033225 | 0.033163 | 0.033636 | 0.034069 | 0.034651 | 0.035255 | 0.036382 | 0.037213
|  | KI11 | Maximum demand forecast(peak season) | Maximum demand (MVA) | KI11Maximum demand forecast(peak season)Maximum demand (MVA) | 27.7733 | 27.5402 | 27.7016 | 27.1939 | 26.8776 | 26.8273 | 27.2102 | 27.5601 | 28.0309 | 28.52 | 29.4314 | 30.1039
|  | KI11 | Maximum demand forecast(peak season) | Power factor (coincident) | KI11Maximum demand forecast(peak season)Power factor (coincident) | 1 | 1 | bar: 4 2023 to 13 2032
|  | KI11 | Maximum demand forecast(non-peak season) | Maximum demand (MW) | KI11Maximum demand forecast(non-peak season)Maximum demand (MW) | 15.486 | 16.2295 | 15.7254 | 15.2091 | 14.7246 | 14.5178 | 14.514 | 14.5171 | 14.5859 | 14.7543 | 14.9788 | 15.2196 |  | Summer
|  | KI11 | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | KI11Maximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 0.26303 | 0.27566 | 0.2671 | 0.25833 | 0.2501 | 0.24659 | 0.24652 | 0.24658 | 0.24774 | 0.2506 | 0.25442 | 0.25851 |  | Summer
|  | KI11 | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | KI11Maximum demand forecast(non-peak season)Maximum demand (MVA) | 15.4883 | 16.2318 | 15.7276 | 15.2113 | 14.7267 | 14.5198 | 14.5161 | 14.5192 | 14.588 | 14.7564 | 14.981 | 15.2218 |  | Summer
|  | KI11 | Hours exceeding | 95% of maximum demand | KI11Hours exceeding95% of maximum demand | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  | KI11 | Hours exceeding | Firm capacity (continuous rating) | KI11Hours exceedingFirm capacity (continuous rating)
|  | KI11 | Hours exceeding | Firm capacity (short-term rating) | KI11Hours exceedingFirm capacity (short-term rating)
|  | KI11 | Regional diversity factor | Summer | KI11Regional diversity factorSummer | 0.7452 | 0.7452 | 0.7452 | 0.7452 | 0.7452 | 0.7452 | 0.7452 | 0.7452 | 0.7452 | 0.7452 | 0.7452 | 0.7452
|  | KI11 | Regional diversity factor | Winter | KI11Regional diversity factorWinter | 0.9059 | 0.9059 | 0.9059 | 0.9059 | 0.9059 | 0.9059 | 0.9059 | 0.9059 | 0.9059 | 0.9059 | 0.9059 | 0.9059
|  | KI11 | Load transfer capacity (MVA) | 1 | KI11Load transfer capacity (MVA)1 | 7.8 | [11 empty] | Electrona
|  | KI11 | Load transfer capacity (MVA) | 2 | KI11Load transfer capacity (MVA)2 | 3.1 | [11 empty] | Knights Road
|  | KI11 | Load transfer capacity (MVA) | 3 | KI11Load transfer capacity (MVA)3 | 1.6 | [11 empty] | Sandy Bay
|  | KI11 | Load transfer capacity (MVA) | 4 | KI11Load transfer capacity (MVA)4
|  | KI11 | Load transfer capacity (MVA) | 5 | KI11Load transfer capacity (MVA)5
|  | KI11 | Embedded generation capacity (MVA) | Units less than 100 kVA | KI11Embedded generation capacity (MVA)Units less than 100 kVA | 9.0801
|  | KI11 | Embedded generation capacity (MVA) | Units greater than 100 kVA | KI11Embedded generation capacity (MVA)Units greater than 100 kVA | 0.30004
|  | KI33 | Substation capacity (winter and summer) (MVA) | Total | KI33Substation capacity (winter and summer) (MVA)Total | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
|  | KI33 | Substation capacity (winter and summer) (MVA) | Firm delivery | KI33Substation capacity (winter and summer) (MVA)Firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  | KI33 | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | KI33Substation capacity (winter and summer) (MVA)Short-term firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  | KI33 | Maximum demand forecast(peak season) | Maximum demand (MW) | KI33Maximum demand forecast(peak season)Maximum demand (MW) | 11.1446 | 11.0767 | 11.192 | 11.23 | 11.3152 | 11.5035 | 11.889 | 12.2878 | 12.796 | 13.3828 | 14.1814 | 14.907
|  | KI33 | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | KI33Maximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 1.0549 | 1.0485 | 1.0594 | 1.063 | 1.0711 | 1.0889 | 1.1254 | 1.1631 | 1.2112 | 1.2668 | 1.3424 | 1.411
|  | KI33 | Maximum demand forecast(peak season) | Maximum demand (MVA) | KI33Maximum demand forecast(peak season)Maximum demand (MVA) | 11.1944 | 11.1262 | 11.242 | 11.2802 | 11.3657 | 11.5549 | 11.9422 | 12.3427 | 12.8532 | 13.4427 | 14.2447 | 14.9736
|  | KI33 | Maximum demand forecast(peak season) | Power factor (coincident) | KI33Maximum demand forecast(peak season)Power factor (coincident) | 0.99555 | 0.99555 | 0.99555 | 0.99555 | 0.99555 | 0.99555 | 0.99555 | 0.99555 | 0.99555 | 0.99555 | 0.99555 | 0.99555
|  | KI33 | Maximum demand forecast(non-peak season) | Maximum demand (MW) | KI33Maximum demand forecast(non-peak season)Maximum demand (MW) | 5.954 | 5.6698 | 5.6142 | 5.7398 | 5.8111 | 5.9629 | 6.1894 | 6.4334 | 6.7152 | 7.097 | 7.5233 | 7.9874 |  | Summer
|  | KI33 | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | KI33Maximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 0.079941 | 0.076126 | 0.075379 | 0.077065 | 0.078022 | 0.080061 | 0.083102 | 0.086378 | 0.090161 | 0.095288 | 0.10101 | 0.10724 |  | Summer
|  | KI33 | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 5.9545 | 5.6704 | 5.6147 | 5.7403 | 5.8116 | 5.9635 | 6.19 | 6.434 | 6.7158 | 7.0977 | 7.524 | 7.9881 |  | Summer
|  | KI33 | Hours exceeding | 95% of maximum demand | KI33Hours exceeding95% of maximum demand | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  | KI33 | Hours exceeding | Firm capacity (continuous rating) | KI33Hours exceedingFirm capacity (continuous rating)
|  | KI33 | Hours exceeding | Firm capacity (short-term rating) | KI33Hours exceedingFirm capacity (short-term rating)
|  | KI33 | Regional diversity factor | Summer | KI33Regional diversity factorSummer | 0.85913 | 0.85913 | 0.85913 | 0.85913 | 0.85913 | 0.85913 | 0.85913 | 0.85913 | 0.85913 | 0.85913 | 0.85913 | 0.85913
|  | KI33 | Regional diversity factor | Winter | KI33Regional diversity factorWinter | 0.94338 | 0.94338 | 0.94338 | 0.94338 | 0.94338 | 0.94338 | 0.94338 | 0.94338 | 0.94338 | 0.94338 | 0.94338 | 0.94338
|  | KI33 | Load transfer capacity (MVA) | 1 | KI33Load transfer capacity (MVA)1
|  | KI33 | Load transfer capacity (MVA) | 2 | KI33Load transfer capacity (MVA)2
|  | KI33 | Load transfer capacity (MVA) | 3 | KI33Load transfer capacity (MVA)3
|  | KI33 | Load transfer capacity (MVA) | 4 | KI33Load transfer capacity (MVA)4
|  | KI33 | Load transfer capacity (MVA) | 5 | KI33Load transfer capacity (MVA)5
|  | KI33 | Embedded generation capacity (MVA) | Units less than 100 kVA | KI33Embedded generation capacity (MVA)Units less than 100 kVA | 2.8651
|  | KI33 | Embedded generation capacity (MVA) | Units greater than 100 kVA | KI33Embedded generation capacity (MVA)Units greater than 100 kVA | 0
|  | KR | Substation capacity (winter and summer) (MVA) | Total | KRSubstation capacity (winter and summer) (MVA)Total | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 50 | 50 | 50 | 50 | 50
|  | KR | Substation capacity (winter and summer) (MVA) | Firm delivery | KRSubstation capacity (winter and summer) (MVA)Firm delivery | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 25 | 25 | 25 | 25 | 25
|  | KR | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | KRSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 30 | 30 | 30 | 30 | 30
|  | KR | Maximum demand forecast(peak season) | Maximum demand (MW) | KRMaximum demand forecast(peak season)Maximum demand (MW) | 19.0644 | 19.9061 | 19.6465 | 19.328 | 19.1615 | 19.0795 | 19.2814 | 19.3797 | 19.526 | 19.6082 | 19.9347 | 20.177
|  | KR | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | KRMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 2.3313 | 2.4343 | 2.4025 | 2.3636 | 2.3432 | 2.3332 | 2.3579 | 2.3699 | 2.3878 | 2.3978 | 2.4378 | 2.4674
|  | KR | Maximum demand forecast(peak season) | Maximum demand (MVA) | KRMaximum demand forecast(peak season)Maximum demand (MVA) | 19.2064 | 20.0543 | 19.7929 | 19.472 | 19.3043 | 19.2216 | 19.425 | 19.524 | 19.6715 | 19.7543 | 20.0832 | 20.3273
|  | KR | Maximum demand forecast(peak season) | Power factor (coincident) | KRMaximum demand forecast(peak season)Power factor (coincident) | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261 | 0.99261
|  | KR | Maximum demand forecast(non-peak season) | Maximum demand (MW) | KRMaximum demand forecast(non-peak season)Maximum demand (MW) | 15.585 | 14.8484 | 14.2654 | 14.259 | 14.2234 | 14.2921 | 14.5084 | 14.6466 | 14.8253 | 14.9828 | 15.1434 | 15.3317 |  | Summer
|  | KR | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | KRMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 2.5475 | 2.4271 | 2.3318 | 2.3307 | 2.3249 | 2.3361 | 2.3715 | 2.3941 | 2.4233 | 2.4491 | 2.4753 | 2.5061 |  | Summer
|  | KR | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 15.7919 | 15.0454 | 14.4547 | 14.4482 | 14.4122 | 14.4818 | 14.7009 | 14.841 | 15.0221 | 15.1817 | 15.3444 | 15.5351 |  | Summer
|  | KR | Hours exceeding | 95% of maximum demand | KRHours exceeding95% of maximum demand | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
|  | KR | Hours exceeding | Firm capacity (continuous rating) | KRHours exceedingFirm capacity (continuous rating)
|  | KR | Hours exceeding | Firm capacity (short-term rating) | KRHours exceedingFirm capacity (short-term rating)
|  | KR | Regional diversity factor | Summer | KRRegional diversity factorSummer | 0.90798 | 0.90798 | 0.90798 | 0.90798 | 0.90798 | 0.90798 | 0.90798 | 0.90798 | 0.90798 | 0.90798 | 0.90798 | 0.90798
|  | KR | Regional diversity factor | Winter | KRRegional diversity factorWinter | 0.96199 | 0.96199 | 0.96199 | 0.96199 | 0.96199 | 0.96199 | 0.96199 | 0.96199 | 0.96199 | 0.96199 | 0.96199 | 0.96199
|  | KR | Load transfer capacity (MVA) | 1 | KRLoad transfer capacity (MVA)1 | 1.7 | [11 empty] | Electrona
|  | KR | Load transfer capacity (MVA) | 2 | KRLoad transfer capacity (MVA)2 | 3.4 | [11 empty] | Kermandie
|  | KR | Load transfer capacity (MVA) | 3 | KRLoad transfer capacity (MVA)3 | 1.7 | [11 empty] | Kingston
|  | KR | Load transfer capacity (MVA) | 4 | KRLoad transfer capacity (MVA)4
|  | KR | Load transfer capacity (MVA) | 5 | KRLoad transfer capacity (MVA)5
|  | KR | Embedded generation capacity (MVA) | Units less than 100 kVA | KREmbedded generation capacity (MVA)Units less than 100 kVA | 6.9122
|  | KR | Embedded generation capacity (MVA) | Units greater than 100 kVA | KREmbedded generation capacity (MVA)Units greater than 100 kVA | 0.1992
|  | LF | Substation capacity (winter and summer) (MVA) | Total | LFSubstation capacity (winter and summer) (MVA)Total | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
|  | LF | Substation capacity (winter and summer) (MVA) | Firm delivery | LFSubstation capacity (winter and summer) (MVA)Firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  | LF | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | LFSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 54 | 54 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72
|  | LF | Maximum demand forecast(peak season) | Maximum demand (MW) | LFMaximum demand forecast(peak season)Maximum demand (MW) | 36.5134 | 35.7283 | 35.974 | 35.303 | 34.9219 | 34.8967 | 35.3879 | 35.7788 | 36.2444 | 36.649 | 37.5155 | 38.1068
|  | LF | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | LFMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 1.5225 | 1.4898 | 1.5 | 1.4721 | 1.4562 | 1.4551 | 1.4756 | 1.4919 | 1.5113 | 1.5282 | 1.5643 | 1.589
|  | LF | Maximum demand forecast(peak season) | Maximum demand (MVA) | LFMaximum demand forecast(peak season)Maximum demand (MVA) | 36.5452 | 35.7593 | 36.0053 | 35.3337 | 34.9522 | 34.9271 | 35.4186 | 35.8099 | 36.2759 | 36.6808 | 37.5481 | 38.14
|  | LF | Maximum demand forecast(peak season) | Power factor (coincident) | LFMaximum demand forecast(peak season)Power factor (coincident) | 0.99913 | 0.99913 | 0.99913 | 0.99913 | 0.99913 | 0.99913 | 0.99913 | 0.99913 | 0.99913 | 0.99913 | 0.99913 | 0.99913
|  | LF | Maximum demand forecast(non-peak season) | Maximum demand (MW) | LFMaximum demand forecast(non-peak season)Maximum demand (MW) | 22.4503 | 20.1015 | 19.5627 | 18.9822 | 18.4995 | 18.3929 | 18.5206 | 18.632 | 18.8023 | 19.0786 | 19.3803 | 19.7567 |  | Summer
|  | LF | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | LFMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 0.31358 | 0.28077 | 0.27325 | 0.26514 | 0.2584 | 0.25691 | 0.25869 | 0.26025 | 0.26262 | 0.26648 | 0.2707 | 0.27595 |  | Summer
|  | LF | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 22.4525 | 20.1035 | 19.5646 | 18.984 | 18.5013 | 18.3947 | 18.5224 | 18.6338 | 18.8042 | 19.0804 | 19.3822 | 19.7586 |  | Summer
|  | LF | Hours exceeding | 95% of maximum demand | LFHours exceeding95% of maximum demand | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  | LF | Hours exceeding | Firm capacity (continuous rating) | LFHours exceedingFirm capacity (continuous rating)
|  | LF | Hours exceeding | Firm capacity (short-term rating) | LFHours exceedingFirm capacity (short-term rating)
|  | LF | Regional diversity factor | Summer | LFRegional diversity factorSummer | 0.81658 | 0.81658 | 0.81658 | 0.81658 | 0.81658 | 0.81658 | 0.81658 | 0.81658 | 0.81658 | 0.81658 | 0.81658 | 0.81658
|  | LF | Regional diversity factor | Winter | LFRegional diversity factorWinter | 0.92622 | 0.92622 | 0.92622 | 0.92622 | 0.92622 | 0.92622 | 0.92622 | 0.92622 | 0.92622 | 0.92622 | 0.92622 | 0.92622
|  | LF | Load transfer capacity (MVA) | 1 | LFLoad transfer capacity (MVA)1
|  | LF | Load transfer capacity (MVA) | 2 | LFLoad transfer capacity (MVA)2
|  | LF | Load transfer capacity (MVA) | 3 | LFLoad transfer capacity (MVA)3
|  | LF | Load transfer capacity (MVA) | 4 | LFLoad transfer capacity (MVA)4
|  | LF | Load transfer capacity (MVA) | 5 | LFLoad transfer capacity (MVA)5
|  | LF | Embedded generation capacity (MVA) | Units less than 100 kVA | LFEmbedded generation capacity (MVA)Units less than 100 kVA | 5.6014
|  | LF | Embedded generation capacity (MVA) | Units greater than 100 kVA | LFEmbedded generation capacity (MVA)Units greater than 100 kVA | 0
|  | MB | Substation capacity (winter and summer) (MVA) | Total | MBSubstation capacity (winter and summer) (MVA)Total | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
|  | MB | Substation capacity (winter and summer) (MVA) | Firm delivery | MBSubstation capacity (winter and summer) (MVA)Firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | MB | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | MBSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | MB | Maximum demand forecast(peak season) | Maximum demand (MW) | MBMaximum demand forecast(peak season)Maximum demand (MW) | 7.652 | 8.2384 | 8.0857 | 7.9917 | 7.9221 | 7.9558 | 8.0918 | 8.1988 | 8.3305 | 8.4494 | 8.577 | 8.698
|  | MB | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | MBMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 0.97178 | 1.0462 | 1.0269 | 1.0149 | 1.0061 | 1.0104 | 1.0276 | 1.0412 | 1.0579 | 1.073 | 1.0893 | 1.1046
|  | MB | Maximum demand forecast(peak season) | Maximum demand (MVA) | MBMaximum demand forecast(peak season)Maximum demand (MVA) | 7.7135 | 8.3046 | 8.1507 | 8.0559 | 7.9858 | 8.0197 | 8.1568 | 8.2646 | 8.3974 | 8.5172 | 8.6459 | 8.7678
|  | MB | Maximum demand forecast(peak season) | Power factor (coincident) | MBMaximum demand forecast(peak season)Power factor (coincident) | 0.99203 | 0.99203 | 0.99203 | 0.99203 | 0.99203 | 0.99203 | 0.99203 | 0.99203 | 0.99203 | 0.99203 | 0.99203 | 0.99203
|  | MB | Maximum demand forecast(non-peak season) | Maximum demand (MW) | MBMaximum demand forecast(non-peak season)Maximum demand (MW) | 4.6448 | 4.6221 | 4.6197 | 4.5333 | 4.494 | 4.4849 | 4.554 | 4.609 | 4.681 | 4.7375 | 4.8654 | 4.9479 |  | Winter
|  | MB | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | MBMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 0.023545 | 0.02343 | 0.023418 | 0.02298 | 0.022781 | 0.022735 | 0.023085 | 0.023364 | 0.023729 | 0.024015 | 0.024664 | 0.025082 |  | Winter
|  | MB | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 4.6448 | 4.6221 | 4.6198 | 4.5333 | 4.494 | 4.4849 | 4.5541 | 4.6091 | 4.6811 | 4.7376 | 4.8655 | 4.9479 |  | Winter
|  | MB | Hours exceeding | 95% of maximum demand | MBHours exceeding95% of maximum demand | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5
|  | MB | Hours exceeding | Firm capacity (continuous rating) | MBHours exceedingFirm capacity (continuous rating) | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760
|  | MB | Hours exceeding | Firm capacity (short-term rating) | MBHours exceedingFirm capacity (short-term rating) | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760
|  | MB | Regional diversity factor | Summer | MBRegional diversity factorSummer | 0.71486 | 0.71486 | 0.71486 | 0.71486 | 0.71486 | 0.71486 | 0.71486 | 0.71486 | 0.71486 | 0.71486 | 0.71486 | 0.71486
|  | MB | Regional diversity factor | Winter | MBRegional diversity factorWinter | 0.69937 | 0.69937 | 0.69937 | 0.69937 | 0.69937 | 0.69937 | 0.69937 | 0.69937 | 0.69937 | 0.69937 | 0.69937 | 0.69937
|  | MB | Load transfer capacity (MVA) | 1 | MBLoad transfer capacity (MVA)1 | 2.3 | [11 empty] | New Norfolk
|  | MB | Load transfer capacity (MVA) | 2 | MBLoad transfer capacity (MVA)2 | 1.3 | [11 empty] | Wayatinah
|  | MB | Load transfer capacity (MVA) | 3 | MBLoad transfer capacity (MVA)3 | 1.8 | [11 empty] | Sorell
|  | MB | Load transfer capacity (MVA) | 4 | MBLoad transfer capacity (MVA)4
|  | MB | Load transfer capacity (MVA) | 5 | MBLoad transfer capacity (MVA)5
|  | MB | Embedded generation capacity (MVA) | Units less than 100 kVA | MBEmbedded generation capacity (MVA)Units less than 100 kVA | 0.91829
|  | MB | Embedded generation capacity (MVA) | Units greater than 100 kVA | MBEmbedded generation capacity (MVA)Units greater than 100 kVA | 0.2
|  | MT | Substation capacity (winter and summer) (MVA) | Total | MTSubstation capacity (winter and summer) (MVA)Total | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
|  | MT | Substation capacity (winter and summer) (MVA) | Firm delivery | MTSubstation capacity (winter and summer) (MVA)Firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  | MT | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | MTSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72
|  | MT | Maximum demand forecast(peak season) | Maximum demand (MW) | MTMaximum demand forecast(peak season)Maximum demand (MW) | 38.0185 | 38.6717 | 38.8779 | 38.1707 | 37.7679 | 37.7716 | 38.3529 | 38.8598 | 39.4836 | 40.0818 | 41.2171 | 42.048
|  | MT | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | MTMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 2.6269 | 2.672 | 2.6863 | 2.6374 | 2.6096 | 2.6098 | 2.65 | 2.685 | 2.7281 | 2.7694 | 2.8479 | 2.9053
|  | MT | Maximum demand forecast(peak season) | Maximum demand (MVA) | MTMaximum demand forecast(peak season)Maximum demand (MVA) | 38.1091 | 38.7639 | 38.9706 | 38.2617 | 37.8579 | 37.8616 | 38.4444 | 38.9525 | 39.5777 | 40.1773 | 41.3154 | 42.1482
|  | MT | Maximum demand forecast(peak season) | Power factor (coincident) | MTMaximum demand forecast(peak season)Power factor (coincident) | 0.99762 | 0.99762 | 0.99762 | 0.99762 | 0.99762 | 0.99762 | 0.99762 | 0.99762 | 0.99762 | 0.99762 | 0.99762 | 0.99762
|  | MT | Maximum demand forecast(non-peak season) | Maximum demand (MW) | MTMaximum demand forecast(non-peak season)Maximum demand (MW) | 22.9463 | 22.6032 | 21.8295 | 21.0963 | 20.5073 | 20.3485 | 20.4722 | 20.6061 | 20.8256 | 21.1964 | 21.6292 | 22.1345 |  | Summer
|  | MT | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | MTMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 1.1363 | 1.1193 | 1.081 | 1.0446 | 1.0155 | 1.0076 | 1.0137 | 1.0204 | 1.0312 | 1.0496 | 1.071 | 1.0961 |  | Summer
|  | MT | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 22.9744 | 22.6309 | 21.8563 | 21.1222 | 20.5324 | 20.3735 | 20.4973 | 20.6313 | 20.8511 | 21.2223 | 21.6557 | 22.1616 |  | Summer
|  | MT | Hours exceeding | 95% of maximum demand | MTHours exceeding95% of maximum demand | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  | MT | Hours exceeding | Firm capacity (continuous rating) | MTHours exceedingFirm capacity (continuous rating)
|  | MT | Hours exceeding | Firm capacity (short-term rating) | MTHours exceedingFirm capacity (short-term rating)
|  | MT | Regional diversity factor | Summer | MTRegional diversity factorSummer | 0.82309 | 0.82309 | 0.82309 | 0.82309 | 0.82309 | 0.82309 | 0.82309 | 0.82309 | 0.82309 | 0.82309 | 0.82309 | 0.82309
|  | MT | Regional diversity factor | Winter | MTRegional diversity factorWinter | 0.94757 | 0.94757 | 0.94757 | 0.94757 | 0.94757 | 0.94757 | 0.94757 | 0.94757 | 0.94757 | 0.94757 | 0.94757 | 0.94757
|  | MT | Load transfer capacity (MVA) | 1 | MTLoad transfer capacity (MVA)1
|  | MT | Load transfer capacity (MVA) | 2 | MTLoad transfer capacity (MVA)2
|  | MT | Load transfer capacity (MVA) | 3 | MTLoad transfer capacity (MVA)3
|  | MT | Load transfer capacity (MVA) | 4 | MTLoad transfer capacity (MVA)4
|  | MT | Load transfer capacity (MVA) | 5 | MTLoad transfer capacity (MVA)5
|  | MT | Embedded generation capacity (MVA) | Units less than 100 kVA | MTEmbedded generation capacity (MVA)Units less than 100 kVA | 11.4925
|  | MT | Embedded generation capacity (MVA) | Units greater than 100 kVA | MTEmbedded generation capacity (MVA)Units greater than 100 kVA | 0
|  | MY | Substation capacity (winter and summer) (MVA) | Total | MYSubstation capacity (winter and summer) (MVA)Total | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
|  | MY | Substation capacity (winter and summer) (MVA) | Firm delivery | MYSubstation capacity (winter and summer) (MVA)Firm delivery | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
|  | MY | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | MYSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  | MY | Maximum demand forecast(peak season) | Maximum demand (MW) | MYMaximum demand forecast(peak season)Maximum demand (MW) | 39.6303 | 38.6721 | 38.6564 | 38.272 | 37.9543 | 37.7915 | 38.1629 | 38.4204 | 38.7705 | 38.9732 | 39.7162 | 40.0682
|  | MY | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | MYMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 1.9921 | 1.9439 | 1.9431 | 1.9238 | 1.9078 | 1.8997 | 1.9183 | 1.9313 | 1.9489 | 1.9591 | 1.9964 | 2.0141
|  | MY | Maximum demand forecast(peak season) | Maximum demand (MVA) | MYMaximum demand forecast(peak season)Maximum demand (MVA) | 39.6803 | 38.721 | 38.7052 | 38.3203 | 38.0022 | 37.8392 | 38.2111 | 38.4689 | 38.8195 | 39.0224 | 39.7663 | 40.1188
|  | MY | Maximum demand forecast(peak season) | Power factor (coincident) | MYMaximum demand forecast(peak season)Power factor (coincident) | 0.99874 | 0.99874 | 0.99874 | 0.99874 | 0.99874 | 0.99874 | 0.99874 | 0.99874 | 0.99874 | 0.99874 | 0.99874 | 0.99874
|  | MY | Maximum demand forecast(non-peak season) | Maximum demand (MW) | MYMaximum demand forecast(non-peak season)Maximum demand (MW) | 23.0841 | 22.3596 | 21.8795 | 21.8195 | 21.5336 | 21.4476 | 21.5756 | 21.6511 | 21.7926 | 21.9479 | 22.1325 | 22.3152 |  | Summer
|  | MY | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | MYMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 1.4913 | 1.4445 | 1.4135 | 1.4096 | 1.3911 | 1.3856 | 1.3938 | 1.3987 | 1.4078 | 1.4179 | 1.4298 | 1.4416 |  | Summer
|  | MY | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 23.1322 | 22.4062 | 21.9251 | 21.8649 | 21.5785 | 21.4923 | 21.6206 | 21.6962 | 21.838 | 21.9937 | 22.1786 | 22.3617 |  | Summer
|  | MY | Hours exceeding | 95% of maximum demand | MYHours exceeding95% of maximum demand | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
|  | MY | Hours exceeding | Firm capacity (continuous rating) | MYHours exceedingFirm capacity (continuous rating)
|  | MY | Hours exceeding | Firm capacity (short-term rating) | MYHours exceedingFirm capacity (short-term rating)
|  | MY | Regional diversity factor | Summer | MYRegional diversity factorSummer | 0.73585 | 0.73585 | 0.73585 | 0.73585 | 0.73585 | 0.73585 | 0.73585 | 0.73585 | 0.73585 | 0.73585 | 0.73585 | 0.73585
|  | MY | Regional diversity factor | Winter | MYRegional diversity factorWinter | 0.93917 | 0.93917 | 0.93917 | 0.93917 | 0.93917 | 0.93917 | 0.93917 | 0.93917 | 0.93917 | 0.93917 | 0.93917 | 0.93917
|  | MY | Load transfer capacity (MVA) | 1 | MYLoad transfer capacity (MVA)1 | 6.3 | [11 empty] | Norwood
|  | MY | Load transfer capacity (MVA) | 2 | MYLoad transfer capacity (MVA)2 | 31.4 | [11 empty] | Trevallyn
|  | MY | Load transfer capacity (MVA) | 3 | MYLoad transfer capacity (MVA)3
|  | MY | Load transfer capacity (MVA) | 4 | MYLoad transfer capacity (MVA)4
|  | MY | Load transfer capacity (MVA) | 5 | MYLoad transfer capacity (MVA)5
|  | MY | Embedded generation capacity (MVA) | Units less than 100 kVA | MYEmbedded generation capacity (MVA)Units less than 100 kVA | 6.4748
|  | MY | Embedded generation capacity (MVA) | Units greater than 100 kVA | MYEmbedded generation capacity (MVA)Units greater than 100 kVA | 2.2
|  | NH | Substation capacity (winter and summer) (MVA) | Total | NHSubstation capacity (winter and summer) (MVA)Total | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
|  | NH | Substation capacity (winter and summer) (MVA) | Firm delivery | NHSubstation capacity (winter and summer) (MVA)Firm delivery | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
|  | NH | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | NHSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
|  | NH | Maximum demand forecast(peak season) | Maximum demand (MW) | NHMaximum demand forecast(peak season)Maximum demand (MW) | 36.9951 | 35.5856 | 36.0976 | 35.8444 | 35.8083 | 36.1298 | 37.0229 | 37.8803 | 38.9008 | 39.8692 | 41.3108 | 42.5469
|  | NH | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | NHMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 1.7571 | 1.6902 | 1.7145 | 1.7025 | 1.7008 | 1.716 | 1.7584 | 1.7992 | 1.8476 | 1.8936 | 1.9621 | 2.0208
|  | NH | Maximum demand forecast(peak season) | Maximum demand (MVA) | NHMaximum demand forecast(peak season)Maximum demand (MVA) | 37.0368 | 35.6257 | 36.1383 | 35.8848 | 35.8487 | 36.1706 | 37.0646 | 37.923 | 38.9446 | 39.9142 | 41.3574 | 42.5949
|  | NH | Maximum demand forecast(peak season) | Power factor (coincident) | NHMaximum demand forecast(peak season)Power factor (coincident) | 0.99887 | 0.99887 | 0.99887 | 0.99887 | 0.99887 | 0.99887 | 0.99887 | 0.99887 | 0.99887 | 0.99887 | 0.99887 | 0.99887
|  | NH | Maximum demand forecast(non-peak season) | Maximum demand (MW) | NHMaximum demand forecast(non-peak season)Maximum demand (MW) | 19.881 | 19.935 | 19.809 | 19.798 | 19.7065 | 19.9177 | 20.3493 | 20.7619 | 21.2297 | 21.7495 | 22.2566 | 22.8603 |  | Summer
|  | NH | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | NHMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 0.43634 | 0.43752 | 0.43476 | 0.43452 | 0.43251 | 0.43714 | 0.44662 | 0.45567 | 0.46594 | 0.47735 | 0.48848 | 0.50173 |  | Summer
|  | NH | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 19.8857 | 19.9398 | 19.8138 | 19.8027 | 19.7113 | 19.9225 | 20.3542 | 20.7669 | 21.2348 | 21.7547 | 22.262 | 22.8658 |  | Summer
|  | NH | Hours exceeding | 95% of maximum demand | NHHours exceeding95% of maximum demand | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5
|  | NH | Hours exceeding | Firm capacity (continuous rating) | NHHours exceedingFirm capacity (continuous rating)
|  | NH | Hours exceeding | Firm capacity (short-term rating) | NHHours exceedingFirm capacity (short-term rating)
|  | NH | Regional diversity factor | Summer | NHRegional diversity factorSummer | 0.82122 | 0.82122 | 0.82122 | 0.82122 | 0.82122 | 0.82122 | 0.82122 | 0.82122 | 0.82122 | 0.82122 | 0.82122 | 0.82122
|  | NH | Regional diversity factor | Winter | NHRegional diversity factorWinter | 0.94864 | 0.94864 | 0.94864 | 0.94864 | 0.94864 | 0.94864 | 0.94864 | 0.94864 | 0.94864 | 0.94864 | 0.94864 | 0.94864
|  | NH | Load transfer capacity (MVA) | 1 | NHLoad transfer capacity (MVA)1 | 9.8 | [11 empty] | Chapel Street
|  | NH | Load transfer capacity (MVA) | 2 | NHLoad transfer capacity (MVA)2 | 14.6 | [11 empty] | East Hobart
|  | NH | Load transfer capacity (MVA) | 3 | NHLoad transfer capacity (MVA)3 | 9.8 | [11 empty] | New Town
|  | NH | Load transfer capacity (MVA) | 4 | NHLoad transfer capacity (MVA)4 | 14.6 | [11 empty] | West Hobart
|  | NH | Load transfer capacity (MVA) | 5 | NHLoad transfer capacity (MVA)5
|  | NH | Embedded generation capacity (MVA) | Units less than 100 kVA | NHEmbedded generation capacity (MVA)Units less than 100 kVA | 5.5279
|  | NH | Embedded generation capacity (MVA) | Units greater than 100 kVA | NHEmbedded generation capacity (MVA)Units greater than 100 kVA | 0
|  | NN | Substation capacity (winter and summer) (MVA) | Total | NNSubstation capacity (winter and summer) (MVA)Total | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  | NN | Substation capacity (winter and summer) (MVA) | Firm delivery | NNSubstation capacity (winter and summer) (MVA)Firm delivery | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
|  | NN | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | NNSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
|  | NN | Maximum demand forecast(peak season) | Maximum demand (MW) | NNMaximum demand forecast(peak season)Maximum demand (MW) | 17.5234 | 14.7982 | 12.2158 | 12.6234 | 12.7399 | 12.8292 | 13.0461 | 13.2303 | 13.4649 | 13.6357 | 13.8508 | 13.9854
|  | NN | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | NNMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 2.5167 | 2.1253 | 1.7544 | 1.813 | 1.8297 | 1.8425 | 1.8737 | 1.9001 | 1.9338 | 1.9583 | 1.9892 | 2.0086
|  | NN | Maximum demand forecast(peak season) | Maximum demand (MVA) | NNMaximum demand forecast(peak season)Maximum demand (MVA) | 17.7032 | 14.95 | 12.3411 | 12.7529 | 12.8706 | 12.9608 | 13.18 | 13.366 | 13.603 | 13.7756 | 13.9929 | 14.1289
|  | NN | Maximum demand forecast(peak season) | Power factor (coincident) | NNMaximum demand forecast(peak season)Power factor (coincident) | 0.98984 | 0.98984 | 0.98984 | 0.98984 | 0.98984 | 0.98984 | 0.98984 | 0.98984 | 0.98984 | 0.98984 | 0.98984 | 0.98984
|  | NN | Maximum demand forecast(non-peak season) | Maximum demand (MW) | NNMaximum demand forecast(non-peak season)Maximum demand (MW) | 17.9506 | 20.7507 | 19.3844 | 19.4148 | 19.5673 | 19.5619 | 19.8373 | 20.0551 | 20.3556 | 20.4969 | 20.9763 | 21.1237 |  | Winter
|  | NN | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | NNMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 1.7936 | 2.0734 | 1.9369 | 1.9399 | 1.9552 | 1.9546 | 1.9821 | 2.0039 | 2.0339 | 2.0481 | 2.096 | 2.1107 |  | Winter
|  | NN | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 18.04 | 20.854 | 19.4809 | 19.5114 | 19.6647 | 19.6593 | 19.9361 | 20.155 | 20.457 | 20.599 | 21.0808 | 21.2289 |  | Winter
|  | NN | Hours exceeding | 95% of maximum demand | NNHours exceeding95% of maximum demand | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
|  | NN | Hours exceeding | Firm capacity (continuous rating) | NNHours exceedingFirm capacity (continuous rating)
|  | NN | Hours exceeding | Firm capacity (short-term rating) | NNHours exceedingFirm capacity (short-term rating)
|  | NN | Regional diversity factor | Summer | NNRegional diversity factorSummer | 0.89365 | 0.89365 | 0.89365 | 0.89365 | 0.89365 | 0.89365 | 0.89365 | 0.89365 | 0.89365 | 0.89365 | 0.89365 | 0.89365
|  | NN | Regional diversity factor | Winter | NNRegional diversity factorWinter | 0.85865 | 0.85865 | 0.85865 | 0.85865 | 0.85865 | 0.85865 | 0.85865 | 0.85865 | 0.85865 | 0.85865 | 0.85865 | 0.85865
|  | NN | Load transfer capacity (MVA) | 1 | NNLoad transfer capacity (MVA)1 | 6.6 | [11 empty] | Meadowbank
|  | NN | Load transfer capacity (MVA) | 2 | NNLoad transfer capacity (MVA)2
|  | NN | Load transfer capacity (MVA) | 3 | NNLoad transfer capacity (MVA)3
|  | NN | Load transfer capacity (MVA) | 4 | NNLoad transfer capacity (MVA)4
|  | NN | Load transfer capacity (MVA) | 5 | NNLoad transfer capacity (MVA)5
|  | NN | Embedded generation capacity (MVA) | Units less than 100 kVA | NNEmbedded generation capacity (MVA)Units less than 100 kVA | 4.4486
|  | NN | Embedded generation capacity (MVA) | Units greater than 100 kVA | NNEmbedded generation capacity (MVA)Units greater than 100 kVA | 0.56
|  | NT | Substation capacity (winter and summer) (MVA) | Total | NTSubstation capacity (winter and summer) (MVA)Total | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5
|  | NT | Substation capacity (winter and summer) (MVA) | Firm delivery | NTSubstation capacity (winter and summer) (MVA)Firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | NT | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | NTSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | NT | Maximum demand forecast(peak season) | Maximum demand (MW) | NTMaximum demand forecast(peak season)Maximum demand (MW) | 3.7662 | 3.8675 | 3.9105 | 3.8469 | 3.8278 | 3.8148 | 3.8672 | 3.8992 | 3.9426 | 3.9619 | 4.0391 | 4.0781
|  | NT | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | NTMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 0.32041 | 0.32902 | 0.33268 | 0.32727 | 0.32564 | 0.32453 | 0.32899 | 0.33172 | 0.33541 | 0.33705 | 0.34362 | 0.34694
|  | NT | Maximum demand forecast(peak season) | Maximum demand (MVA) | NTMaximum demand forecast(peak season)Maximum demand (MVA) | 3.7798 | 3.8815 | 3.9247 | 3.8608 | 3.8416 | 3.8285 | 3.8812 | 3.9133 | 3.9569 | 3.9762 | 4.0537 | 4.0929
|  | NT | Maximum demand forecast(peak season) | Power factor (coincident) | NTMaximum demand forecast(peak season)Power factor (coincident) | 0.9964 | 0.9964 | 0.9964 | 0.9964 | 0.9964 | 0.9964 | 0.9964 | 0.9964 | 0.9964 | 0.9964 | 0.9964 | 0.9964
|  | NT | Maximum demand forecast(non-peak season) | Maximum demand (MW) | NTMaximum demand forecast(non-peak season)Maximum demand (MW) | 4.1941 | 4.0325 | 3.9898 | 3.9435 | 3.9159 | 3.9225 | 3.9817 | 4.0207 | 4.074 | 4.1155 | 4.1626 | 4.2094 |  | Summer
|  | NT | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | NTMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 0.35845 | 0.34464 | 0.34099 | 0.33704 | 0.33467 | 0.33524 | 0.3403 | 0.34363 | 0.34818 | 0.35173 | 0.35576 | 0.35975 |  | Summer
|  | NT | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 4.2094 | 4.0472 | 4.0044 | 3.9579 | 3.9301 | 3.9368 | 3.9962 | 4.0354 | 4.0888 | 4.1305 | 4.1778 | 4.2247 |  | Summer
|  | NT | Hours exceeding | 95% of maximum demand | NTHours exceeding95% of maximum demand | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
|  | NT | Hours exceeding | Firm capacity (continuous rating) | NTHours exceedingFirm capacity (continuous rating) | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760
|  | NT | Hours exceeding | Firm capacity (short-term rating) | NTHours exceedingFirm capacity (short-term rating) | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760
|  | NT | Regional diversity factor | Summer | NTRegional diversity factorSummer | 0.89037 | 0.89037 | 0.89037 | 0.89037 | 0.89037 | 0.89037 | 0.89037 | 0.89037 | 0.89037 | 0.89037 | 0.89037 | 0.89037
|  | NT | Regional diversity factor | Winter | NTRegional diversity factorWinter | 0.875 | 0.875 | 0.875 | 0.875 | 0.875 | 0.875 | 0.875 | 0.875 | 0.875 | 0.875 | 0.875 | 0.875
|  | NT | Load transfer capacity (MVA) | 1 | NTLoad transfer capacity (MVA)1
|  | NT | Load transfer capacity (MVA) | 2 | NTLoad transfer capacity (MVA)2
|  | NT | Load transfer capacity (MVA) | 3 | NTLoad transfer capacity (MVA)3
|  | NT | Load transfer capacity (MVA) | 4 | NTLoad transfer capacity (MVA)4
|  | NT | Load transfer capacity (MVA) | 5 | NTLoad transfer capacity (MVA)5
|  | NT | Embedded generation capacity (MVA) | Units less than 100 kVA | NTEmbedded generation capacity (MVA)Units less than 100 kVA | 0
|  | NT | Embedded generation capacity (MVA) | Units greater than 100 kVA | NTEmbedded generation capacity (MVA)Units greater than 100 kVA | 0
|  | NW | Substation capacity (winter and summer) (MVA) | Total | NWSubstation capacity (winter and summer) (MVA)Total | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
|  | NW | Substation capacity (winter and summer) (MVA) | Firm delivery | NWSubstation capacity (winter and summer) (MVA)Firm delivery | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
|  | NW | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | NWSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  | NW | Maximum demand forecast(peak season) | Maximum demand (MW) | NWMaximum demand forecast(peak season)Maximum demand (MW) | 29.5605 | 29.3876 | 29.2028 | 28.6609 | 28.368 | 28.2616 | 28.5956 | 28.8422 | 29.1613 | 29.358 | 29.9636 | 30.2549
|  | NW | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | NWMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 0.70668 | 0.70255 | 0.69813 | 0.68518 | 0.67817 | 0.67563 | 0.68361 | 0.68951 | 0.69714 | 0.70184 | 0.71632 | 0.72328
|  | NW | Maximum demand forecast(peak season) | Maximum demand (MVA) | NWMaximum demand forecast(peak season)Maximum demand (MVA) | 29.5689 | 29.396 | 29.2112 | 28.6691 | 28.3761 | 28.2697 | 28.6037 | 28.8504 | 29.1696 | 29.3664 | 29.9722 | 30.2636
|  | NW | Maximum demand forecast(peak season) | Power factor (coincident) | NWMaximum demand forecast(peak season)Power factor (coincident) | 0.99971 | 0.99971 | 0.99971 | 0.99971 | 0.99971 | 0.99971 | 0.99971 | 0.99971 | 0.99971 | 0.99971 | 0.99971 | 0.99971
|  | NW | Maximum demand forecast(non-peak season) | Maximum demand (MW) | NWMaximum demand forecast(non-peak season)Maximum demand (MW) | 16.3697 | 16.7137 | 16.0983 | 15.7144 | 15.3717 | 15.2719 | 15.3791 | 15.4696 | 15.6203 | 15.8102 | 16.043 | 16.2816 |  | Summer
|  | NW | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | NWMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 0.23927 | 0.2443 | 0.2353 | 0.22969 | 0.22468 | 0.22322 | 0.22479 | 0.22611 | 0.22831 | 0.23109 | 0.23449 | 0.23798 |  | Summer
|  | NW | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 16.3714 | 16.7155 | 16.1 | 15.7161 | 15.3734 | 15.2735 | 15.3807 | 15.4712 | 15.6219 | 15.8118 | 16.0447 | 16.2834 |  | Summer
|  | NW | Hours exceeding | 95% of maximum demand | NWHours exceeding95% of maximum demand | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
|  | NW | Hours exceeding | Firm capacity (continuous rating) | NWHours exceedingFirm capacity (continuous rating)
|  | NW | Hours exceeding | Firm capacity (short-term rating) | NWHours exceedingFirm capacity (short-term rating)
|  | NW | Regional diversity factor | Summer | NWRegional diversity factorSummer | 0.87602 | 0.87602 | 0.87602 | 0.87602 | 0.87602 | 0.87602 | 0.87602 | 0.87602 | 0.87602 | 0.87602 | 0.87602 | 0.87602
|  | NW | Regional diversity factor | Winter | NWRegional diversity factorWinter | 0.90014 | 0.90014 | 0.90014 | 0.90014 | 0.90014 | 0.90014 | 0.90014 | 0.90014 | 0.90014 | 0.90014 | 0.90014 | 0.90014
|  | NW | Load transfer capacity (MVA) | 1 | NWLoad transfer capacity (MVA)1 | 16.2 | [11 empty] | Hadspen
|  | NW | Load transfer capacity (MVA) | 2 | NWLoad transfer capacity (MVA)2 | 10.8 | [11 empty] | Mowbray
|  | NW | Load transfer capacity (MVA) | 3 | NWLoad transfer capacity (MVA)3 | 27 | [11 empty] | St Leonards
|  | NW | Load transfer capacity (MVA) | 4 | NWLoad transfer capacity (MVA)4 | 16.2 | [11 empty] | Trevallyn
|  | NW | Load transfer capacity (MVA) | 5 | NWLoad transfer capacity (MVA)5
|  | NW | Embedded generation capacity (MVA) | Units less than 100 kVA | NWEmbedded generation capacity (MVA)Units less than 100 kVA | 7.5109
|  | NW | Embedded generation capacity (MVA) | Units greater than 100 kVA | NWEmbedded generation capacity (MVA)Units greater than 100 kVA | 0.58708
|  | PL | Substation capacity (winter and summer) (MVA) | Total | PLSubstation capacity (winter and summer) (MVA)Total | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 50 | 50 | 50 | 50 | 50
|  | PL | Substation capacity (winter and summer) (MVA) | Firm delivery | PLSubstation capacity (winter and summer) (MVA)Firm delivery | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 25[2] | 25 | 25 | 25 | 25
|  | PL | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | PLSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 27 | 27 | 27 | 27 | 27 | 30 | 30 | 30 | 30 | 30 | 30 | 30
|  | PL | Maximum demand forecast(peak season) | Maximum demand (MW) | PLMaximum demand forecast(peak season)Maximum demand (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | PL | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | PLMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 22.0321 | 22.6255 | 23.2909 | 23.1324 | 23.0263 | 23.011 | 23.1473 | 23.2525 | 23.406 | 23.5057 | 26.1236 | 26.1849
|  | PL | Maximum demand forecast(peak season) | Maximum demand (MVA) | PLMaximum demand forecast(peak season)Maximum demand (MVA) | 22.0321 | 22.6255 | 23.2909 | 23.1324 | 23.0263 | 23.011 | 23.1473 | 23.2525 | 23.406 | 23.5057 | 26.1236 | 26.1849
|  | PL | Maximum demand forecast(peak season) | Power factor (coincident) | PLMaximum demand forecast(peak season)Power factor (coincident) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | PL | Maximum demand forecast(non-peak season) | Maximum demand (MW) | PLMaximum demand forecast(non-peak season)Maximum demand (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Winter
|  | PL | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | PLMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 20.7189 | 21.4055 | 22.3483 | 22.1556 | 22.0766 | 22.0139 | 22.1241 | 22.2087 | 22.3388 | 22.3994 | 25.1789 | 25.2418 |  | Winter
|  | PL | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 20.7189 | 21.4055 | 22.3483 | 22.1556 | 22.0766 | 22.0139 | 22.1241 | 22.2087 | 22.3388 | 22.3994 | 25.1789 | 25.2418 |  | Winter
|  | PL | Hours exceeding | 95% of maximum demand | PLHours exceeding95% of maximum demand | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5
|  | PL | Hours exceeding | Firm capacity (continuous rating) | PLHours exceedingFirm capacity (continuous rating)
|  | PL | Hours exceeding | Firm capacity (short-term rating) | PLHours exceedingFirm capacity (short-term rating)
|  | PL | Regional diversity factor | Summer | PLRegional diversity factorSummer | 0.6205 | 0.6205 | 0.6205 | 0.6205 | 0.6205 | 0.6205 | 0.6205 | 0.6205 | 0.6205 | 0.6205 | 0.6205 | 0.6205
|  | PL | Regional diversity factor | Winter | PLRegional diversity factorWinter | 0.86096 | 0.86096 | 0.86096 | 0.86096 | 0.86096 | 0.86096 | 0.86096 | 0.86096 | 0.86096 | 0.86096 | 0.86096 | 0.86096
|  | PL | Load transfer capacity (MVA) | 1 | PLLoad transfer capacity (MVA)1 | 3.9 | [11 empty] | Burnie
|  | PL | Load transfer capacity (MVA) | 2 | PLLoad transfer capacity (MVA)2 | 3.9 | [11 empty] | Smithton
|  | PL | Load transfer capacity (MVA) | 3 | PLLoad transfer capacity (MVA)3
|  | PL | Load transfer capacity (MVA) | 4 | PLLoad transfer capacity (MVA)4
|  | PL | Load transfer capacity (MVA) | 5 | PLLoad transfer capacity (MVA)5
|  | PL | Embedded generation capacity (MVA) | Units less than 100 kVA | PLEmbedded generation capacity (MVA)Units less than 100 kVA | 2.3477
|  | PL | Embedded generation capacity (MVA) | Units greater than 100 kVA | PLEmbedded generation capacity (MVA)Units greater than 100 kVA | 0.45
|  | PM | Substation capacity (winter and summer) (MVA) | Total | PMSubstation capacity (winter and summer) (MVA)Total | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
|  | PM | Substation capacity (winter and summer) (MVA) | Firm delivery | PMSubstation capacity (winter and summer) (MVA)Firm delivery | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
|  | PM | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | PMSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
|  | PM | Maximum demand forecast(peak season) | Maximum demand (MW) | PMMaximum demand forecast(peak season)Maximum demand (MW) | 10.971 | 14.3642 | 15.2001 | 15.47 | 15.5243 | 15.6517 | 15.9628 | 16.2031 | 16.5015 | 16.7445 | 16.9846 | 17.2551
|  | PM | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | PMMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 3.4746 | 4.5493 | 4.814 | 4.8995 | 4.9167 | 4.957 | 5.0556 | 5.1317 | 5.2262 | 5.3031 | 5.3792 | 5.4649
|  | PM | Maximum demand forecast(peak season) | Maximum demand (MVA) | PMMaximum demand forecast(peak season)Maximum demand (MVA) | 11.5081 | 15.0674 | 15.9442 | 16.2273 | 16.2842 | 16.4179 | 16.7443 | 16.9963 | 17.3093 | 17.5643 | 17.8161 | 18.0998
|  | PM | Maximum demand forecast(peak season) | Power factor (coincident) | PMMaximum demand forecast(peak season)Power factor (coincident) | 0.95333 | 0.95333 | 0.95333 | 0.95333 | 0.95333 | 0.95333 | 0.95333 | 0.95333 | 0.95333 | 0.95333 | 0.95333 | 0.95333
|  | PM | Maximum demand forecast(non-peak season) | Maximum demand (MW) | PMMaximum demand forecast(non-peak season)Maximum demand (MW) | 5.9938 | 7.0633 | 8.0388 | 8.3475 | 8.4516 | 8.478 | 8.6187 | 8.7245 | 8.8645 | 8.9475 | 9.1566 | 9.2794 |  | Winter
|  | PM | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | PMMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 1.12 | 1.3199 | 1.5022 | 1.5599 | 1.5793 | 1.5843 | 1.6106 | 1.6303 | 1.6565 | 1.672 | 1.7111 | 1.734 |  | Winter
|  | PM | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 6.0975 | 7.1856 | 8.1779 | 8.492 | 8.5979 | 8.6247 | 8.7679 | 8.8755 | 9.018 | 9.1023 | 9.3151 | 9.44 |  | Winter
|  | PM | Hours exceeding | 95% of maximum demand | PMHours exceeding95% of maximum demand | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14
|  | PM | Hours exceeding | Firm capacity (continuous rating) | PMHours exceedingFirm capacity (continuous rating)
|  | PM | Hours exceeding | Firm capacity (short-term rating) | PMHours exceedingFirm capacity (short-term rating)
|  | PM | Regional diversity factor | Summer | PMRegional diversity factorSummer | 0.69309 | 0.69309 | 0.69309 | 0.69309 | 0.69309 | 0.69309 | 0.69309 | 0.69309 | 0.69309 | 0.69309 | 0.69309 | 0.69309
|  | PM | Regional diversity factor | Winter | PMRegional diversity factorWinter | 0.56731 | 0.56731 | 0.56731 | 0.56731 | 0.56731 | 0.56731 | 0.56731 | 0.56731 | 0.56731 | 0.56731 | 0.56731 | 0.56731
|  | PM | Load transfer capacity (MVA) | 1 | PMLoad transfer capacity (MVA)1 | 1 | [11 empty] | Avoca
|  | PM | Load transfer capacity (MVA) | 2 | PMLoad transfer capacity (MVA)2 | 5 | [11 empty] | Hadspen
|  | PM | Load transfer capacity (MVA) | 3 | PMLoad transfer capacity (MVA)3 | 2 | [11 empty] | Norwood
|  | PM | Load transfer capacity (MVA) | 4 | PMLoad transfer capacity (MVA)4 | 1.5 | [11 empty] | Railton
|  | PM | Load transfer capacity (MVA) | 5 | PMLoad transfer capacity (MVA)5
|  | PM | Embedded generation capacity (MVA) | Units less than 100 kVA | PMEmbedded generation capacity (MVA)Units less than 100 kVA | 1.026
|  | PM | Embedded generation capacity (MVA) | Units greater than 100 kVA | PMEmbedded generation capacity (MVA)Units greater than 100 kVA | 0
|  | QT | Substation capacity (winter and summer) (MVA) | Total | QTSubstation capacity (winter and summer) (MVA)Total | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
|  | QT | Substation capacity (winter and summer) (MVA) | Firm delivery | QTSubstation capacity (winter and summer) (MVA)Firm delivery | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
|  | QT | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | QTSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
|  | QT | Maximum demand forecast(peak season) | Maximum demand (MW) | QTMaximum demand forecast(peak season)Maximum demand (MW) | 5.7832 | 6.157 | 6.248 | 6.1492 | 6.1219 | 6.1051 | 6.1944 | 6.2547 | 6.3409 | 6.4 | 6.5601 | 6.6713
|  | QT | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | QTMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 0.16154 | 0.17198 | 0.17452 | 0.17176 | 0.171 | 0.17053 | 0.17302 | 0.17471 | 0.17712 | 0.17877 | 0.18324 | 0.18635
|  | QT | Maximum demand forecast(peak season) | Maximum demand (MVA) | QTMaximum demand forecast(peak season)Maximum demand (MVA) | 5.7855 | 6.1594 | 6.2504 | 6.1516 | 6.1243 | 6.1075 | 6.1968 | 6.2572 | 6.3434 | 6.4025 | 6.5627 | 6.6739
|  | QT | Maximum demand forecast(peak season) | Power factor (coincident) | QTMaximum demand forecast(peak season)Power factor (coincident) | 0.99961 | 0.99961 | 0.99961 | 0.99961 | 0.99961 | 0.99961 | 0.99961 | 0.99961 | 0.99961 | 0.99961 | 0.99961 | 0.99961
|  | QT | Maximum demand forecast(non-peak season) | Maximum demand (MW) | QTMaximum demand forecast(non-peak season)Maximum demand (MW) | 4.9227 | 3.5383 | 3.4887 | 3.4219 | 3.3854 | 3.3807 | 3.4231 | 3.4503 | 3.4961 | 3.5461 | 3.6114 | 3.6946 |  | Summer
|  | QT | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | QTMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 1.6318 | 1.1729 | 1.1564 | 1.1343 | 1.1222 | 1.1206 | 1.1347 | 1.1437 | 1.1589 | 1.1755 | 1.1971 | 1.2247 |  | Summer
|  | QT | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 5.1861 | 3.7277 | 3.6754 | 3.605 | 3.5666 | 3.5616 | 3.6063 | 3.6349 | 3.6832 | 3.7358 | 3.8046 | 3.8923 |  | Summer
|  | QT | Hours exceeding | 95% of maximum demand | QTHours exceeding95% of maximum demand | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7
|  | QT | Hours exceeding | Firm capacity (continuous rating) | QTHours exceedingFirm capacity (continuous rating)
|  | QT | Hours exceeding | Firm capacity (short-term rating) | QTHours exceedingFirm capacity (short-term rating)
|  | QT | Regional diversity factor | Summer | QTRegional diversity factorSummer | 0.84143 | 0.84143 | 0.84143 | 0.84143 | 0.84143 | 0.84143 | 0.84143 | 0.84143 | 0.84143 | 0.84143 | 0.84143 | 0.84143
|  | QT | Regional diversity factor | Winter | QTRegional diversity factorWinter | 0.88151 | 0.88151 | 0.88151 | 0.88151 | 0.88151 | 0.88151 | 0.88151 | 0.88151 | 0.88151 | 0.88151 | 0.88151 | 0.88151
|  | QT | Load transfer capacity (MVA) | 1 | QTLoad transfer capacity (MVA)1
|  | QT | Load transfer capacity (MVA) | 2 | QTLoad transfer capacity (MVA)2
|  | QT | Load transfer capacity (MVA) | 3 | QTLoad transfer capacity (MVA)3
|  | QT | Load transfer capacity (MVA) | 4 | QTLoad transfer capacity (MVA)4
|  | QT | Load transfer capacity (MVA) | 5 | QTLoad transfer capacity (MVA)5
|  | QT | Embedded generation capacity (MVA) | Units less than 100 kVA | QTEmbedded generation capacity (MVA)Units less than 100 kVA | 0.88118
|  | QT | Embedded generation capacity (MVA) | Units greater than 100 kVA | QTEmbedded generation capacity (MVA)Units greater than 100 kVA | 0
|  | RA | Substation capacity (winter and summer) (MVA) | Total | RASubstation capacity (winter and summer) (MVA)Total | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
|  | RA | Substation capacity (winter and summer) (MVA) | Firm delivery | RASubstation capacity (winter and summer) (MVA)Firm delivery | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
|  | RA | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | RASubstation capacity (winter and summer) (MVA)Short-term firm delivery | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
|  | RA | Maximum demand forecast(peak season) | Maximum demand (MW) | RAMaximum demand forecast(peak season)Maximum demand (MW) | 47.0716 | 48.9105 | 48.9116 | 47.7573 | 47.1589 | 48.1493 | 49.2743 | 50.1864 | 50.5503 | 49.9107 | 50.7342 | 49.9078
|  | RA | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | RAMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 5.2053 | 5.4086 | 5.4087 | 5.2811 | 5.2149 | 5.3244 | 5.4488 | 5.5497 | 5.5899 | 5.5192 | 5.6103 | 5.5189
|  | RA | Maximum demand forecast(peak season) | Maximum demand (MVA) | RAMaximum demand forecast(peak season)Maximum demand (MVA) | 47.3585 | 49.2087 | 49.2097 | 48.0484 | 47.4464 | 48.4428 | 49.5747 | 50.4923 | 50.8584 | 50.2149 | 51.0435 | 50.212
|  | RA | Maximum demand forecast(peak season) | Power factor (coincident) | RAMaximum demand forecast(peak season)Power factor (coincident) | 0.99394 | 0.99394 | 0.99394 | 0.99394 | 0.99394 | 0.99394 | 0.99394 | 0.99394 | 0.99394 | 0.99394 | 0.99394 | 0.99394
|  | RA | Maximum demand forecast(non-peak season) | Maximum demand (MW) | RAMaximum demand forecast(non-peak season)Maximum demand (MW) | 46.8524 | 50.1494 | 49.4045 | 48.5118 | 47.8451 | 49.4199 | 50.8217 | 52.0116 | 52.5317 | 52.0838 | 52.5815 | 51.7708 |  | Summer
|  | RA | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | RAMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 4.1307 | 4.4213 | 4.3557 | 4.277 | 4.2182 | 4.357 | 4.4806 | 4.5855 | 4.6314 | 4.5919 | 4.6358 | 4.5643 |  | Summer
|  | RA | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 47.0341 | 50.3439 | 49.5961 | 48.7 | 48.0307 | 49.6116 | 51.0189 | 52.2134 | 52.7354 | 52.2858 | 52.7854 | 51.9716 |  | Summer
|  | RA | Hours exceeding | 95% of maximum demand | RAHours exceeding95% of maximum demand | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5
|  | RA | Hours exceeding | Firm capacity (continuous rating) | RAHours exceedingFirm capacity (continuous rating)
|  | RA | Hours exceeding | Firm capacity (short-term rating) | RAHours exceedingFirm capacity (short-term rating)
|  | RA | Regional diversity factor | Summer | RARegional diversity factorSummer | 0.76883 | 0.76883 | 0.76883 | 0.76883 | 0.76883 | 0.76883 | 0.76883 | 0.76883 | 0.76883 | 0.76883 | 0.76883 | 0.76883
|  | RA | Regional diversity factor | Winter | RARegional diversity factorWinter | 0.95984 | 0.95984 | 0.95984 | 0.95984 | 0.95984 | 0.95984 | 0.95984 | 0.95984 | 0.95984 | 0.95984 | 0.95984 | 0.95984
|  | RA | Load transfer capacity (MVA) | 1 | RALoad transfer capacity (MVA)1 | 8.7 | [11 empty] | Devonport
|  | RA | Load transfer capacity (MVA) | 2 | RALoad transfer capacity (MVA)2 | 4.4 | [11 empty] | Ulverstone
|  | RA | Load transfer capacity (MVA) | 3 | RALoad transfer capacity (MVA)3
|  | RA | Load transfer capacity (MVA) | 4 | RALoad transfer capacity (MVA)4
|  | RA | Load transfer capacity (MVA) | 5 | RALoad transfer capacity (MVA)5
|  | RA | Embedded generation capacity (MVA) | Units less than 100 kVA | RAEmbedded generation capacity (MVA)Units less than 100 kVA | 11.638
|  | RA | Embedded generation capacity (MVA) | Units greater than 100 kVA | RAEmbedded generation capacity (MVA)Units greater than 100 kVA | 3.2592
|  | RB22 | Substation capacity (winter and summer) (MVA) | Total | RB22Substation capacity (winter and summer) (MVA)Total | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19
|  | RB22 | Substation capacity (winter and summer) (MVA) | Firm delivery | RB22Substation capacity (winter and summer) (MVA)Firm delivery | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
|  | RB22 | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | RB22Substation capacity (winter and summer) (MVA)Short-term firm delivery | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
|  | RB22 | Maximum demand forecast(peak season) | Maximum demand (MW) | RB22Maximum demand forecast(peak season)Maximum demand (MW) | 1.92 | 2.2611 | 2.3989 | 2.3506 | 2.3231 | 2.3168 | 2.3414 | 2.3576 | 2.3869 | 2.4214 | 2.4678 | 2.5269
|  | RB22 | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | RB22Maximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 0.08986 | 0.10583 | 0.11228 | 0.11001 | 0.10873 | 0.10843 | 0.10958 | 0.11034 | 0.11171 | 0.11333 | 0.1155 | 0.11827
|  | RB22 | Maximum demand forecast(peak season) | Maximum demand (MVA) | RB22Maximum demand forecast(peak season)Maximum demand (MVA) | 1.9221 | 2.2636 | 2.4016 | 2.3532 | 2.3257 | 2.3194 | 2.344 | 2.3602 | 2.3895 | 2.4241 | 2.4705 | 2.5297
|  | RB22 | Maximum demand forecast(peak season) | Power factor (coincident) | RB22Maximum demand forecast(peak season)Power factor (coincident) | 0.99891 | 0.99891 | 0.99891 | 0.99891 | 0.99891 | 0.99891 | 0.99891 | 0.99891 | 0.99891 | 0.99891 | 0.99891 | 0.99891
|  | RB22 | Maximum demand forecast(non-peak season) | Maximum demand (MW) | RB22Maximum demand forecast(non-peak season)Maximum demand (MW) | 0.77031 | 5.6174 | 5.7358 | 5.6365 | 5.6024 | 5.5777 | 5.6503 | 5.6989 | 5.7721 | 5.8187 | 5.9584 | 6.0452 |  | Winter
|  | RB22 | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | RB22Maximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 0.044378 | 0.32362 | 0.33045 | 0.32473 | 0.32276 | 0.32134 | 0.32552 | 0.32832 | 0.33254 | 0.33522 | 0.34327 | 0.34827 |  | Winter
|  | RB22 | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 0.77159 | 5.6267 | 5.7453 | 5.6459 | 5.6116 | 5.587 | 5.6597 | 5.7084 | 5.7817 | 5.8284 | 5.9683 | 6.0552 |  | Winter
|  | RB22 | Hours exceeding | 95% of maximum demand | RB22Hours exceeding95% of maximum demand | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
|  | RB22 | Hours exceeding | Firm capacity (continuous rating) | RB22Hours exceedingFirm capacity (continuous rating)
|  | RB22 | Hours exceeding | Firm capacity (short-term rating) | RB22Hours exceedingFirm capacity (short-term rating)
|  | RB22 | Regional diversity factor | Summer | RB22Regional diversity factorSummer | 0.64286 | 0.64286 | 0.64286 | 0.64286 | 0.64286 | 0.64286 | 0.64286 | 0.64286 | 0.64286 | 0.64286 | 0.64286 | 0.64286
|  | RB22 | Regional diversity factor | Winter | RB22Regional diversity factorWinter | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | RB22 | Load transfer capacity (MVA) | 1 | RB22Load transfer capacity (MVA)1
|  | RB22 | Load transfer capacity (MVA) | 2 | RB22Load transfer capacity (MVA)2
|  | RB22 | Load transfer capacity (MVA) | 3 | RB22Load transfer capacity (MVA)3
|  | RB22 | Load transfer capacity (MVA) | 4 | RB22Load transfer capacity (MVA)4
|  | RB22 | Load transfer capacity (MVA) | 5 | RB22Load transfer capacity (MVA)5
|  | RB22 | Embedded generation capacity (MVA) | Units less than 100 kVA | RB22Embedded generation capacity (MVA)Units less than 100 kVA | 0
|  | RB22 | Embedded generation capacity (MVA) | Units greater than 100 kVA | RB22Embedded generation capacity (MVA)Units greater than 100 kVA | 0
|  | RB44 | Substation capacity (winter and summer) (MVA) | Total | RB44Substation capacity (winter and summer) (MVA)Total | 72 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102
|  | RB44 | Substation capacity (winter and summer) (MVA) | Firm delivery | RB44Substation capacity (winter and summer) (MVA)Firm delivery | 36 | 66[2] | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66
|  | RB44 | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | RB44Substation capacity (winter and summer) (MVA)Short-term firm delivery | 36 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72
|  | RB44 | Maximum demand forecast(peak season) | Maximum demand (MW) | RB44Maximum demand forecast(peak season)Maximum demand (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | RB44 | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | RB44Maximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 42.7625 | 42.8784 | 41.3864 | 40.7444 | 40.4416 | 40.2791 | 40.4455 | 40.549 | 40.7129 | 40.6756 | 41.7647 | 41.6739
|  | RB44 | Maximum demand forecast(peak season) | Maximum demand (MVA) | RB44Maximum demand forecast(peak season)Maximum demand (MVA) | 42.7625 | 42.8784 | 41.3864 | 40.7444 | 40.4416 | 40.2791 | 40.4455 | 40.549 | 40.7129 | 40.6756 | 41.7647 | 41.6739
|  | RB44 | Maximum demand forecast(peak season) | Power factor (coincident) | RB44Maximum demand forecast(peak season)Power factor (coincident) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | RB44 | Maximum demand forecast(non-peak season) | Maximum demand (MW) | RB44Maximum demand forecast(non-peak season)Maximum demand (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Summer
|  | RB44 | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | RB44Maximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 40.0117 | 42.0001 | 40.1039 | 39.5664 | 39.2252 | 39.1698 | 39.3604 | 39.494 | 39.6985 | 39.7745 | 40.6762 | 40.6294 |  | Summer
|  | RB44 | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 40.0117 | 42.0001 | 40.1039 | 39.5664 | 39.2252 | 39.1698 | 39.3604 | 39.494 | 39.6985 | 39.7745 | 40.6762 | 40.6294 |  | Summer
|  | RB44 | Hours exceeding | 95% of maximum demand | RB44Hours exceeding95% of maximum demand | 154 | 154 | 154 | 154 | 154 | 154 | 154 | 154 | 154 | 154 | 154 | 154
|  | RB44 | Hours exceeding | Firm capacity (continuous rating) | RB44Hours exceedingFirm capacity (continuous rating)
|  | RB44 | Hours exceeding | Firm capacity (short-term rating) | RB44Hours exceedingFirm capacity (short-term rating)
|  | RB44 | Regional diversity factor | Summer | RB44Regional diversity factorSummer | 0.88287 | 0.88287 | 0.88287 | 0.88287 | 0.88287 | 0.88287 | 0.88287 | 0.88287 | 0.88287 | 0.88287 | 0.88287 | 0.88287
|  | RB44 | Regional diversity factor | Winter | RB44Regional diversity factorWinter | 0.86062 | 0.86062 | 0.86062 | 0.86062 | 0.86062 | 0.86062 | 0.86062 | 0.86062 | 0.86062 | 0.86062 | 0.86062 | 0.86062
|  | RB44 | Load transfer capacity (MVA) | 1 | RB44Load transfer capacity (MVA)1
|  | RB44 | Load transfer capacity (MVA) | 2 | RB44Load transfer capacity (MVA)2
|  | RB44 | Load transfer capacity (MVA) | 3 | RB44Load transfer capacity (MVA)3
|  | RB44 | Load transfer capacity (MVA) | 4 | RB44Load transfer capacity (MVA)4
|  | RB44 | Load transfer capacity (MVA) | 5 | RB44Load transfer capacity (MVA)5
|  | RB44 | Embedded generation capacity (MVA) | Units less than 100 kVA | RB44Embedded generation capacity (MVA)Units less than 100 kVA | 0.57149
|  | RB44 | Embedded generation capacity (MVA) | Units greater than 100 kVA | RB44Embedded generation capacity (MVA)Units greater than 100 kVA | 0
|  | RI | Substation capacity (winter and summer) (MVA) | Total | RISubstation capacity (winter and summer) (MVA)Total | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
|  | RI | Substation capacity (winter and summer) (MVA) | Firm delivery | RISubstation capacity (winter and summer) (MVA)Firm delivery | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
|  | RI | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | RISubstation capacity (winter and summer) (MVA)Short-term firm delivery | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
|  | RI | Maximum demand forecast(peak season) | Maximum demand (MW) | RIMaximum demand forecast(peak season)Maximum demand (MW) | 68.9955 | 66.4123 | 67.4645 | 69.1963 | 70.7617 | 71.7285 | 73.2111 | 74.2957 | 75.5155 | 76.4382 | 78.2705 | 79.5727
|  | RI | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | RIMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 14.892 | 14.3344 | 14.5615 | 14.9353 | 15.2732 | 15.4819 | 15.8019 | 16.036 | 16.2992 | 16.4984 | 16.8939 | 17.175
|  | RI | Maximum demand forecast(peak season) | Maximum demand (MVA) | RIMaximum demand forecast(peak season)Maximum demand (MVA) | 70.5844 | 67.9417 | 69.0181 | 70.7898 | 72.3912 | 73.3803 | 74.8971 | 76.0066 | 77.2545 | 78.1984 | 80.0729 | 81.4051
|  | RI | Maximum demand forecast(peak season) | Power factor (coincident) | RIMaximum demand forecast(peak season)Power factor (coincident) | 0.97749 | 0.97749 | 0.97749 | 0.97749 | 0.97749 | 0.97749 | 0.97749 | 0.97749 | 0.97749 | 0.97749 | 0.97749 | 0.97749
|  | RI | Maximum demand forecast(non-peak season) | Maximum demand (MW) | RIMaximum demand forecast(non-peak season)Maximum demand (MW) | 44.3146 | 45.5488 | 45.1732 | 47.351 | 48.887 | 49.9401 | 51.0056 | 51.7492 | 52.5932 | 53.4366 | 54.2591 | 55.1917 |  | Summer
|  | RI | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | RIMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 3.9069 | 4.0157 | 3.9826 | 4.1746 | 4.31 | 4.4029 | 4.4968 | 4.5624 | 4.6368 | 4.7112 | 4.7837 | 4.8659 |  | Summer
|  | RI | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 44.4865 | 45.7255 | 45.3484 | 47.5347 | 49.0766 | 50.1338 | 51.2035 | 51.95 | 52.7972 | 53.6439 | 54.4696 | 55.4058 |  | Summer
|  | RI | Hours exceeding | 95% of maximum demand | RIHours exceeding95% of maximum demand | 23.5 | 23.5 | 23.5 | 23.5 | 23.5 | 23.5 | 23.5 | 23.5 | 23.5 | 23.5 | 23.5 | 23.5
|  | RI | Hours exceeding | Firm capacity (continuous rating) | RIHours exceedingFirm capacity (continuous rating)
|  | RI | Hours exceeding | Firm capacity (short-term rating) | RIHours exceedingFirm capacity (short-term rating)
|  | RI | Regional diversity factor | Summer | RIRegional diversity factorSummer | 0.79104 | 0.79104 | 0.79104 | 0.79104 | 0.79104 | 0.79104 | 0.79104 | 0.79104 | 0.79104 | 0.79104 | 0.79104 | 0.79104
|  | RI | Regional diversity factor | Winter | RIRegional diversity factorWinter | 0.90684 | 0.90684 | 0.90684 | 0.90684 | 0.90684 | 0.90684 | 0.90684 | 0.90684 | 0.90684 | 0.90684 | 0.90684 | 0.90684
|  | RI | Load transfer capacity (MVA) | 1 | RILoad transfer capacity (MVA)1
|  | RI | Load transfer capacity (MVA) | 2 | RILoad transfer capacity (MVA)2
|  | RI | Load transfer capacity (MVA) | 3 | RILoad transfer capacity (MVA)3
|  | RI | Load transfer capacity (MVA) | 4 | RILoad transfer capacity (MVA)4
|  | RI | Load transfer capacity (MVA) | 5 | RILoad transfer capacity (MVA)5
|  | RI | Embedded generation capacity (MVA) | Units less than 100 kVA | RIEmbedded generation capacity (MVA)Units less than 100 kVA | 5.8486
|  | RI | Embedded generation capacity (MVA) | Units greater than 100 kVA | RIEmbedded generation capacity (MVA)Units greater than 100 kVA | 0.59998
|  | RK | Substation capacity (winter and summer) (MVA) | Total | RKSubstation capacity (winter and summer) (MVA)Total | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
|  | RK | Substation capacity (winter and summer) (MVA) | Firm delivery | RKSubstation capacity (winter and summer) (MVA)Firm delivery | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
|  | RK | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | RKSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42
|  | RK | Maximum demand forecast(peak season) | Maximum demand (MW) | RKMaximum demand forecast(peak season)Maximum demand (MW) | 21.6654 | 22.851 | 23.0555 | 22.7306 | 22.6047 | 22.7396 | 23.2151 | 23.6343 | 24.1171 | 24.6214 | 25.4553 | 26.0846
|  | RK | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | RKMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 0.74456 | 0.7853 | 0.79233 | 0.78116 | 0.77683 | 0.78147 | 0.79781 | 0.81222 | 0.82881 | 0.84614 | 0.8748 | 0.89642
|  | RK | Maximum demand forecast(peak season) | Maximum demand (MVA) | RKMaximum demand forecast(peak season)Maximum demand (MVA) | 21.6782 | 22.8645 | 23.0691 | 22.744 | 22.6181 | 22.753 | 23.2288 | 23.6482 | 24.1313 | 24.6359 | 25.4703 | 26.1
|  | RK | Maximum demand forecast(peak season) | Power factor (coincident) | RKMaximum demand forecast(peak season)Power factor (coincident) | 0.99941 | 0.99941 | 0.99941 | 0.99941 | 0.99941 | 0.99941 | 0.99941 | 0.99941 | 0.99941 | 0.99941 | 0.99941 | 0.99941
|  | RK | Maximum demand forecast(non-peak season) | Maximum demand (MW) | RKMaximum demand forecast(non-peak season)Maximum demand (MW) | 14.3624 | 13.4037 | 12.6987 | 12.1228 | 11.687 | 11.5103 | 11.5139 | 11.5282 | 11.6011 | 11.7892 | 12.0344 | 12.3032 |  | Summer
|  | RK | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | RKMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 0.083615 | 0.078034 | 0.073929 | 0.070576 | 0.068039 | 0.067011 | 0.067032 | 0.067115 | 0.067539 | 0.068634 | 0.070062 | 0.071627 |  | Summer
|  | RK | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 14.3626 | 13.4039 | 12.6989 | 12.123 | 11.6872 | 11.5105 | 11.5141 | 11.5284 | 11.6013 | 11.7894 | 12.0346 | 12.3035 |  | Summer
|  | RK | Hours exceeding | 95% of maximum demand | RKHours exceeding95% of maximum demand | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
|  | RK | Hours exceeding | Firm capacity (continuous rating) | RKHours exceedingFirm capacity (continuous rating)
|  | RK | Hours exceeding | Firm capacity (short-term rating) | RKHours exceedingFirm capacity (short-term rating)
|  | RK | Regional diversity factor | Summer | RKRegional diversity factorSummer | 0.81879 | 0.81879 | 0.81879 | 0.81879 | 0.81879 | 0.81879 | 0.81879 | 0.81879 | 0.81879 | 0.81879 | 0.81879 | 0.81879
|  | RK | Regional diversity factor | Winter | RKRegional diversity factorWinter | 0.8624 | 0.8624 | 0.8624 | 0.8624 | 0.8624 | 0.8624 | 0.8624 | 0.8624 | 0.8624 | 0.8624 | 0.8624 | 0.8624
|  | RK | Load transfer capacity (MVA) | 1 | RKLoad transfer capacity (MVA)1 | 4.8 | [11 empty] | Cambridge
|  | RK | Load transfer capacity (MVA) | 2 | RKLoad transfer capacity (MVA)2 | 5.8 | [11 empty] | Howrah
|  | RK | Load transfer capacity (MVA) | 3 | RKLoad transfer capacity (MVA)3
|  | RK | Load transfer capacity (MVA) | 4 | RKLoad transfer capacity (MVA)4
|  | RK | Load transfer capacity (MVA) | 5 | RKLoad transfer capacity (MVA)5
|  | RK | Embedded generation capacity (MVA) | Units less than 100 kVA | RKEmbedded generation capacity (MVA)Units less than 100 kVA | 7.1907
|  | RK | Embedded generation capacity (MVA) | Units greater than 100 kVA | RKEmbedded generation capacity (MVA)Units greater than 100 kVA | 0
|  | SD | Substation capacity (winter and summer) (MVA) | Total | SDSubstation capacity (winter and summer) (MVA)Total | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63
|  | SD | Substation capacity (winter and summer) (MVA) | Firm delivery | SDSubstation capacity (winter and summer) (MVA)Firm delivery | 31.5 | 31.5 | 31.5 | 31.5 | 31.5 | 31.5 | 31.5 | 31.5 | 31.5 | 31.5 | 31.5 | 31.5
|  | SD | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | SDSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36
|  | SD | Maximum demand forecast(peak season) | Maximum demand (MW) | SDMaximum demand forecast(peak season)Maximum demand (MW) | 11.889 | 11.7572 | 11.7139 | 11.4179 | 11.255 | 11.3389 | 11.4754 | 11.5805 | 11.7524 | 11.8908 | 12.2263 | 12.4833
|  | SD | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | SDMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 0.035163 | 0.034773 | 0.034645 | 0.03377 | 0.033288 | 0.033536 | 0.03394 | 0.034251 | 0.034759 | 0.035168 | 0.036161 | 0.036921
|  | SD | Maximum demand forecast(peak season) | Maximum demand (MVA) | SDMaximum demand forecast(peak season)Maximum demand (MVA) | 11.889 | 11.7572 | 11.714 | 11.4179 | 11.255 | 11.339 | 11.4754 | 11.5805 | 11.7524 | 11.8908 | 12.2264 | 12.4833
|  | SD | Maximum demand forecast(peak season) | Power factor (coincident) | SDMaximum demand forecast(peak season)Power factor (coincident) | 1 | 1 | bar: 4 2023 to 13 2032
|  | SD | Maximum demand forecast(non-peak season) | Maximum demand (MW) | SDMaximum demand forecast(non-peak season)Maximum demand (MW) | 12.4921 | 12.3721 | 12.0423 | 11.7486 | 11.5144 | 11.6133 | 11.7194 | 11.7952 | 11.9316 | 12.0703 | 12.2435 | 12.4503 |  | Summer
|  | SD | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | SDMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 2.3814 | 2.3585 | 2.2956 | 2.2396 | 2.195 | 2.2138 | 2.2341 | 2.2485 | 2.2745 | 2.301 | 2.334 | 2.3734 |  | Summer
|  | SD | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 12.717 | 12.5948 | 12.2591 | 11.9601 | 11.7217 | 11.8224 | 11.9304 | 12.0076 | 12.1465 | 12.2877 | 12.464 | 12.6745 |  | Summer
|  | SD | Hours exceeding | 95% of maximum demand | SDHours exceeding95% of maximum demand | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
|  | SD | Hours exceeding | Firm capacity (continuous rating) | SDHours exceedingFirm capacity (continuous rating)
|  | SD | Hours exceeding | Firm capacity (short-term rating) | SDHours exceedingFirm capacity (short-term rating)
|  | SD | Regional diversity factor | Summer | SDRegional diversity factorSummer | 0.76872 | 0.76872 | 0.76872 | 0.76872 | 0.76872 | 0.76872 | 0.76872 | 0.76872 | 0.76872 | 0.76872 | 0.76872 | 0.76872
|  | SD | Regional diversity factor | Winter | SDRegional diversity factorWinter | 1 | 1 | bar: 4 2023 to 13 2032
|  | SD | Load transfer capacity (MVA) | 1 | SDLoad transfer capacity (MVA)1 | 4.8 | [11 empty] | Derby
|  | SD | Load transfer capacity (MVA) | 2 | SDLoad transfer capacity (MVA)2 | 3.2 | [11 empty] | George Town
|  | SD | Load transfer capacity (MVA) | 3 | SDLoad transfer capacity (MVA)3 | 2.1 | [11 empty] | Trevallyn
|  | SD | Load transfer capacity (MVA) | 4 | SDLoad transfer capacity (MVA)4
|  | SD | Load transfer capacity (MVA) | 5 | SDLoad transfer capacity (MVA)5
|  | SD | Embedded generation capacity (MVA) | Units less than 100 kVA | SDEmbedded generation capacity (MVA)Units less than 100 kVA | 4.8918
|  | SD | Embedded generation capacity (MVA) | Units greater than 100 kVA | SDEmbedded generation capacity (MVA)Units greater than 100 kVA | 1.89
|  | SL | Substation capacity (winter and summer) (MVA) | Total | SLSubstation capacity (winter and summer) (MVA)Total | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
|  | SL | Substation capacity (winter and summer) (MVA) | Firm delivery | SLSubstation capacity (winter and summer) (MVA)Firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  | SL | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | SLSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77
|  | SL | Maximum demand forecast(peak season) | Maximum demand (MW) | SLMaximum demand forecast(peak season)Maximum demand (MW) | 23.7352 | 31.164 | 30.8905 | 30.2488 | 29.8933 | 29.7295 | 30.0188 | 30.2206 | 30.4894 | 30.6153 | 31.1633 | 31.3662
|  | SL | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | SLMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 1.0964 | 1.4396 | 1.4269 | 1.3973 | 1.3809 | 1.3733 | 1.3867 | 1.396 | 1.4084 | 1.4142 | 1.4395 | 1.4489
|  | SL | Maximum demand forecast(peak season) | Maximum demand (MVA) | SLMaximum demand forecast(peak season)Maximum demand (MVA) | 23.7605 | 31.1972 | 30.9234 | 30.2811 | 29.9252 | 29.7612 | 30.0508 | 30.2528 | 30.5219 | 30.6479 | 31.1965 | 31.3996
|  | SL | Maximum demand forecast(peak season) | Power factor (coincident) | SLMaximum demand forecast(peak season)Power factor (coincident) | 0.99893 | 0.99893 | 0.99893 | 0.99893 | 0.99893 | 0.99893 | 0.99893 | 0.99893 | 0.99893 | 0.99893 | 0.99893 | 0.99893
|  | SL | Maximum demand forecast(non-peak season) | Maximum demand (MW) | SLMaximum demand forecast(non-peak season)Maximum demand (MW) | 19.1756 | 36.3181 | 34.8065 | 34.091 | 33.5128 | 33.3066 | 33.5498 | 33.702 | 33.9761 | 34.1421 | 34.3945 | 34.4605 |  | Summer
|  | SL | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | SLMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 0.35344 | 0.6694 | 0.64154 | 0.62836 | 0.6177 | 0.6139 | 0.61838 | 0.62119 | 0.62624 | 0.6293 | 0.63395 | 0.63517 |  | Summer
|  | SL | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 19.1789 | 36.3243 | 34.8125 | 34.0968 | 33.5185 | 33.3122 | 33.5555 | 33.7078 | 33.9819 | 34.1479 | 34.4003 | 34.4663 |  | Summer
|  | SL | Hours exceeding | 95% of maximum demand | SLHours exceeding95% of maximum demand | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5
|  | SL | Hours exceeding | Firm capacity (continuous rating) | SLHours exceedingFirm capacity (continuous rating)
|  | SL | Hours exceeding | Firm capacity (short-term rating) | SLHours exceedingFirm capacity (short-term rating)
|  | SL | Regional diversity factor | Summer | SLRegional diversity factorSummer | 0.65982 | 0.65982 | 0.65982 | 0.65982 | 0.65982 | 0.65982 | 0.65982 | 0.65982 | 0.65982 | 0.65982 | 0.65982 | 0.65982
|  | SL | Regional diversity factor | Winter | SLRegional diversity factorWinter | 0.9316 | 0.9316 | 0.9316 | 0.9316 | 0.9316 | 0.9316 | 0.9316 | 0.9316 | 0.9316 | 0.9316 | 0.9316 | 0.9316
|  | SL | Load transfer capacity (MVA) | 1 | SLLoad transfer capacity (MVA)1 | 3 | [11 empty] | Mowbray
|  | SL | Load transfer capacity (MVA) | 2 | SLLoad transfer capacity (MVA)2 | 10 | [11 empty] | Norwood
|  | SL | Load transfer capacity (MVA) | 3 | SLLoad transfer capacity (MVA)3 | 3 | [11 empty] | Trevallyn
|  | SL | Load transfer capacity (MVA) | 4 | SLLoad transfer capacity (MVA)4
|  | SL | Load transfer capacity (MVA) | 5 | SLLoad transfer capacity (MVA)5
|  | SL | Embedded generation capacity (MVA) | Units less than 100 kVA | SLEmbedded generation capacity (MVA)Units less than 100 kVA | 5.9534
|  | SL | Embedded generation capacity (MVA) | Units greater than 100 kVA | SLEmbedded generation capacity (MVA)Units greater than 100 kVA | 0
|  | SM | Substation capacity (winter and summer) (MVA) | Total | SMSubstation capacity (winter and summer) (MVA)Total | 20 | 20 | 20 | 20 | 20 | 20 | 50 | 50 | 50 | 50 | 50 | 50
|  | SM | Substation capacity (winter and summer) (MVA) | Firm delivery | SMSubstation capacity (winter and summer) (MVA)Firm delivery | 10 | 10 | 10 | 10 | 10 | 10 | 25[1] | 25 | 25 | 25 | 25 | 25
|  | SM | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | SMSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 12 | 12 | 12 | 12 | 12 | 12 | 30 | 30 | 30 | 30 | 30 | 30
|  | SM | Maximum demand forecast(peak season) | Maximum demand (MW) | SMMaximum demand forecast(peak season)Maximum demand (MW) | 15.0979 | 17.166 | 17.2776 | 16.9626 | 16.78 | 16.7012 | 16.8888 | 17.0174 | 17.1983 | 17.3321 | 17.7096 | 17.9428
|  | SM | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | SMMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 0.63288 | 0.71957 | 0.72425 | 0.71104 | 0.70339 | 0.70008 | 0.70795 | 0.71334 | 0.72092 | 0.72653 | 0.74235 | 0.75213
|  | SM | Maximum demand forecast(peak season) | Maximum demand (MVA) | SMMaximum demand forecast(peak season)Maximum demand (MVA) | 15.1112 | 17.1811 | 17.2928 | 16.9775 | 16.7947 | 16.7159 | 16.9037 | 17.0323 | 17.2134 | 17.3474 | 17.7252 | 17.9586
|  | SM | Maximum demand forecast(peak season) | Power factor (coincident) | SMMaximum demand forecast(peak season)Power factor (coincident) | 0.99912 | 0.99912 | 0.99912 | 0.99912 | 0.99912 | 0.99912 | 0.99912 | 0.99912 | 0.99912 | 0.99912 | 0.99912 | 0.99912
|  | SM | Maximum demand forecast(non-peak season) | Maximum demand (MW) | SMMaximum demand forecast(non-peak season)Maximum demand (MW) | 10.7192 | 11.0894 | 10.7116 | 10.4131 | 10.1477 | 10.0107 | 10.013 | 9.9967 | 10.024 | 10.0686 | 10.1487 | 10.2285 |  | Summer
|  | SM | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | SMMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 0.99562 | 1.03 | 0.99492 | 0.96719 | 0.94254 | 0.92982 | 0.93003 | 0.92852 | 0.93105 | 0.93519 | 0.94263 | 0.95005 |  | Summer
|  | SM | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 10.7653 | 11.1371 | 10.7577 | 10.4579 | 10.1914 | 10.0538 | 10.0561 | 10.0398 | 10.0671 | 10.1119 | 10.1924 | 10.2725 |  | Summer
|  | SM | Hours exceeding | 95% of maximum demand | SMHours exceeding95% of maximum demand | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
|  | SM | Hours exceeding | Firm capacity (continuous rating) | SMHours exceedingFirm capacity (continuous rating)
|  | SM | Hours exceeding | Firm capacity (short-term rating) | SMHours exceedingFirm capacity (short-term rating)
|  | SM | Regional diversity factor | Summer | SMRegional diversity factorSummer | 0.63105 | 0.63105 | 0.63105 | 0.63105 | 0.63105 | 0.63105 | 0.63105 | 0.63105 | 0.63105 | 0.63105 | 0.63105 | 0.63105
|  | SM | Regional diversity factor | Winter | SMRegional diversity factorWinter | 0.75654 | 0.75654 | 0.75654 | 0.75654 | 0.75654 | 0.75654 | 0.75654 | 0.75654 | 0.75654 | 0.75654 | 0.75654 | 0.75654
|  | SM | Load transfer capacity (MVA) | 1 | SMLoad transfer capacity (MVA)1 | 2.8 | [11 empty] | Avoca
|  | SM | Load transfer capacity (MVA) | 2 | SMLoad transfer capacity (MVA)2 | 4 | [11 empty] | Derby
|  | SM | Load transfer capacity (MVA) | 3 | SMLoad transfer capacity (MVA)3 | 4.5 | [11 empty] | Triabunna
|  | SM | Load transfer capacity (MVA) | 4 | SMLoad transfer capacity (MVA)4
|  | SM | Load transfer capacity (MVA) | 5 | SMLoad transfer capacity (MVA)5
|  | SM | Embedded generation capacity (MVA) | Units less than 100 kVA | SMEmbedded generation capacity (MVA)Units less than 100 kVA | 6.2124
|  | SM | Embedded generation capacity (MVA) | Units greater than 100 kVA | SMEmbedded generation capacity (MVA)Units greater than 100 kVA | 0
|  | SO | Substation capacity (winter and summer) (MVA) | Total | SOSubstation capacity (winter and summer) (MVA)Total | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
|  | SO | Substation capacity (winter and summer) (MVA) | Firm delivery | SOSubstation capacity (winter and summer) (MVA)Firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  | SO | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | SOSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61
|  | SO | Maximum demand forecast(peak season) | Maximum demand (MW) | SOMaximum demand forecast(peak season)Maximum demand (MW) | 34.9526 | 37.4978 | 38.0792 | 38.8537 | 39.1968 | 39.3632 | 39.9656 | 40.3804 | 40.9158 | 41.3741 | 42.4227 | 43.0846
|  | SO | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | SOMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 0.22481 | 0.24118 | 0.24492 | 0.2499 | 0.25211 | 0.25318 | 0.25706 | 0.25972 | 0.26317 | 0.26612 | 0.27286 | 0.27712
|  | SO | Maximum demand forecast(peak season) | Maximum demand (MVA) | SOMaximum demand forecast(peak season)Maximum demand (MVA) | 34.9534 | 37.4986 | 38.08 | 38.8545 | 39.1976 | 39.364 | 39.9664 | 40.3812 | 40.9167 | 41.3749 | 42.4236 | 43.0855
|  | SO | Maximum demand forecast(peak season) | Power factor (coincident) | SOMaximum demand forecast(peak season)Power factor (coincident) | 0.99998 | 0.99998 | 0.99998 | 0.99998 | 0.99998 | 0.99998 | 0.99998 | 0.99998 | 0.99998 | 0.99998 | 0.99998 | 0.99998
|  | SO | Maximum demand forecast(non-peak season) | Maximum demand (MW) | SOMaximum demand forecast(non-peak season)Maximum demand (MW) | 23.1326 | 23.6982 | 23.4565 | 24.4295 | 24.7411 | 24.9145 | 25.238 | 25.4428 | 25.7436 | 26.0853 | 26.5141 | 26.9055 |  | Summer
|  | SO | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | SOMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 0.28605 | 0.29304 | 0.29005 | 0.30208 | 0.30594 | 0.30808 | 0.31208 | 0.31461 | 0.31833 | 0.32256 | 0.32786 | 0.3327 |  | Summer
|  | SO | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 23.1344 | 23.7 | 23.4583 | 24.4314 | 24.743 | 24.9164 | 25.24 | 25.4448 | 25.7455 | 26.0873 | 26.5161 | 26.9075 |  | Summer
|  | SO | Hours exceeding | 95% of maximum demand | SOHours exceeding95% of maximum demand | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
|  | SO | Hours exceeding | Firm capacity (continuous rating) | SOHours exceedingFirm capacity (continuous rating)
|  | SO | Hours exceeding | Firm capacity (short-term rating) | SOHours exceedingFirm capacity (short-term rating)
|  | SO | Regional diversity factor | Summer | SORegional diversity factorSummer | 0.77083 | 0.77083 | 0.77083 | 0.77083 | 0.77083 | 0.77083 | 0.77083 | 0.77083 | 0.77083 | 0.77083 | 0.77083 | 0.77083
|  | SO | Regional diversity factor | Winter | SORegional diversity factorWinter | 0.92281 | 0.92281 | 0.92281 | 0.92281 | 0.92281 | 0.92281 | 0.92281 | 0.92281 | 0.92281 | 0.92281 | 0.92281 | 0.92281
|  | SO | Load transfer capacity (MVA) | 1 | SOLoad transfer capacity (MVA)1 | 1.5 | [11 empty] | Avoca
|  | SO | Load transfer capacity (MVA) | 2 | SOLoad transfer capacity (MVA)2 | 1.5 | [11 empty] | Meadowbank
|  | SO | Load transfer capacity (MVA) | 3 | SOLoad transfer capacity (MVA)3 | 1.5 | [11 empty] | Triabunna
|  | SO | Load transfer capacity (MVA) | 4 | SOLoad transfer capacity (MVA)4
|  | SO | Load transfer capacity (MVA) | 5 | SOLoad transfer capacity (MVA)5
|  | SO | Embedded generation capacity (MVA) | Units less than 100 kVA | SOEmbedded generation capacity (MVA)Units less than 100 kVA | 12.6619
|  | SO | Embedded generation capacity (MVA) | Units greater than 100 kVA | SOEmbedded generation capacity (MVA)Units greater than 100 kVA | 1.067
|  | SR | Substation capacity (winter and summer) (MVA) | Total | SRSubstation capacity (winter and summer) (MVA)Total | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 50 | 50 | 50 | 50
|  | SR | Substation capacity (winter and summer) (MVA) | Firm delivery | SRSubstation capacity (winter and summer) (MVA)Firm delivery | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 25[2] | 25[2] | 25 | 25
|  | SR | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | SRSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 30 | 30 | 30 | 30
|  | SR | Maximum demand forecast(peak season) | Maximum demand (MW) | SRMaximum demand forecast(peak season)Maximum demand (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | SR | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | SRMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 24.3329 | 23.3432 | 25.5383 | 25.5158 | 25.5064 | 25.4986 | 25.5108 | 25.5195 | 25.533 | 25.5376 | 30.444 | 30.448
|  | SR | Maximum demand forecast(peak season) | Maximum demand (MVA) | SRMaximum demand forecast(peak season)Maximum demand (MVA) | 24.3329 | 23.3432 | 25.5383 | 25.5158 | 25.5064 | 25.4986 | 25.5108 | 25.5195 | 25.533 | 25.5376 | 30.444 | 30.448
|  | SR | Maximum demand forecast(peak season) | Power factor (coincident) | SRMaximum demand forecast(peak season)Power factor (coincident) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | SR | Maximum demand forecast(non-peak season) | Maximum demand (MW) | SRMaximum demand forecast(non-peak season)Maximum demand (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Summer
|  | SR | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | SRMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 22.9611 | 23.1001 | 25.2805 | 25.2588 | 25.2428 | 25.2341 | 25.2373 | 25.2391 | 25.2449 | 25.2482 | 30.1519 | 30.1534 |  | Summer
|  | SR | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 22.9611 | 23.1001 | 25.2805 | 25.2588 | 25.2428 | 25.2341 | 25.2373 | 25.2391 | 25.2449 | 25.2482 | 30.1519 | 30.1534 |  | Summer
|  | SR | Hours exceeding | 95% of maximum demand | SRHours exceeding95% of maximum demand | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  | SR | Hours exceeding | Firm capacity (continuous rating) | SRHours exceedingFirm capacity (continuous rating)
|  | SR | Hours exceeding | Firm capacity (short-term rating) | SRHours exceedingFirm capacity (short-term rating)
|  | SR | Regional diversity factor | Summer | SRRegional diversity factorSummer | 0.79167 | 0.79167 | 0.79167 | 0.79167 | 0.79167 | 0.79167 | 0.79167 | 0.79167 | 0.79167 | 0.79167 | 0.79167 | 0.79167
|  | SR | Regional diversity factor | Winter | SRRegional diversity factorWinter | -0.17391 | -0.17391 | -0.17391 | -0.17391 | -0.17391 | -0.17391 | -0.17391 | -0.17391 | -0.17391 | -0.17391 | -0.17391 | -0.17391
|  | SR | Load transfer capacity (MVA) | 1 | SRLoad transfer capacity (MVA)1
|  | SR | Load transfer capacity (MVA) | 2 | SRLoad transfer capacity (MVA)2
|  | SR | Load transfer capacity (MVA) | 3 | SRLoad transfer capacity (MVA)3
|  | SR | Load transfer capacity (MVA) | 4 | SRLoad transfer capacity (MVA)4
|  | SR | Load transfer capacity (MVA) | 5 | SRLoad transfer capacity (MVA)5
|  | SR | Embedded generation capacity (MVA) | Units less than 100 kVA | SREmbedded generation capacity (MVA)Units less than 100 kVA | 0.19812
|  | SR | Embedded generation capacity (MVA) | Units greater than 100 kVA | SREmbedded generation capacity (MVA)Units greater than 100 kVA | 0
|  | ST | Substation capacity (winter and summer) (MVA) | Total | STSubstation capacity (winter and summer) (MVA)Total | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
|  | ST | Substation capacity (winter and summer) (MVA) | Firm delivery | STSubstation capacity (winter and summer) (MVA)Firm delivery | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
|  | ST | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | STSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42
|  | ST | Maximum demand forecast(peak season) | Maximum demand (MW) | STMaximum demand forecast(peak season)Maximum demand (MW) | 19.646 | 21.4091 | 22.7895 | 22.9876 | 23.0115 | 22.9398 | 23.2186 | 23.3937 | 23.6519 | 23.773 | 24.2515 | 24.4967
|  | ST | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | STMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 4.0645 | 4.4292 | 4.7148 | 4.7558 | 4.7608 | 4.7459 | 4.8036 | 4.8398 | 4.8932 | 4.9183 | 5.0173 | 5.068
|  | ST | Maximum demand forecast(peak season) | Maximum demand (MVA) | STMaximum demand forecast(peak season)Maximum demand (MVA) | 20.062 | 21.8625 | 23.2722 | 23.4744 | 23.4989 | 23.4256 | 23.7103 | 23.8891 | 24.1527 | 24.2765 | 24.7651 | 25.0154
|  | ST | Maximum demand forecast(peak season) | Power factor (coincident) | STMaximum demand forecast(peak season)Power factor (coincident) | 0.97926 | 0.97926 | 0.97926 | 0.97926 | 0.97926 | 0.97926 | 0.97926 | 0.97926 | 0.97926 | 0.97926 | 0.97926 | 0.97926
|  | ST | Maximum demand forecast(non-peak season) | Maximum demand (MW) | STMaximum demand forecast(non-peak season)Maximum demand (MW) | 23.3627 | 24.2787 | 25.1565 | 25.4082 | 25.3327 | 25.3452 | 25.6509 | 25.8448 | 26.1386 | 26.3573 | 26.6146 | 26.8606 |  | Summer
|  | ST | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | STMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 6.8813 | 7.1511 | 7.4097 | 7.4838 | 7.4616 | 7.4652 | 7.5553 | 7.6124 | 7.6989 | 7.7634 | 7.8392 | 7.9116 |  | Summer
|  | ST | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 24.355 | 25.3099 | 26.2251 | 26.4874 | 26.4087 | 26.4217 | 26.7404 | 26.9425 | 27.2489 | 27.4768 | 27.7451 | 28.0015 |  | Summer
|  | ST | Hours exceeding | 95% of maximum demand | STHours exceeding95% of maximum demand | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5
|  | ST | Hours exceeding | Firm capacity (continuous rating) | STHours exceedingFirm capacity (continuous rating)
|  | ST | Hours exceeding | Firm capacity (short-term rating) | STHours exceedingFirm capacity (short-term rating)
|  | ST | Regional diversity factor | Summer | STRegional diversity factorSummer | 0.87291 | 0.87291 | 0.87291 | 0.87291 | 0.87291 | 0.87291 | 0.87291 | 0.87291 | 0.87291 | 0.87291 | 0.87291 | 0.87291
|  | ST | Regional diversity factor | Winter | STRegional diversity factorWinter | 0.79216 | 0.79216 | 0.79216 | 0.79216 | 0.79216 | 0.79216 | 0.79216 | 0.79216 | 0.79216 | 0.79216 | 0.79216 | 0.79216
|  | ST | Load transfer capacity (MVA) | 1 | STLoad transfer capacity (MVA)1 | 5.1 | [11 empty] | Port Latta
|  | ST | Load transfer capacity (MVA) | 2 | STLoad transfer capacity (MVA)2
|  | ST | Load transfer capacity (MVA) | 3 | STLoad transfer capacity (MVA)3
|  | ST | Load transfer capacity (MVA) | 4 | STLoad transfer capacity (MVA)4
|  | ST | Load transfer capacity (MVA) | 5 | STLoad transfer capacity (MVA)5
|  | ST | Embedded generation capacity (MVA) | Units less than 100 kVA | STEmbedded generation capacity (MVA)Units less than 100 kVA | 3.3141
|  | ST | Embedded generation capacity (MVA) | Units greater than 100 kVA | STEmbedded generation capacity (MVA)Units greater than 100 kVA | 1.1333
|  | TB | Substation capacity (winter and summer) (MVA) | Total | TBSubstation capacity (winter and summer) (MVA)Total | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
|  | TB | Substation capacity (winter and summer) (MVA) | Firm delivery | TBSubstation capacity (winter and summer) (MVA)Firm delivery | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
|  | TB | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | TBSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
|  | TB | Maximum demand forecast(peak season) | Maximum demand (MW) | TBMaximum demand forecast(peak season)Maximum demand (MW) | 7.8426 | 9.0762 | 9.1933 | 9.2029 | 9.1935 | 9.1834 | 9.3127 | 9.4109 | 9.5514 | 9.6738 | 9.9467 | 10.1283
|  | TB | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | TBMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 0.0015794 | 0.0018278 | 0.0018514 | 0.0018534 | 0.0018515 | 0.0018494 | 0.0018755 | 0.0018953 | 0.0019236 | 0.0019482 | 0.0020032 | 0.0020397
|  | TB | Maximum demand forecast(peak season) | Maximum demand (MVA) | TBMaximum demand forecast(peak season)Maximum demand (MVA) | 7.8426 | 9.0762 | 9.1933 | 9.2029 | 9.1935 | 9.1834 | 9.3127 | 9.4109 | 9.5514 | 9.6738 | 9.9467 | 10.1283
|  | TB | Maximum demand forecast(peak season) | Power factor (coincident) | TBMaximum demand forecast(peak season)Power factor (coincident) | 1 | 1 | bar: 4 2023 to 13 2032
|  | TB | Maximum demand forecast(non-peak season) | Maximum demand (MW) | TBMaximum demand forecast(non-peak season)Maximum demand (MW) | 6.0711 | 5.7971 | 5.7707 | 5.8635 | 5.8758 | 5.9039 | 5.994 | 6.069 | 6.1705 | 6.2866 | 6.4299 | 6.565 |  | Summer
|  | TB | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | TBMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 0.72003 | 0.68754 | 0.6844 | 0.69541 | 0.69687 | 0.7002 | 0.71089 | 0.71979 | 0.73182 | 0.74559 | 0.76259 | 0.77861 |  | Summer
|  | TB | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 6.1136 | 5.8378 | 5.8111 | 5.9046 | 5.917 | 5.9452 | 6.036 | 6.1116 | 6.2137 | 6.3307 | 6.475 | 6.611 |  | Summer
|  | TB | Hours exceeding | 95% of maximum demand | TBHours exceeding95% of maximum demand | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
|  | TB | Hours exceeding | Firm capacity (continuous rating) | TBHours exceedingFirm capacity (continuous rating)
|  | TB | Hours exceeding | Firm capacity (short-term rating) | TBHours exceedingFirm capacity (short-term rating)
|  | TB | Regional diversity factor | Summer | TBRegional diversity factorSummer | 0.662 | 0.662 | 0.662 | 0.662 | 0.662 | 0.662 | 0.662 | 0.662 | 0.662 | 0.662 | 0.662 | 0.662
|  | TB | Regional diversity factor | Winter | TBRegional diversity factorWinter | 0.82309 | 0.82309 | 0.82309 | 0.82309 | 0.82309 | 0.82309 | 0.82309 | 0.82309 | 0.82309 | 0.82309 | 0.82309 | 0.82309
|  | TB | Load transfer capacity (MVA) | 1 | TBLoad transfer capacity (MVA)1 | 3 | [11 empty] | St Marys
|  | TB | Load transfer capacity (MVA) | 2 | TBLoad transfer capacity (MVA)2 | 1.8 | [11 empty] | Sorell
|  | TB | Load transfer capacity (MVA) | 3 | TBLoad transfer capacity (MVA)3
|  | TB | Load transfer capacity (MVA) | 4 | TBLoad transfer capacity (MVA)4
|  | TB | Load transfer capacity (MVA) | 5 | TBLoad transfer capacity (MVA)5
|  | TB | Embedded generation capacity (MVA) | Units less than 100 kVA | TBEmbedded generation capacity (MVA)Units less than 100 kVA | 2.9445
|  | TB | Embedded generation capacity (MVA) | Units greater than 100 kVA | TBEmbedded generation capacity (MVA)Units greater than 100 kVA | 0
|  | TR | Substation capacity (winter and summer) (MVA) | Total | TRSubstation capacity (winter and summer) (MVA)Total | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
|  | TR | Substation capacity (winter and summer) (MVA) | Firm delivery | TRSubstation capacity (winter and summer) (MVA)Firm delivery | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
|  | TR | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | TRSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130
|  | TR | Maximum demand forecast(peak season) | Maximum demand (MW) | TRMaximum demand forecast(peak season)Maximum demand (MW) | 68.7474 | 71.3185 | 70.6338 | 69.5668 | 68.9002 | 68.5953 | 69.2318 | 69.648 | 70.2338 | 70.5642 | 71.8643 | 72.4594
|  | TR | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | TRMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 0.88769 | 0.92089 | 0.91205 | 0.89827 | 0.88966 | 0.88573 | 0.89394 | 0.89932 | 0.90688 | 0.91115 | 0.92794 | 0.93562
|  | TR | Maximum demand forecast(peak season) | Maximum demand (MVA) | TRMaximum demand forecast(peak season)Maximum demand (MVA) | 68.7532 | 71.3244 | 70.6397 | 69.5726 | 68.9059 | 68.601 | 69.2376 | 69.6539 | 70.2397 | 70.5701 | 71.8702 | 72.4654
|  | TR | Maximum demand forecast(peak season) | Power factor (coincident) | TRMaximum demand forecast(peak season)Power factor (coincident) | 0.99992 | 0.99992 | 0.99992 | 0.99992 | 0.99992 | 0.99992 | 0.99992 | 0.99992 | 0.99992 | 0.99992 | 0.99992 | 0.99992
|  | TR | Maximum demand forecast(non-peak season) | Maximum demand (MW) | TRMaximum demand forecast(non-peak season)Maximum demand (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Summer
|  | TR | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | TRMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 38.8026 | 38.6613 | 37.1623 | 36.7065 | 36.0912 | 35.8842 | 36.0529 | 36.1513 | 36.3832 | 36.7016 | 37.103 | 37.5277 |  | Summer
|  | TR | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 38.8026 | 38.6613 | 37.1623 | 36.7065 | 36.0912 | 35.8842 | 36.0529 | 36.1513 | 36.3832 | 36.7016 | 37.103 | 37.5277 |  | Summer
|  | TR | Hours exceeding | 95% of maximum demand | TRHours exceeding95% of maximum demand | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5
|  | TR | Hours exceeding | Firm capacity (continuous rating) | TRHours exceedingFirm capacity (continuous rating)
|  | TR | Hours exceeding | Firm capacity (short-term rating) | TRHours exceedingFirm capacity (short-term rating)
|  | TR | Regional diversity factor | Summer | TRRegional diversity factorSummer | 0.88594 | 0.88594 | 0.88594 | 0.88594 | 0.88594 | 0.88594 | 0.88594 | 0.88594 | 0.88594 | 0.88594 | 0.88594 | 0.88594
|  | TR | Regional diversity factor | Winter | TRRegional diversity factorWinter | 0.92367 | 0.92367 | 0.92367 | 0.92367 | 0.92367 | 0.92367 | 0.92367 | 0.92367 | 0.92367 | 0.92367 | 0.92367 | 0.92367
|  | TR | Load transfer capacity (MVA) | 1 | TRLoad transfer capacity (MVA)1 | 3.6 | [11 empty] | George Town
|  | TR | Load transfer capacity (MVA) | 2 | TRLoad transfer capacity (MVA)2 | 14.4 | [11 empty] | Hadspen
|  | TR | Load transfer capacity (MVA) | 3 | TRLoad transfer capacity (MVA)3 | 36.1 | [11 empty] | Mowbray
|  | TR | Load transfer capacity (MVA) | 4 | TRLoad transfer capacity (MVA)4 | 21.7 | [11 empty] | Norwood
|  | TR | Load transfer capacity (MVA) | 5 | TRLoad transfer capacity (MVA)5 | 21.7 | [11 empty] | St Leonards
|  | TR | Embedded generation capacity (MVA) | Units less than 100 kVA | TREmbedded generation capacity (MVA)Units less than 100 kVA | 20.6073
|  | TR | Embedded generation capacity (MVA) | Units greater than 100 kVA | TREmbedded generation capacity (MVA)Units greater than 100 kVA | 2
|  | TU | Substation capacity (winter and summer) (MVA) | Total | TUSubstation capacity (winter and summer) (MVA)Total | 13[1] | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
|  | TU | Substation capacity (winter and summer) (MVA) | Firm delivery | TUSubstation capacity (winter and summer) (MVA)Firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | TU | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | TUSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | TU | Maximum demand forecast(peak season) | Maximum demand (MW) | TUMaximum demand forecast(peak season)Maximum demand (MW) | 1.1388 | 1.0108 | 1.0203 | 1.006 | 1.0013 | 1.0033 | 1.0226 | 1.0384 | 1.0577 | 1.0736 | 1.105 | 1.1277
|  | TU | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | TUMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 0.20177 | 0.17909 | 0.18077 | 0.17823 | 0.1774 | 0.17776 | 0.18118 | 0.18398 | 0.1874 | 0.19021 | 0.19578 | 0.19981
|  | TU | Maximum demand forecast(peak season) | Maximum demand (MVA) | TUMaximum demand forecast(peak season)Maximum demand (MVA) | 1.1565 | 1.0265 | 1.0362 | 1.0216 | 1.0169 | 1.0189 | 1.0385 | 1.0546 | 1.0742 | 1.0903 | 1.1222 | 1.1453
|  | TU | Maximum demand forecast(peak season) | Power factor (coincident) | TUMaximum demand forecast(peak season)Power factor (coincident) | 0.98466 | 0.98466 | 0.98466 | 0.98466 | 0.98466 | 0.98466 | 0.98466 | 0.98466 | 0.98466 | 0.98466 | 0.98466 | 0.98466
|  | TU | Maximum demand forecast(non-peak season) | Maximum demand (MW) | TUMaximum demand forecast(non-peak season)Maximum demand (MW) | 0.70339 | 0.74848 | 0.73044 | 0.71522 | 0.70394 | 0.70275 | 0.71177 | 0.71896 | 0.72924 | 0.74036 | 0.75361 | 0.76824 |  | Summer
|  | TU | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | TUMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 0.040785 | 0.043399 | 0.042354 | 0.041471 | 0.040817 | 0.040748 | 0.041271 | 0.041688 | 0.042284 | 0.042929 | 0.043697 | 0.044545 |  | Summer
|  | TU | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 0.70458 | 0.74973 | 0.73167 | 0.71642 | 0.70512 | 0.70393 | 0.71297 | 0.72017 | 0.73047 | 0.7416 | 0.75488 | 0.76953 |  | Summer
|  | TU | Hours exceeding | 95% of maximum demand | TUHours exceeding95% of maximum demand | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5
|  | TU | Hours exceeding | Firm capacity (continuous rating) | TUHours exceedingFirm capacity (continuous rating) | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760
|  | TU | Hours exceeding | Firm capacity (short-term rating) | TUHours exceedingFirm capacity (short-term rating) | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760
|  | TU | Regional diversity factor | Summer | TURegional diversity factorSummer | 0.61017 | 0.61017 | 0.61017 | 0.61017 | 0.61017 | 0.61017 | 0.61017 | 0.61017 | 0.61017 | 0.61017 | 0.61017 | 0.61017
|  | TU | Regional diversity factor | Winter | TURegional diversity factorWinter | 0.83333 | 0.83333 | 0.83333 | 0.83333 | 0.83333 | 0.83333 | 0.83333 | 0.83333 | 0.83333 | 0.83333 | 0.83333 | 0.83333
|  | TU | Load transfer capacity (MVA) | 1 | TULoad transfer capacity (MVA)1
|  | TU | Load transfer capacity (MVA) | 2 | TULoad transfer capacity (MVA)2
|  | TU | Load transfer capacity (MVA) | 3 | TULoad transfer capacity (MVA)3
|  | TU | Load transfer capacity (MVA) | 4 | TULoad transfer capacity (MVA)4
|  | TU | Load transfer capacity (MVA) | 5 | TULoad transfer capacity (MVA)5
|  | TU | Embedded generation capacity (MVA) | Units less than 100 kVA | TUEmbedded generation capacity (MVA)Units less than 100 kVA | 0.0657
|  | TU | Embedded generation capacity (MVA) | Units greater than 100 kVA | TUEmbedded generation capacity (MVA)Units greater than 100 kVA | 0
|  | UL | Substation capacity (winter and summer) (MVA) | Total | ULSubstation capacity (winter and summer) (MVA)Total | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
|  | UL | Substation capacity (winter and summer) (MVA) | Firm delivery | ULSubstation capacity (winter and summer) (MVA)Firm delivery | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
|  | UL | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | ULSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54
|  | UL | Maximum demand forecast(peak season) | Maximum demand (MW) | ULMaximum demand forecast(peak season)Maximum demand (MW) | 32.1449 | 31.413 | 31.4189 | 30.875 | 30.5323 | 30.3636 | 30.6814 | 30.9119 | 31.2463 | 31.4904 | 32.2099 | 32.605
|  | UL | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | ULMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 0.019434 | 0.018991 | 0.018995 | 0.018666 | 0.018459 | 0.018357 | 0.018549 | 0.018689 | 0.018891 | 0.019038 | 0.019473 | 0.019712
|  | UL | Maximum demand forecast(peak season) | Maximum demand (MVA) | ULMaximum demand forecast(peak season)Maximum demand (MVA) | 32.1449 | 31.413 | 31.4189 | 30.875 | 30.5323 | 30.3636 | 30.6814 | 30.9119 | 31.2463 | 31.4904 | 32.2099 | 32.605
|  | UL | Maximum demand forecast(peak season) | Power factor (coincident) | ULMaximum demand forecast(peak season)Power factor (coincident) | 1 | 1 | bar: 4 2023 to 13 2032
|  | UL | Maximum demand forecast(non-peak season) | Maximum demand (MW) | ULMaximum demand forecast(non-peak season)Maximum demand (MW) | 23.1136 | 19.017 | 18.26 | 17.6394 | 17.0603 | 16.7292 | 16.6369 | 16.5286 | 16.5022 | 16.5325 | 16.6353 | 16.7459 |  | Summer
|  | UL | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | ULMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 2.1163 | 1.7412 | 1.6719 | 1.6151 | 1.562 | 1.5317 | 1.5233 | 1.5133 | 1.5109 | 1.5137 | 1.5231 | 1.5332 |  | Summer
|  | UL | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 23.2102 | 19.0966 | 18.3364 | 17.7131 | 17.1317 | 16.7992 | 16.7065 | 16.5977 | 16.5712 | 16.6017 | 16.7049 | 16.8159 |  | Summer
|  | UL | Hours exceeding | 95% of maximum demand | ULHours exceeding95% of maximum demand | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  | UL | Hours exceeding | Firm capacity (continuous rating) | ULHours exceedingFirm capacity (continuous rating)
|  | UL | Hours exceeding | Firm capacity (short-term rating) | ULHours exceedingFirm capacity (short-term rating)
|  | UL | Regional diversity factor | Summer | ULRegional diversity factorSummer | 0.67998 | 0.67998 | 0.67998 | 0.67998 | 0.67998 | 0.67998 | 0.67998 | 0.67998 | 0.67998 | 0.67998 | 0.67998 | 0.67998
|  | UL | Regional diversity factor | Winter | ULRegional diversity factorWinter | 0.84857 | 0.84857 | 0.84857 | 0.84857 | 0.84857 | 0.84857 | 0.84857 | 0.84857 | 0.84857 | 0.84857 | 0.84857 | 0.84857
|  | UL | Load transfer capacity (MVA) | 1 | ULLoad transfer capacity (MVA)1 | 6.8 | [11 empty] | Burnie
|  | UL | Load transfer capacity (MVA) | 2 | ULLoad transfer capacity (MVA)2 | 10.3 | [11 empty] | Devonport
|  | UL | Load transfer capacity (MVA) | 3 | ULLoad transfer capacity (MVA)3 | 3.4 | [11 empty] | Railton
|  | UL | Load transfer capacity (MVA) | 4 | ULLoad transfer capacity (MVA)4
|  | UL | Load transfer capacity (MVA) | 5 | ULLoad transfer capacity (MVA)5
|  | UL | Embedded generation capacity (MVA) | Units less than 100 kVA | ULEmbedded generation capacity (MVA)Units less than 100 kVA | 10.809
|  | UL | Embedded generation capacity (MVA) | Units greater than 100 kVA | ULEmbedded generation capacity (MVA)Units greater than 100 kVA | 8.805
|  | WA | Substation capacity (winter and summer) (MVA) | Total | WASubstation capacity (winter and summer) (MVA)Total | 3.8[1] | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
|  | WA | Substation capacity (winter and summer) (MVA) | Firm delivery | WASubstation capacity (winter and summer) (MVA)Firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | WA | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | WASubstation capacity (winter and summer) (MVA)Short-term firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | WA | Maximum demand forecast(peak season) | Maximum demand (MW) | WAMaximum demand forecast(peak season)Maximum demand (MW) | 0.55828 | 0.9055 | 0.91106 | 0.89818 | 0.89597 | 0.90378 | 0.92808 | 0.95177 | 0.98174 | 1.014 | 1.0626 | 1.1053
|  | WA | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | WAMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 0.0055062 | 0.0089309 | 0.0089856 | 0.0088587 | 0.0088369 | 0.0089139 | 0.0091535 | 0.0093872 | 0.0096828 | 0.010001 | 0.01048 | 0.010901
|  | WA | Maximum demand forecast(peak season) | Maximum demand (MVA) | WAMaximum demand forecast(peak season)Maximum demand (MVA) | 0.55831 | 0.90555 | 0.9111 | 0.89823 | 0.89602 | 0.90382 | 0.92812 | 0.95182 | 0.98179 | 1.0141 | 1.0627 | 1.1053
|  | WA | Maximum demand forecast(peak season) | Power factor (coincident) | WAMaximum demand forecast(peak season)Power factor (coincident) | 0.99995 | 0.99995 | 0.99995 | 0.99995 | 0.99995 | 0.99995 | 0.99995 | 0.99995 | 0.99995 | 0.99995 | 0.99995 | 0.99995
|  | WA | Maximum demand forecast(non-peak season) | Maximum demand (MW) | WAMaximum demand forecast(non-peak season)Maximum demand (MW) | 0.13803 | 0.13627 | 0.12788 | 0.12512 | 0.12552 | 0.12971 | 0.13897 | 0.15142 | 0.16709 | 0.18996 | 0.21861 | 0.249 |  | Summer
|  | WA | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | WAMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 0.04537 | 0.044789 | 0.042033 | 0.041124 | 0.041255 | 0.042633 | 0.045677 | 0.049768 | 0.054919 | 0.062438 | 0.071855 | 0.081841 |  | Summer
|  | WA | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 0.1453 | 0.14344 | 0.13461 | 0.1317 | 0.13212 | 0.13654 | 0.14628 | 0.15938 | 0.17588 | 0.19996 | 0.23012 | 0.2621 |  | Summer
|  | WA | Hours exceeding | 95% of maximum demand | WAHours exceeding95% of maximum demand | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
|  | WA | Hours exceeding | Firm capacity (continuous rating) | WAHours exceedingFirm capacity (continuous rating) | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760
|  | WA | Hours exceeding | Firm capacity (short-term rating) | WAHours exceedingFirm capacity (short-term rating) | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760
|  | WA | Regional diversity factor | Summer | WARegional diversity factorSummer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | WA | Regional diversity factor | Winter | WARegional diversity factorWinter | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | WA | Load transfer capacity (MVA) | 1 | WALoad transfer capacity (MVA)1 | 0.9 | [11 empty] | Arthurs Lake
|  | WA | Load transfer capacity (MVA) | 2 | WALoad transfer capacity (MVA)2
|  | WA | Load transfer capacity (MVA) | 3 | WALoad transfer capacity (MVA)3
|  | WA | Load transfer capacity (MVA) | 4 | WALoad transfer capacity (MVA)4
|  | WA | Load transfer capacity (MVA) | 5 | WALoad transfer capacity (MVA)5
|  | WA | Embedded generation capacity (MVA) | Units less than 100 kVA | WAEmbedded generation capacity (MVA)Units less than 100 kVA | 0
|  | WA | Embedded generation capacity (MVA) | Units greater than 100 kVA | WAEmbedded generation capacity (MVA)Units greater than 100 kVA | 0
|  | WV | Substation capacity (winter and summer) (MVA) | Total | WVSubstation capacity (winter and summer) (MVA)Total | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
|  | WV | Substation capacity (winter and summer) (MVA) | Firm delivery | WVSubstation capacity (winter and summer) (MVA)Firm delivery | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
|  | WV | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | WVSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28
|  | WV | Maximum demand forecast(peak season) | Maximum demand (MW) | WVMaximum demand forecast(peak season)Maximum demand (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | WV | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | WVMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 12.614 | 11.4381 | 11.1202 | 10.8327 | 10.6808 | 10.5453 | 10.6117 | 10.6468 | 10.733 | 10.7357 | 10.9305 | 10.9317
|  | WV | Maximum demand forecast(peak season) | Maximum demand (MVA) | WVMaximum demand forecast(peak season)Maximum demand (MVA) | 12.614 | 11.4381 | 11.1202 | 10.8327 | 10.6808 | 10.5453 | 10.6117 | 10.6468 | 10.733 | 10.7357 | 10.9305 | 10.9317
|  | WV | Maximum demand forecast(peak season) | Power factor (coincident) | WVMaximum demand forecast(peak season)Power factor (coincident) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | WV | Maximum demand forecast(non-peak season) | Maximum demand (MW) | WVMaximum demand forecast(non-peak season)Maximum demand (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Summer
|  | WV | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | WVMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 7.9193 | 8.8731 | 8.4105 | 8.1959 | 8.0304 | 7.9395 | 7.9713 | 7.9837 | 8.0338 | 8.0532 | 8.1104 | 8.1003 |  | Summer
|  | WV | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 7.9193 | 8.8731 | 8.4105 | 8.1959 | 8.0304 | 7.9395 | 7.9713 | 7.9837 | 8.0338 | 8.0532 | 8.1104 | 8.1003 |  | Summer
|  | WV | Hours exceeding | 95% of maximum demand | WVHours exceeding95% of maximum demand | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
|  | WV | Hours exceeding | Firm capacity (continuous rating) | WVHours exceedingFirm capacity (continuous rating)
|  | WV | Hours exceeding | Firm capacity (short-term rating) | WVHours exceedingFirm capacity (short-term rating)
|  | WV | Regional diversity factor | Summer | WVRegional diversity factorSummer | 0.77692 | 0.77692 | 0.77692 | 0.77692 | 0.77692 | 0.77692 | 0.77692 | 0.77692 | 0.77692 | 0.77692 | 0.77692 | 0.77692
|  | WV | Regional diversity factor | Winter | WVRegional diversity factorWinter | 0.8574 | 0.8574 | 0.8574 | 0.8574 | 0.8574 | 0.8574 | 0.8574 | 0.8574 | 0.8574 | 0.8574 | 0.8574 | 0.8574
|  | WV | Load transfer capacity (MVA) | 1 | WVLoad transfer capacity (MVA)1
|  | WV | Load transfer capacity (MVA) | 2 | WVLoad transfer capacity (MVA)2
|  | WV | Load transfer capacity (MVA) | 3 | WVLoad transfer capacity (MVA)3
|  | WV | Load transfer capacity (MVA) | 4 | WVLoad transfer capacity (MVA)4
|  | WV | Load transfer capacity (MVA) | 5 | WVLoad transfer capacity (MVA)5
|  | WV | Embedded generation capacity (MVA) | Units less than 100 kVA | WVEmbedded generation capacity (MVA)Units less than 100 kVA | 4.0988
|  | WV | Embedded generation capacity (MVA) | Units greater than 100 kVA | WVEmbedded generation capacity (MVA)Units greater than 100 kVA | 0.265

## Zone subs & sub-trans lines
[5 empty] | Planning area |  |  |  | Greater Hobart | [5 empty] | Sub-transmission lines |  | Source substation
| Zone substation: |  |  |  | Supplying |  |  |  | Distribution lines | [5 empty] | 24401 | Howrah1 | Mornington
| Howrah |  |  |  | Voltage |  |  |  | 33/11 kV | [5 empty] | 24406 | Howrah2 | Mornington
[5 empty] | Number of transformers |  |  |  | 2 | [6 empty] | Howrah3
[5 empty] | Peaking season |  |  |  | Winter
Forecast | Parameter |  |  | 2021 (Actual) | 2022 (Actuals) | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
Substation capacity (winter and summer) (MVA) | Total | Substation capacity (winter and summer) (MVA) | HOZSubstation capacity (winter and summer) (MVA)Total | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
| Firm delivery | Substation capacity (winter and summer) (MVA) | HOZSubstation capacity (winter and summer) (MVA)Firm delivery | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
| Short-term firm delivery | Substation capacity (winter and summer) (MVA) | HOZSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 32.5 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5
Sub-transmission line capacity (MVA) | Total (winter) | Sub-transmission lines capacity | HOZSub-transmission lines capacityTotal (winter) | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7
| Firm delivery (winter) | Sub-transmission lines capacity | HOZSub-transmission lines capacityFirm delivery (winter) | 18.3[1] | 18.3[1] | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3
| Total (summer) | Sub-transmission lines capacity | HOZSub-transmission lines capacityTotal (summer) | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7
| Firm delivery (summer) | Sub-transmission lines capacity | HOZSub-transmission lines capacityFirm delivery (summer) | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3
Maximum demand forecast | Maximum demand (MVA) | Maximum demand forecast(peak season) | HOZMaximum demand forecast(peak season)Maximum demand (MVA) | 21.6344 | 21.2816 | 21.5126 | 21.2046 | 21.057 | 21.1297 | 21.5141 | 21.8508 | 22.2417 | 22.604 | 23.2603 | 23.7391
(Winter) | Power factor (coincident) | Maximum demand forecast(peak season) | HOZMaximum demand forecast(peak season)Power factor (coincident) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum demand forecast | Maximum demand (MVA) | Maximum demand forecast(non-peak season) | HOZMaximum demand forecast(non-peak season)Maximum demand (MVA) | 11.3546 | 12.0396 | 11.5871 | 11.2266 | 10.9494 | 10.8814 | 10.9733 | 11.0704 | 11.2184 | 11.4326 | 11.6903 | 11.9613
(Summer) | Power factor (coincident) | Maximum demand forecast(non-peak season) | HOZMaximum demand forecast(non-peak season)Power factor (coincident) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hours exceeding | 95% of maximum demand | Hours exceeding | HOZHours exceeding95% of maximum demand | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
Load transfer capacity (MVA) | Bellerive | Load transfer capacity (MVA)1 | HOZLoad transfer capacity (MVA)1 | 2.4
| Rokeby | Load transfer capacity (MVA)2 | HOZLoad transfer capacity (MVA)2 | 7.1
|  | Load transfer capacity (MVA)3 | HOZLoad transfer capacity (MVA)3
|  | Load transfer capacity (MVA)4 | HOZLoad transfer capacity (MVA)4
Embedded generation capacity (MVA) | Units less than 100 kVA | Embedded generation capacity (MVA) | HOZEmbedded generation capacity (MVA)Units less than 100 kVA | 1.905
| Units greater than 100 kVA | Embedded generation capacity (MVA) | HOZEmbedded generation capacity (MVA)Units greater than 100 kVA
DER Maximum | PV
EV
Battery
| Notes |  |  | [1] From this data, the load at Howrah Zone has currently exceeds the firm rating of the sub-transmission lines. However we believe the assigned rating of these lines are overly conservative and are currently investigating this. Therefore this has not been identified as a constraint in this APR.
|  |  |  | #VALUE! | 2022 (Actuals) | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 |  |  | 2032
|  |  |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
|  |  |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
|  |  |  | 32.5 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5
|  |  |  | 21.6344 | 21.2816 | 21.5126 | 21.2046 | 21.057 | 21.1297 | 21.5141 | 21.8508 | 22.2417 | 22.604 | 23.2603 | 23.7391

## Zone data (hidden)
[6 empty] | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 13 | 14
[6 empty] | 2021 (Actual) | 2022 (Actuals) | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | Load transfer point | Non-peaking season | Substation | Planning area | Supplying | Voltage | Number of transformers | Peaking season | Substation |  |  | Sub-transmission feeders | Source substation | Substation | Comment | Zone | hours above 95% of MD
Bellerive | BEZ | BEZ | Substation capacity (winter and summer) (MVA) | Total | BEZSubstation capacity (winter and summer) (MVA)Total | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 50 | 50 | 50 |  |  | Bellerive | Greater Hobart | Distribution lines | 33/11 kV | 2 | Winter | Bellerive | 1 | Bellerive1 | 25305 | Lindisfarne | Bellerive | [1] We propose to replace the supply transformers due to asset condition in 2028 with new units of standard size, as detailed in Section 4.9 of this APR. Upon replacement of the transformers, the firm rating of the substation will be limited by the rating of the 11 kV switchboard. [2] Load reduction following transfer of load to new Rosny Park Zone Substation, as detailed in chapter 6 of this APR. | BEZ | 3
Cambridge | CAZ | BEZ | Substation capacity (winter and summer) (MVA) | Firm delivery | BEZSubstation capacity (winter and summer) (MVA)Firm delivery | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.9[1] | 22.9 | 22.9 | 22.9 | 22.9 |  |  | Cambridge | Greater Hobart | Distribution lines | 33/11 kV | 2 | Winter | Bellerive | 2 | Bellerive2 | 25310 | Lindisfarne | Claremont | [1] We propose to replace the supply transformers due to asset condition in 2020 with new units of standard size, as detailed in Section 6.9.3 of this APR. | CAZ | 11
Claremont | CLZ | BEZ | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | BEZSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 |  |  | Claremont | Greater Hobart | Distribution lines | 33/11 kV | 2 | Winter | Bellerive | 3 | Bellerive3 |  |  | Derwent Park | [1] We propose to replace the supply transformers due to asset condition in 2025 with new units of standard size, as detailed in Section 4.9 of this APR. Upon replacement of the transformers, the firm rating of the substation will be limited by the rating of the 11 kV switchboard. [2] Currently in summer, and from 2024 in winter, load exceeds the firm rating of the sub-transmission lines, as detailed in Section 6.9.2 of this APR. | CLZ | 1.5
Derwent Park | DPZ | BEZ | Sub-transmission lines capacity | Total (winter) | BEZSub-transmission lines capacityTotal (winter) | 39.4 | 39.4 | 39.4 | 39.4 | 39.4 | 39.4 | 39.4 | 39.4 | 39.4 | 39.4 | 39.4 | 39.4 |  |  | Derwent Park | Greater Hobart | Distribution lines | 33/11 kV | 2 | Winter | Cambridge | 1 | Cambridge1 | 25309 | Lindisfarne | East Hobart | [1] From summer 2018, load is forecast to exceed the firm rating of the sub-transmission lines, as detailed in Section 6.9.2 of this APR. | DPZ | 5.5
East Hobart | EHZ | BEZ | Sub-transmission lines capacity | Firm delivery (winter) | BEZSub-transmission lines capacityFirm delivery (winter) | 19.4 | 19.4 | 19.4 | 19.4 | 19.4 | 19.4 | 19.4 | 19.4 | 19.4 | 19.4 | 19.4 | 19.4 |  |  | East Hobart | Greater Hobart | Distribution lines | 33/11 kV | 3 | Winter | Cambridge | 2 | Cambridge2 | 24402 | Mornington | Geilston Bay | [1] We propose to replace the supply transformers due to asset condition in 2027 with new units of standard size, as detailed in Section 4.9 of this APR. Upon replacement of the transformers, the firm rating of the substation will be limited by the rating of the 11 kV switchboard. | EHZ | 16
Geilston Bay | GBZ | BEZ | Sub-transmission lines capacity | Total (summer) | BEZSub-transmission lines capacityTotal (summer) | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 |  |  | Geilston Bay | Greater Hobart | Distribution lines | 33/11 kV | 2 | Winter | Cambridge | 3 | Cambridge3 |  |  | Howrah | [1] From this data, the load at Howrah Zone has currently exceeds the firm rating of the sub-transmission lines. However we believe the assigned rating of these lines are overly conservative and are currently investigating this. Therefore this has not been identified as a constraint in this APR. | GBZ | 1.5
Howrah | HOZ | BEZ | Sub-transmission lines capacity | Firm delivery (summer) | BEZSub-transmission lines capacityFirm delivery (summer) | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 |  |  | Howrah | Greater Hobart | Distribution lines | 33/11 kV | 2 | Winter | Claremont | 1 | Claremont1 | 10007 | Creek Road | New Town | [1] Currently in summer, and in winter from 2024, load exceeds the firm rating of the sub-transmission lines, as detailed in Section 6.9.2 of this APR. [1] We propose to replace the supply transformers due to asset condition in 2022 with new units of standard size, as detailed in Section 6.9.3 of this APR. Upon replacement of the transformers, the firm rating of the substation will be limited by the rating of the 11 kV switchboard. | HOZ | 1.5
New Town | NTZ | BEZ | Maximum demand forecast(peak season) | Maximum demand (MVA) | BEZMaximum demand forecast(peak season)Maximum demand (MVA) | 10.4442 | 10.3203 | 10.4279 | 10.2694 | 10.1792 | 10.1931 | 10.3633 | 10.5157 | 10.7032 | 10.8832 | 11.2093 | 11.4546 |  |  | New Town | Greater Hobart | Distribution lines | 33/11 kV | 2 | Winter | Claremont | 2 | Claremont2 | 10026 | Creek Road | Trial Harbour | [1] Load forecast step increase in 2018 from point load increase. | NTZ | 12.5
Rosny Park | RPZ | BEZ | Maximum demand forecast(peak season) | Power factor (coincident) | BEZMaximum demand forecast(peak season)Power factor (coincident) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Rosny Park | Greater Hobart | Distribution lines | 33/11 kV | 1 | Winter | Claremont | 3 | Claremont3 |  |  | Gretna rural | [1] Rural zone substations are supplied from within the distribution network, not by sub-transmission lines. | RPZ | 7
Sandy Bay | SBZ | BEZ | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | BEZMaximum demand forecast(non-peak season)Maximum demand (MVA) | 9.6417 | 7.558 | 7.3066 | 7.1006 | 6.9294 | 6.8764 | 6.9203 | 6.963 | 7.036 | 7.1379 | 7.2637 | 7.3924 |  | Summer | Sandy Bay | Greater Hobart | Distribution lines | 33/11 kV | 3 | Winter | Derwent Park | 1 | Derwent Park1 | 11021 | Risdon | New Norfolk rural | [1] Rural zone substations are supplied from within the distribution network, not by sub-transmission lines. [2] We propose to replace and rationalise the supply transformers due to asset condition in by 2019 with new 3 x 5 MVA units of standard size. | SBZ | 3
Summerleas | SUZ | BEZ | Maximum demand forecast(non-peak season) | Power factor (coincident) | BEZMaximum demand forecast(non-peak season)Power factor (coincident) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Summer | Summerleas | Kingston-South | Distribution lines | 33/11 kV | 1 | Winter | Derwent Park | 2 | Derwent Park2 | 11025 | Risdon | Richmond rural | [1] Rural zone substations are supplied from within the distribution network, not by sub-transmission lines. [2] The supply transformers replacement is a committed project to commission in 2023 with new 2 x 5 MVA units of standard size. [3] Load currently exceeds the firm rating of the substation, however fast, remote load transfers exist to manage this. This has not been identified as a constraint in this APR. | SUZ | 2.5
Trial Harbour | THZ | BEZ | Hours exceeding | 95% of maximum demand | BEZHours exceeding95% of maximum demand | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  |  | Trial Harbour | West Coast | Distribution lines | 44/22 kV | 2 | Winter | Derwent Park | 3 | Derwent Park3 |  |  | Wayatinah rural | [1] Rural zone substations are supplied from within the distribution network, not by sub-transmission lines. | THZ | 7
West Hobart | WHZ | BEZ | Load transfer capacity (MVA) | 1 | BEZLoad transfer capacity (MVA)1 | 6.2 | [11 empty] | Cambridge |  | West Hobart | Greater Hobart | Distribution lines | 33/11 kV | 3 | Winter | East Hobart | 1 | East Hobart1 | 11004 | Risdon |  |  | WHZ | 1
Gretna rural | GRZ | BEZ | Load transfer capacity (MVA) | 2 | BEZLoad transfer capacity (MVA)2 | 4.1 | [11 empty] | Geilston Bay |  | Gretna rural | Central | Distribution lines | 22/11 kV | 1 | Summer | East Hobart | 2 | East Hobart2 | 11005 | Risdon |  |  | GRZ | 0.5
Richmond rural | RIZ | BEZ | Load transfer capacity (MVA) | 3 | BEZLoad transfer capacity (MVA)3 | 3.1 | [11 empty] | Howrah |  | New Norfolk rural | Central | Distribution lines | 22/11 kV | 4 | Winter | East Hobart | 3 | East Hobart3 | 11006 | Risdon |  |  | NNZ | #N/A
Wayatinah rural | WYZ | BEZ | Load transfer capacity (MVA) | 4 | BEZLoad transfer capacity (MVA)4 | 3.1 | [11 empty] | Rokeby |  | Richmond rural | Eastern | Distribution lines | 22/11 kV | 2 | Winter | Geilston Bay | 1 | Geilston Bay1 | 25307 | Lindisfarne |  |  | RIZ | 8.5
|  | BEZ | Embedded generation capacity (MVA) | Units less than 100 kVA | BEZEmbedded generation capacity (MVA)Units less than 100 kVA | 0.876 | [13 empty] | Wayatinah rural | Central | Distribution lines | 11/22 kV | 1 | Winter | Geilston Bay | 2 | Geilston Bay2 | 25308 | Lindisfarne |  |  | WYZ | 5.5
|  | BEZ | Embedded generation capacity (MVA) | Units greater than 100 kVA | BEZEmbedded generation capacity (MVA)Units greater than 100 kVA | [20 empty] | Geilston Bay | 3 | Geilston Bay3
|  | CAZ | Substation capacity (winter and summer) (MVA) | Total | CAZSubstation capacity (winter and summer) (MVA)Total | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | [8 empty] | Howrah | 1 | Howrah1 | 24401 | Mornington
|  | CAZ | Substation capacity (winter and summer) (MVA) | Firm delivery | CAZSubstation capacity (winter and summer) (MVA)Firm delivery | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | [8 empty] | Howrah | 2 | Howrah2 | 24406 | Mornington
|  | CAZ | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | CAZSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | [8 empty] | Howrah | 3 | Howrah3
|  | CAZ | Sub-transmission lines capacity | Total (winter) | CAZSub-transmission lines capacityTotal (winter) | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | [8 empty] | New Town | 1 | New Town1 | 11023 | Risdon
|  | CAZ | Sub-transmission lines capacity | Firm delivery (winter) | CAZSub-transmission lines capacityFirm delivery (winter) | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | [8 empty] | New Town | 2 | New Town2 | 11027 | Risdon
|  | CAZ | Sub-transmission lines capacity | Total (summer) | CAZSub-transmission lines capacityTotal (summer) | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | [8 empty] | New Town | 3 | New Town3
|  | CAZ | Sub-transmission lines capacity | Firm delivery (summer) | CAZSub-transmission lines capacityFirm delivery (summer) | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | [8 empty] | Rosny Park | 1 | Rosny Park1 | 24405 | Mornington
|  | CAZ | Maximum demand forecast(peak season) | Maximum demand (MVA) | CAZMaximum demand forecast(peak season)Maximum demand (MVA) | 17.4502 | 16.9885 | 17.0118 | 16.6128 | 16.4143 | 16.3909 | 16.6224 | 16.7917 | 16.9888 | 17.1201 | 17.4447 | 17.6761 | [8 empty] | Rosny Park | 2 | Rosny Park2
|  | CAZ | Maximum demand forecast(peak season) | Power factor (coincident) | CAZMaximum demand forecast(peak season)Power factor (coincident) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | Rosny Park | 3 | Rosny Park3
|  | CAZ | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | CAZMaximum demand forecast(non-peak season)Maximum demand (MVA) | 11.5972 | 12.5347 | 12.2623 | 11.9919 | 11.7976 | 11.8209 | 11.9891 | 12.1207 | 12.2792 | 12.4435 | 12.5918 | 12.7962 |  | Summer | [6 empty] | Sandy Bay | 1 | Sandy Bay1 | 10008 | Creek Road
|  | CAZ | Maximum demand forecast(non-peak season) | Power factor (coincident) | CAZMaximum demand forecast(non-peak season)Power factor (coincident) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Summer | [6 empty] | Sandy Bay | 2 | Sandy Bay2 | 10022 | Creek Road
|  | CAZ | Hours exceeding | 95% of maximum demand | CAZHours exceeding95% of maximum demand | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | [8 empty] | Sandy Bay | 3 | Sandy Bay3 | 10024 | Creek Road
|  | CAZ | Load transfer capacity (MVA) | 1 | CAZLoad transfer capacity (MVA)1 | 7.4 | [11 empty] | Bellerive | [7 empty] | Summerleas | 1 | Summerleas1 | 36240 | Kingston
|  | CAZ | Load transfer capacity (MVA) | 2 | CAZLoad transfer capacity (MVA)2 | 7.4 | [11 empty] | Rokeby | [7 empty] | Summerleas | 2 | Summerleas2
|  | CAZ | Load transfer capacity (MVA) | 3 | CAZLoad transfer capacity (MVA)3 | [20 empty] | Summerleas | 3 | Summerleas3
|  | CAZ | Load transfer capacity (MVA) | 4 | CAZLoad transfer capacity (MVA)4 | [20 empty] | Trial Harbour | 1 | Trial Harbour1 | 97013 | 50[1]
|  | CAZ | Embedded generation capacity (MVA) | Units less than 100 kVA | CAZEmbedded generation capacity (MVA)Units less than 100 kVA | 1.794 | [19 empty] | Trial Harbour | 2 | Trial Harbour2
|  | CAZ | Embedded generation capacity (MVA) | Units greater than 100 kVA | CAZEmbedded generation capacity (MVA)Units greater than 100 kVA | [20 empty] | Trial Harbour | 3 | Trial Harbour3
|  | CLZ | Substation capacity (winter and summer) (MVA) | Total | CLZSubstation capacity (winter and summer) (MVA)Total | 45 | 45 | 45 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | [8 empty] | West Hobart | 1 | West Hobart1 | 10001 | Creek Road
|  | CLZ | Substation capacity (winter and summer) (MVA) | Firm delivery | CLZSubstation capacity (winter and summer) (MVA)Firm delivery | 22.5 | 22.5 | 25[1] | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | [8 empty] | West Hobart | 2 | West Hobart2 | 10002 | Creek Road
|  | CLZ | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | CLZSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 30 | 30 | 30 | 30 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | [8 empty] | West Hobart | 3 | West Hobart3 | 10003 | Creek Road
|  | CLZ | Sub-transmission lines capacity | Total (winter) | CLZSub-transmission lines capacityTotal (winter) | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | [8 empty] | Gretna rural | 1 | Gretna rural1 | [1]
|  | CLZ | Sub-transmission lines capacity | Firm delivery (winter) | CLZSub-transmission lines capacityFirm delivery (winter) | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | [8 empty] | Gretna rural | 2 | Gretna rural2
|  | CLZ | Sub-transmission lines capacity | Total (summer) | CLZSub-transmission lines capacityTotal (summer) | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | [8 empty] | Gretna rural | 3 | Gretna rural3
|  | CLZ | Sub-transmission lines capacity | Firm delivery (summer) | CLZSub-transmission lines capacityFirm delivery (summer) | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | [8 empty] | New Norfolk rural | 1 | New Norfolk rural1 | [1]
|  | CLZ | Maximum demand forecast(peak season) | Maximum demand (MVA) | CLZMaximum demand forecast(peak season)Maximum demand (MVA) | 22.3649 | 22.118 | 22.3641 | 21.9673 | 21.8083 | 21.8308 | 22.2188 | 22.5457 | 22.9666 | 23.3675 | 24.0959 | 24.6231 | [8 empty] | New Norfolk rural | 2 | New Norfolk rural2
|  | CLZ | Maximum demand forecast(peak season) | Power factor (coincident) | CLZMaximum demand forecast(peak season)Power factor (coincident) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | New Norfolk rural | 3 | New Norfolk rural3
|  | CLZ | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | CLZMaximum demand forecast(non-peak season)Maximum demand (MVA) | 14.3675 | 12.6915 | 12.3336 | 11.9896 | 11.7432 | 11.7204 | 11.8959 | 12.0854 | 12.345 | 12.7175 | 13.1502 | 13.5975 |  | Summer | [6 empty] | Richmond rural | 1 | Richmond rural1 | [1]
|  | CLZ | Maximum demand forecast(non-peak season) | Power factor (coincident) | CLZMaximum demand forecast(non-peak season)Power factor (coincident) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Summer | [6 empty] | Richmond rural | 2 | Richmond rural2
|  | CLZ | Hours exceeding | 95% of maximum demand | CLZHours exceeding95% of maximum demand | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | [8 empty] | Richmond rural | 3 | Richmond rural3
|  | CLZ | Load transfer capacity (MVA) | 1 | CLZLoad transfer capacity (MVA)1 | 4.2 | [11 empty] | Bridgewater | [7 empty] | Wayatinah rural | 1 | Wayatinah rural1 | [1]
|  | CLZ | Load transfer capacity (MVA) | 2 | CLZLoad transfer capacity (MVA)2 | 5.9 | [11 empty] | Chapel Street | [7 empty] | Wayatinah rural | 2 | Wayatinah rural2
|  | CLZ | Load transfer capacity (MVA) | 3 | CLZLoad transfer capacity (MVA)3 | 0.8 | [11 empty] | New Norfolk | [7 empty] | Wayatinah rural | 3 | Wayatinah rural3
|  | CLZ | Load transfer capacity (MVA) | 4 | CLZLoad transfer capacity (MVA)4
|  | CLZ | Embedded generation capacity (MVA) | Units less than 100 kVA | CLZEmbedded generation capacity (MVA)Units less than 100 kVA | 1.318
|  | CLZ | Embedded generation capacity (MVA) | Units greater than 100 kVA | CLZEmbedded generation capacity (MVA)Units greater than 100 kVA
|  | DPZ | Substation capacity (winter and summer) (MVA) | Total | DPZSubstation capacity (winter and summer) (MVA)Total | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 50 | 50 | 50 | 50 | 50
|  | DPZ | Substation capacity (winter and summer) (MVA) | Firm delivery | DPZSubstation capacity (winter and summer) (MVA)Firm delivery | 22.5 | 22.9[1] | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9
|  | DPZ | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | DPZSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9
|  | DPZ | Sub-transmission lines capacity | Total (winter) | DPZSub-transmission lines capacityTotal (winter) | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1
|  | DPZ | Sub-transmission lines capacity | Firm delivery (winter) | DPZSub-transmission lines capacityFirm delivery (winter) | 21.4 | 21.4 | 21.4 | 21.4 | 21.4 | 21.4 | 21.4 | 21.4 | 21.4 | 21.4 | 21.4 | 21.4
|  | DPZ | Sub-transmission lines capacity | Total (summer) | DPZSub-transmission lines capacityTotal (summer) | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9
|  | DPZ | Sub-transmission lines capacity | Firm delivery (summer) | DPZSub-transmission lines capacityFirm delivery (summer) | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4
|  | DPZ | Maximum demand forecast(peak season) | Maximum demand (MVA) | DPZMaximum demand forecast(peak season)Maximum demand (MVA) | 19.6301 | 19.1852 | 19.4164 | 19.058 | 18.852 | 18.8312 | 19.1122 | 19.3447 | 19.6213 | 19.8379 | 20.2967 | 20.6115
|  | DPZ | Maximum demand forecast(peak season) | Power factor (coincident) | DPZMaximum demand forecast(peak season)Power factor (coincident) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | DPZ | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | DPZMaximum demand forecast(non-peak season)Maximum demand (MVA) | 14.472 | 12.9504 | 12.751 | 12.5131 | 12.3045 | 12.3101 | 12.4769 | 12.6229 | 12.8048 | 13.0048 | 13.2059 | 13.4335 |  | Summer
|  | DPZ | Maximum demand forecast(non-peak season) | Power factor (coincident) | DPZMaximum demand forecast(non-peak season)Power factor (coincident) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Summer
|  | DPZ | Hours exceeding | 95% of maximum demand | DPZHours exceeding95% of maximum demand | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5
|  | DPZ | Load transfer capacity (MVA) | 1 | DPZLoad transfer capacity (MVA)1 | 13.9 | [11 empty] | Chapel Street
|  | DPZ | Load transfer capacity (MVA) | 2 | DPZLoad transfer capacity (MVA)2 | 9.4 | [11 empty] | New Town
|  | DPZ | Load transfer capacity (MVA) | 3 | DPZLoad transfer capacity (MVA)3
|  | DPZ | Load transfer capacity (MVA) | 4 | DPZLoad transfer capacity (MVA)4
|  | DPZ | Embedded generation capacity (MVA) | Units less than 100 kVA | DPZEmbedded generation capacity (MVA)Units less than 100 kVA | 0.786 | 0.786
|  | DPZ | Embedded generation capacity (MVA) | Units greater than 100 kVA | DPZEmbedded generation capacity (MVA)Units greater than 100 kVA
|  | EHZ | Substation capacity (winter and summer) (MVA) | Total | EHZSubstation capacity (winter and summer) (MVA)Total | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
|  | EHZ | Substation capacity (winter and summer) (MVA) | Firm delivery | EHZSubstation capacity (winter and summer) (MVA)Firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  | EHZ | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | EHZSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78
|  | EHZ | Sub-transmission lines capacity | Total (winter) | EHZSub-transmission lines capacityTotal (winter) | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71
|  | EHZ | Sub-transmission lines capacity | Firm delivery (winter) | EHZSub-transmission lines capacityFirm delivery (winter) | 47.2 | 47.2 | 47.2 | 47.2 | 47.2 | 47.2 | 47.2 | 47.2 | 47.2 | 47.2 | 47.2 | 47.2
|  | EHZ | Sub-transmission lines capacity | Total (summer) | EHZSub-transmission lines capacityTotal (summer) | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5
|  | EHZ | Sub-transmission lines capacity | Firm delivery (summer) | EHZSub-transmission lines capacityFirm delivery (summer) | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9
|  | EHZ | Maximum demand forecast(peak season) | Maximum demand (MVA) | EHZMaximum demand forecast(peak season)Maximum demand (MVA) | 28.5788 | 29.2574 | 29.6632 | 31.8147 | 32.94 | 33.4795 | 34.1831 | 34.6615 | 35.1923 | 35.5262 | 36.2663 | 36.7728
|  | EHZ | Maximum demand forecast(peak season) | Power factor (coincident) | EHZMaximum demand forecast(peak season)Power factor (coincident) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | EHZ | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | EHZMaximum demand forecast(non-peak season)Maximum demand (MVA) | 23.8871 | 23.8662 | 23.4563 | 25.8637 | 27.0012 | 27.5933 | 28.1669 | 28.5239 | 28.9528 | 29.2924 | 29.6187 | 29.9456 |  | Summer
|  | EHZ | Maximum demand forecast(non-peak season) | Power factor (coincident) | EHZMaximum demand forecast(non-peak season)Power factor (coincident) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Summer
|  | EHZ | Hours exceeding | 95% of maximum demand | EHZHours exceeding95% of maximum demand | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
|  | EHZ | Load transfer capacity (MVA) | 1 | EHZLoad transfer capacity (MVA)1 | 4.3 | [11 empty] | Geilston Bay
|  | EHZ | Load transfer capacity (MVA) | 2 | EHZLoad transfer capacity (MVA)2 | 9.9 | [11 empty] | North Hobart
|  | EHZ | Load transfer capacity (MVA) | 3 | EHZLoad transfer capacity (MVA)3 | 11.3 | [11 empty] | West Hobart
|  | EHZ | Load transfer capacity (MVA) | 4 | EHZLoad transfer capacity (MVA)4
|  | EHZ | Embedded generation capacity (MVA) | Units less than 100 kVA | EHZEmbedded generation capacity (MVA)Units less than 100 kVA | 0.356
|  | EHZ | Embedded generation capacity (MVA) | Units greater than 100 kVA | EHZEmbedded generation capacity (MVA)Units greater than 100 kVA
|  | GBZ | Substation capacity (winter and summer) (MVA) | Total | GBZSubstation capacity (winter and summer) (MVA)Total | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 50 | 50 | 50
|  | GBZ | Substation capacity (winter and summer) (MVA) | Firm delivery | GBZSubstation capacity (winter and summer) (MVA)Firm delivery | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.9[1] | 22.9 | 22.9 | 22.9 | 22.9
|  | GBZ | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | GBZSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9
|  | GBZ | Sub-transmission lines capacity | Total (winter) | GBZSub-transmission lines capacityTotal (winter) | 46.3 | 46.3 | 46.3 | 46.3 | 46.3 | 46.3 | 46.3 | 46.3 | 46.3 | 46.3 | 46.3 | 46.3
|  | GBZ | Sub-transmission lines capacity | Firm delivery (winter) | GBZSub-transmission lines capacityFirm delivery (winter) | 22.6 | 22.6 | 22.6 | 22.6 | 22.6 | 22.6 | 22.6 | 22.6 | 22.6 | 22.6 | 22.6 | 22.6
|  | GBZ | Sub-transmission lines capacity | Total (summer) | GBZSub-transmission lines capacityTotal (summer) | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27
|  | GBZ | Sub-transmission lines capacity | Firm delivery (summer) | GBZSub-transmission lines capacityFirm delivery (summer) | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4
|  | GBZ | Maximum demand forecast(peak season) | Maximum demand (MVA) | GBZMaximum demand forecast(peak season)Maximum demand (MVA) | 19.1596 | 19.0827 | 19.1263 | 18.7793 | 18.5522 | 18.4896 | 18.6986 | 18.863 | 19.0743 | 19.2745 | 19.751 | 20.0212
|  | GBZ | Maximum demand forecast(peak season) | Power factor (coincident) | GBZMaximum demand forecast(peak season)Power factor (coincident) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | GBZ | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | GBZMaximum demand forecast(non-peak season)Maximum demand (MVA) | 11.0712 | 10.354 | 9.9818 | 9.6686 | 9.4018 | 9.3182 | 9.362 | 9.411 | 9.5001 | 9.6705 | 9.885 | 10.1046 |  | Summer
|  | GBZ | Maximum demand forecast(non-peak season) | Power factor (coincident) | GBZMaximum demand forecast(non-peak season)Power factor (coincident) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Summer
|  | GBZ | Hours exceeding | 95% of maximum demand | GBZHours exceeding95% of maximum demand | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
|  | GBZ | Load transfer capacity (MVA) | 1 | GBZLoad transfer capacity (MVA)1 | 5.1 | [11 empty] | Bellerive
|  | GBZ | Load transfer capacity (MVA) | 2 | GBZLoad transfer capacity (MVA)2 | 5.1 | [11 empty] | Derwent Park
|  | GBZ | Load transfer capacity (MVA) | 3 | GBZLoad transfer capacity (MVA)3 | 3.8 | [11 empty] | West Hobart
|  | GBZ | Load transfer capacity (MVA) | 4 | GBZLoad transfer capacity (MVA)4
|  | GBZ | Embedded generation capacity (MVA) | Units less than 100 kVA | GBZEmbedded generation capacity (MVA)Units less than 100 kVA | 1.491
|  | GBZ | Embedded generation capacity (MVA) | Units greater than 100 kVA | GBZEmbedded generation capacity (MVA)Units greater than 100 kVA
|  | HOZ | Substation capacity (winter and summer) (MVA) | Total | HOZSubstation capacity (winter and summer) (MVA)Total | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
|  | HOZ | Substation capacity (winter and summer) (MVA) | Firm delivery | HOZSubstation capacity (winter and summer) (MVA)Firm delivery | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
|  | HOZ | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | HOZSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 32.5 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5
|  | HOZ | Sub-transmission lines capacity | Total (winter) | HOZSub-transmission lines capacityTotal (winter) | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7
|  | HOZ | Sub-transmission lines capacity | Firm delivery (winter) | HOZSub-transmission lines capacityFirm delivery (winter) | 18.3[1] | 18.3[1] | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3
|  | HOZ | Sub-transmission lines capacity | Total (summer) | HOZSub-transmission lines capacityTotal (summer) | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7
|  | HOZ | Sub-transmission lines capacity | Firm delivery (summer) | HOZSub-transmission lines capacityFirm delivery (summer) | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3
|  | HOZ | Maximum demand forecast(peak season) | Maximum demand (MVA) | HOZMaximum demand forecast(peak season)Maximum demand (MVA) | 21.6344 | 21.2816 | 21.5126 | 21.2046 | 21.057 | 21.1297 | 21.5141 | 21.8508 | 22.2417 | 22.604 | 23.2603 | 23.7391
|  | HOZ | Maximum demand forecast(peak season) | Power factor (coincident) | HOZMaximum demand forecast(peak season)Power factor (coincident) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | HOZ | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | HOZMaximum demand forecast(non-peak season)Maximum demand (MVA) | 11.3546 | 12.0396 | 11.5871 | 11.2266 | 10.9494 | 10.8814 | 10.9733 | 11.0704 | 11.2184 | 11.4326 | 11.6903 | 11.9613 |  | Summer
|  | HOZ | Maximum demand forecast(non-peak season) | Power factor (coincident) | HOZMaximum demand forecast(non-peak season)Power factor (coincident) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Summer
|  | HOZ | Hours exceeding | 95% of maximum demand | HOZHours exceeding95% of maximum demand | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
|  | HOZ | Load transfer capacity (MVA) | 1 | HOZLoad transfer capacity (MVA)1 | 2.4 | [11 empty] | Bellerive
|  | HOZ | Load transfer capacity (MVA) | 2 | HOZLoad transfer capacity (MVA)2 | 7.1 | [11 empty] | Rokeby
|  | HOZ | Load transfer capacity (MVA) | 3 | HOZLoad transfer capacity (MVA)3
|  | HOZ | Load transfer capacity (MVA) | 4 | HOZLoad transfer capacity (MVA)4
|  | HOZ | Embedded generation capacity (MVA) | Units less than 100 kVA | HOZEmbedded generation capacity (MVA)Units less than 100 kVA | 1.905
|  | HOZ | Embedded generation capacity (MVA) | Units greater than 100 kVA | HOZEmbedded generation capacity (MVA)Units greater than 100 kVA
|  | NTZ | Substation capacity (winter and summer) (MVA) | Total | NTZSubstation capacity (winter and summer) (MVA)Total | 45 | 45 | 45 | 45 | 45 | 45 | 50 | 50 | 50 | 50 | 50 | 50
|  | NTZ | Substation capacity (winter and summer) (MVA) | Firm delivery | NTZSubstation capacity (winter and summer) (MVA)Firm delivery | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.9[2] | 22.9 | 22.9 | 22.9 | 22.9 | 22.9
|  | NTZ | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | NTZSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9
|  | NTZ | Sub-transmission lines capacity | Total (winter) | NTZSub-transmission lines capacityTotal (winter) | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9
|  | NTZ | Sub-transmission lines capacity | Firm delivery (winter) | NTZSub-transmission lines capacityFirm delivery (winter) | 21.4 | 21.4 | 21.4 | 21.4 | 21.4 | 21.4 | 21.4 | 21.4 | 21.4 | 21.4 | 21.4 | 21.4
|  | NTZ | Sub-transmission lines capacity | Total (summer) | NTZSub-transmission lines capacityTotal (summer) | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8
|  | NTZ | Sub-transmission lines capacity | Firm delivery (summer) | NTZSub-transmission lines capacityFirm delivery (summer) | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4
|  | NTZ | Maximum demand forecast(peak season) | Maximum demand (MVA) | NTZMaximum demand forecast(peak season)Maximum demand (MVA) | 22.3948 | 22.067 | 22.5275 | 22.4988 | 23.1802 | 23.6793 | 24.2949 | 24.7818 | 25.3366 | 25.8535 | 26.6954 | 27.3562
|  | NTZ | Maximum demand forecast(peak season) | Power factor (coincident) | NTZMaximum demand forecast(peak season)Power factor (coincident) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | NTZ | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | NTZMaximum demand forecast(non-peak season)Maximum demand (MVA) | 13.7969 | 17.1169 | 17.0384 | 17.0891 | 17.691 | 18.1609 | 18.5833 | 18.8829 | 19.2011 | 19.5502 | 19.9064 | 20.2937 |  | Summer
|  | NTZ | Maximum demand forecast(non-peak season) | Power factor (coincident) | NTZMaximum demand forecast(non-peak season)Power factor (coincident) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Summer
|  | NTZ | Hours exceeding | 95% of maximum demand | NTZHours exceeding95% of maximum demand | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5
|  | NTZ | Load transfer capacity (MVA) | 1 | NTZLoad transfer capacity (MVA)1 | 3.9 | [11 empty] | Chapel Street
|  | NTZ | Load transfer capacity (MVA) | 2 | NTZLoad transfer capacity (MVA)2 | 4.8 | [11 empty] | Derwent Park
|  | NTZ | Load transfer capacity (MVA) | 3 | NTZLoad transfer capacity (MVA)3 | 3.9 | [11 empty] | East Hobart
|  | NTZ | Load transfer capacity (MVA) | 4 | NTZLoad transfer capacity (MVA)4 | 7.7 | [11 empty] | North Hobart
|  | NTZ | Embedded generation capacity (MVA) | Units less than 100 kVA | NTZEmbedded generation capacity (MVA)Units less than 100 kVA | 1.446
|  | NTZ | Embedded generation capacity (MVA) | Units greater than 100 kVA | NTZEmbedded generation capacity (MVA)Units greater than 100 kVA
|  | RPZ | Substation capacity (winter and summer) (MVA) | Total | RPZSubstation capacity (winter and summer) (MVA)Total | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
|  | RPZ | Substation capacity (winter and summer) (MVA) | Firm delivery | RPZSubstation capacity (winter and summer) (MVA)Firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | RPZ | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | RPZSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | RPZ | Sub-transmission lines capacity | Total (winter) | RPZSub-transmission lines capacityTotal (winter) | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3
|  | RPZ | Sub-transmission lines capacity | Firm delivery (winter) | RPZSub-transmission lines capacityFirm delivery (winter) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | RPZ | Sub-transmission lines capacity | Total (summer) | RPZSub-transmission lines capacityTotal (summer) | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3
|  | RPZ | Sub-transmission lines capacity | Firm delivery (summer) | RPZSub-transmission lines capacityFirm delivery (summer) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | RPZ | Maximum demand forecast(peak season) | Maximum demand (MVA) | RPZMaximum demand forecast(peak season)Maximum demand (MVA) | 15.8764 | 15.1503 | 15.2175 | 14.9433 | 14.778 | 14.7572 | 14.9595 | 15.1315 | 15.3475 | 15.5485 | 15.963 | 16.2412
|  | RPZ | Maximum demand forecast(peak season) | Power factor (coincident) | RPZMaximum demand forecast(peak season)Power factor (coincident) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | RPZ | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | RPZMaximum demand forecast(non-peak season)Maximum demand (MVA) | 8.4629 | 9.8715 | 9.5571 | 9.29 | 9.067 | 9.0111 | 9.0741 | 9.1337 | 9.2278 | 9.3684 | 9.5351 | 9.7121 |  | Summer
|  | RPZ | Maximum demand forecast(non-peak season) | Power factor (coincident) | RPZMaximum demand forecast(non-peak season)Power factor (coincident) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Summer
|  | RPZ | Hours exceeding | 95% of maximum demand | RPZHours exceeding95% of maximum demand | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7
|  | RPZ | Load transfer capacity (MVA) | 1 | RPZLoad transfer capacity (MVA)1
|  | RPZ | Load transfer capacity (MVA) | 2 | RPZLoad transfer capacity (MVA)2
|  | RPZ | Load transfer capacity (MVA) | 3 | RPZLoad transfer capacity (MVA)3
|  | RPZ | Load transfer capacity (MVA) | 4 | RPZLoad transfer capacity (MVA)4
|  | RPZ | Embedded generation capacity (MVA) | Units less than 100 kVA | RPZEmbedded generation capacity (MVA)Units less than 100 kVA | 1.342
|  | RPZ | Embedded generation capacity (MVA) | Units greater than 100 kVA | RPZEmbedded generation capacity (MVA)Units greater than 100 kVA
|  | SBZ | Substation capacity (winter and summer) (MVA) | Total | SBZSubstation capacity (winter and summer) (MVA)Total | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
|  | SBZ | Substation capacity (winter and summer) (MVA) | Firm delivery | SBZSubstation capacity (winter and summer) (MVA)Firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  | SBZ | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | SBZSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78
|  | SBZ | Sub-transmission lines capacity | Total (winter) | SBZSub-transmission lines capacityTotal (winter) | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71
|  | SBZ | Sub-transmission lines capacity | Firm delivery (winter) | SBZSub-transmission lines capacityFirm delivery (winter) | 47.3 | 47.3 | 47.3 | 47.3 | 47.3 | 47.3 | 47.3 | 47.3 | 47.3 | 47.3 | 47.3 | 47.3
|  | SBZ | Sub-transmission lines capacity | Total (summer) | SBZSub-transmission lines capacityTotal (summer) | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5
|  | SBZ | Sub-transmission lines capacity | Firm delivery (summer) | SBZSub-transmission lines capacityFirm delivery (summer) | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9
|  | SBZ | Maximum demand forecast(peak season) | Maximum demand (MVA) | SBZMaximum demand forecast(peak season)Maximum demand (MVA) | 37.5846 | 39.248 | 39.2574 | 38.7716 | 38.4295 | 38.3492 | 38.8584 | 39.3168 | 39.9507 | 40.5843 | 41.8064 | 42.6291
|  | SBZ | Maximum demand forecast(peak season) | Power factor (coincident) | SBZMaximum demand forecast(peak season)Power factor (coincident) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | SBZ | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | SBZMaximum demand forecast(non-peak season)Maximum demand (MVA) | 20.8534 | 18.7989 | 18.2036 | 17.9705 | 17.6707 | 17.6398 | 17.8429 | 18.0825 | 18.416 | 18.947 | 19.5684 | 20.2212 |  | Summer
|  | SBZ | Maximum demand forecast(non-peak season) | Power factor (coincident) | SBZMaximum demand forecast(non-peak season)Power factor (coincident) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Summer
|  | SBZ | Hours exceeding | 95% of maximum demand | SBZHours exceeding95% of maximum demand | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  | SBZ | Load transfer capacity (MVA) | 1 | SBZLoad transfer capacity (MVA)1 | 1.7 | [11 empty] | Kingston
|  | SBZ | Load transfer capacity (MVA) | 2 | SBZLoad transfer capacity (MVA)2 | 13.2 | [11 empty] | West Hobart
|  | SBZ | Load transfer capacity (MVA) | 3 | SBZLoad transfer capacity (MVA)3
|  | SBZ | Load transfer capacity (MVA) | 4 | SBZLoad transfer capacity (MVA)4
|  | SBZ | Embedded generation capacity (MVA) | Units less than 100 kVA | SBZEmbedded generation capacity (MVA)Units less than 100 kVA | 3.212 | 3.212
|  | SBZ | Embedded generation capacity (MVA) | Units greater than 100 kVA | SBZEmbedded generation capacity (MVA)Units greater than 100 kVA
|  | SUZ | Substation capacity (winter and summer) (MVA) | Total | SUZSubstation capacity (winter and summer) (MVA)Total | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
|  | SUZ | Substation capacity (winter and summer) (MVA) | Firm delivery | SUZSubstation capacity (winter and summer) (MVA)Firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | SUZ | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | SUZSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | SUZ | Sub-transmission lines capacity | Total (winter) | SUZSub-transmission lines capacityTotal (winter) | 21.3 | 21.3 | 21.3 | 21.3 | 21.3 | 21.3 | 21.3 | 21.3 | 21.3 | 21.3 | 21.3 | 21.3
|  | SUZ | Sub-transmission lines capacity | Firm delivery (winter) | SUZSub-transmission lines capacityFirm delivery (winter) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | SUZ | Sub-transmission lines capacity | Total (summer) | SUZSub-transmission lines capacityTotal (summer) | 21.3 | 21.3 | 21.3 | 21.3 | 21.3 | 21.3 | 21.3 | 21.3 | 21.3 | 21.3 | 21.3 | 21.3
|  | SUZ | Sub-transmission lines capacity | Firm delivery (summer) | SUZSub-transmission lines capacityFirm delivery (summer) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | SUZ | Maximum demand forecast(peak season) | Maximum demand (MVA) | SUZMaximum demand forecast(peak season)Maximum demand (MVA) | 11.8138 | 12.055 | 12.1258 | 12.0599 | 12.014 | 12.031 | 12.2151 | 12.3675 | 12.5587 | 12.7346 | 13.0894 | 13.3299
|  | SUZ | Maximum demand forecast(peak season) | Power factor (coincident) | SUZMaximum demand forecast(peak season)Power factor (coincident) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | SUZ | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | SUZMaximum demand forecast(non-peak season)Maximum demand (MVA) | 6.0811 | 5.7946 | 5.5758 | 5.519 | 5.416 | 5.3729 | 5.3878 | 5.3999 | 5.4379 | 5.5173 | 5.6174 | 5.7323 |  | Summer
|  | SUZ | Maximum demand forecast(non-peak season) | Power factor (coincident) | SUZMaximum demand forecast(non-peak season)Power factor (coincident) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Summer
|  | SUZ | Hours exceeding | 95% of maximum demand | SUZHours exceeding95% of maximum demand | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  | SUZ | Load transfer capacity (MVA) | 1 | SUZLoad transfer capacity (MVA)1 | 4.9 | [11 empty] | Kingston
|  | SUZ | Load transfer capacity (MVA) | 2 | SUZLoad transfer capacity (MVA)2
|  | SUZ | Load transfer capacity (MVA) | 3 | SUZLoad transfer capacity (MVA)3
|  | SUZ | Load transfer capacity (MVA) | 4 | SUZLoad transfer capacity (MVA)4
|  | SUZ | Embedded generation capacity (MVA) | Units less than 100 kVA | SUZEmbedded generation capacity (MVA)Units less than 100 kVA | 1.311
|  | SUZ | Embedded generation capacity (MVA) | Units greater than 100 kVA | SUZEmbedded generation capacity (MVA)Units greater than 100 kVA
|  | THZ | Substation capacity (winter and summer) (MVA) | Total | THZSubstation capacity (winter and summer) (MVA)Total | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
|  | THZ | Substation capacity (winter and summer) (MVA) | Firm delivery | THZSubstation capacity (winter and summer) (MVA)Firm delivery | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
|  | THZ | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | THZSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26
|  | THZ | Sub-transmission lines capacity | Total (winter) | THZSub-transmission lines capacityTotal (winter) | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1
|  | THZ | Sub-transmission lines capacity | Firm delivery (winter) | THZSub-transmission lines capacityFirm delivery (winter) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | THZ | Sub-transmission lines capacity | Total (summer) | THZSub-transmission lines capacityTotal (summer) | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1
|  | THZ | Sub-transmission lines capacity | Firm delivery (summer) | THZSub-transmission lines capacityFirm delivery (summer) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | THZ | Maximum demand forecast(peak season) | Maximum demand (MVA) | THZMaximum demand forecast(peak season)Maximum demand (MVA) | 2.6591 | 3.1466 | 3.1968 | 2.8121 | 2.6243 | 2.555 | 2.5728 | 2.5956 | 2.629 | 2.6513 | 2.7148 | 2.7584
|  | THZ | Maximum demand forecast(peak season) | Power factor (coincident) | THZMaximum demand forecast(peak season)Power factor (coincident) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | THZ | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | THZMaximum demand forecast(non-peak season)Maximum demand (MVA) | 1.9425 | 2.2437 | 2.2965 | 1.9216 | 1.7276 | 1.6645 | 1.6666 | 1.6788 | 1.6992 | 1.7213 | 1.7495 | 1.7864 |  | Summer
|  | THZ | Maximum demand forecast(non-peak season) | Power factor (coincident) | THZMaximum demand forecast(non-peak season)Power factor (coincident) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Summer
|  | THZ | Hours exceeding | 95% of maximum demand | THZHours exceeding95% of maximum demand | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7
|  | THZ | Load transfer capacity (MVA) | 1 | THZLoad transfer capacity (MVA)1
|  | THZ | Load transfer capacity (MVA) | 2 | THZLoad transfer capacity (MVA)2
|  | THZ | Load transfer capacity (MVA) | 3 | THZLoad transfer capacity (MVA)3
|  | THZ | Load transfer capacity (MVA) | 4 | THZLoad transfer capacity (MVA)4
|  | THZ | Embedded generation capacity (MVA) | Units less than 100 kVA | THZEmbedded generation capacity (MVA)Units less than 100 kVA | 0.11
|  | THZ | Embedded generation capacity (MVA) | Units greater than 100 kVA | THZEmbedded generation capacity (MVA)Units greater than 100 kVA
|  | WHZ | Substation capacity (winter and summer) (MVA) | Total | WHZSubstation capacity (winter and summer) (MVA)Total | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
|  | WHZ | Substation capacity (winter and summer) (MVA) | Firm delivery | WHZSubstation capacity (winter and summer) (MVA)Firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  | WHZ | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | WHZSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78
|  | WHZ | Sub-transmission lines capacity | Total (winter) | WHZSub-transmission lines capacityTotal (winter) | 67.9 | 67.9 | 67.9 | 67.9 | 67.9 | 67.9 | 67.9 | 67.9 | 67.9 | 67.9 | 67.9 | 67.9
|  | WHZ | Sub-transmission lines capacity | Firm delivery (winter) | WHZSub-transmission lines capacityFirm delivery (winter) | 45.3 | 45.3 | 45.3 | 45.3 | 45.3 | 45.3 | 45.3 | 45.3 | 45.3 | 45.3 | 45.3 | 45.3
|  | WHZ | Sub-transmission lines capacity | Total (summer) | WHZSub-transmission lines capacityTotal (summer) | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3
|  | WHZ | Sub-transmission lines capacity | Firm delivery (summer) | WHZSub-transmission lines capacityFirm delivery (summer) | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9
|  | WHZ | Maximum demand forecast(peak season) | Maximum demand (MVA) | WHZMaximum demand forecast(peak season)Maximum demand (MVA) | 37.525 | 37.7186 | 38.7146 | 38.6083 | 38.5951 | 38.8252 | 39.6229 | 40.3429 | 41.2148 | 42.0053 | 43.3042 | 44.3479
|  | WHZ | Maximum demand forecast(peak season) | Power factor (coincident) | WHZMaximum demand forecast(peak season)Power factor (coincident) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | WHZ | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | WHZMaximum demand forecast(non-peak season)Maximum demand (MVA) | 23.1266 | 26.2904 | 27.1819 | 27.3333 | 27.2628 | 27.4879 | 27.9795 | 28.4224 | 28.9438 | 29.527 | 30.1052 | 30.7868 |  | Summer
|  | WHZ | Maximum demand forecast(non-peak season) | Power factor (coincident) | WHZMaximum demand forecast(non-peak season)Power factor (coincident) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Summer
|  | WHZ | Hours exceeding | 95% of maximum demand | WHZHours exceeding95% of maximum demand | 1 | 1 | bar: 4 2023 to 13 2032
|  | WHZ | Load transfer capacity (MVA) | 1 | WHZLoad transfer capacity (MVA)1 | 8.5 | [11 empty] | East Hobart
|  | WHZ | Load transfer capacity (MVA) | 2 | WHZLoad transfer capacity (MVA)2 | 6.4 | [11 empty] | North Hobart
|  | WHZ | Load transfer capacity (MVA) | 3 | WHZLoad transfer capacity (MVA)3 | 8.5 | [11 empty] | Sandy Bay
|  | WHZ | Load transfer capacity (MVA) | 4 | WHZLoad transfer capacity (MVA)4
|  | WHZ | Embedded generation capacity (MVA) | Units less than 100 kVA | WHZEmbedded generation capacity (MVA)Units less than 100 kVA | 1.957
|  | WHZ | Embedded generation capacity (MVA) | Units greater than 100 kVA | WHZEmbedded generation capacity (MVA)Units greater than 100 kVA | 1.1
|  | GRZ | Substation capacity (winter and summer) (MVA) | Total | GRZSubstation capacity (winter and summer) (MVA)Total | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  | GRZ | Substation capacity (winter and summer) (MVA) | Firm delivery | GRZSubstation capacity (winter and summer) (MVA)Firm delivery | 1 | 1 | bar: 4 2023 to 13 2032
|  | GRZ | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | GRZSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3
|  | GRZ | Sub-transmission lines capacity | Total (winter) | GRZSub-transmission lines capacityTotal (winter)
|  | GRZ | Sub-transmission lines capacity | Firm delivery (winter) | GRZSub-transmission lines capacityFirm delivery (winter)
|  | GRZ | Sub-transmission lines capacity | Total (summer) | GRZSub-transmission lines capacityTotal (summer)
|  | GRZ | Sub-transmission lines capacity | Firm delivery (summer) | GRZSub-transmission lines capacityFirm delivery (summer)
|  | GRZ | Maximum demand forecast(peak season) | Maximum demand (MVA) | GRZMaximum demand forecast(peak season)Maximum demand (MVA) | 1.0285 | 1.9864 | 1.9416 | 1.918 | 1.9007 | 1.9054 | 1.9353 | 1.9578 | 1.9863 | 2.0091 | 2.0342 | 2.0542
|  | GRZ | Maximum demand forecast(peak season) | Power factor (coincident) | GRZMaximum demand forecast(peak season)Power factor (coincident) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | GRZ | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | GRZMaximum demand forecast(non-peak season)Maximum demand (MVA) | 0.032832 | 0.31302 | 0.31721 | 0.31313 | 0.31199 | 0.31317 | 0.31973 | 0.32525 | 0.33194 | 0.33786 | 0.34866 | 0.35711 |  | Winter
|  | GRZ | Maximum demand forecast(non-peak season) | Power factor (coincident) | GRZMaximum demand forecast(non-peak season)Power factor (coincident) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Winter
|  | GRZ | Hours exceeding | 95% of maximum demand | GRZHours exceeding95% of maximum demand | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  | GRZ | Load transfer capacity (MVA) | 1 | GRZLoad transfer capacity (MVA)1
|  | GRZ | Load transfer capacity (MVA) | 2 | GRZLoad transfer capacity (MVA)2
|  | GRZ | Load transfer capacity (MVA) | 3 | GRZLoad transfer capacity (MVA)3
|  | GRZ | Load transfer capacity (MVA) | 4 | GRZLoad transfer capacity (MVA)4
|  | GRZ | Embedded generation capacity (MVA) | Units less than 100 kVA | GRZEmbedded generation capacity (MVA)Units less than 100 kVA | 0.116
|  | GRZ | Embedded generation capacity (MVA) | Units greater than 100 kVA | GRZEmbedded generation capacity (MVA)Units greater than 100 kVA
|  | NNZ | Substation capacity (winter and summer) (MVA) | Total | NNZSubstation capacity (winter and summer) (MVA)Total | 10 | 10 | 10 | 15[2] | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
|  | NNZ | Substation capacity (winter and summer) (MVA) | Firm delivery | NNZSubstation capacity (winter and summer) (MVA)Firm delivery | 7.5 | 7.5 | 7.5 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
|  | NNZ | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | NNZSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 10 | 10 | 10 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
|  | NNZ | Sub-transmission lines capacity | Total (winter) | NNZSub-transmission lines capacityTotal (winter)
|  | NNZ | Sub-transmission lines capacity | Firm delivery (winter) | NNZSub-transmission lines capacityFirm delivery (winter)
|  | NNZ | Sub-transmission lines capacity | Total (summer) | NNZSub-transmission lines capacityTotal (summer)
|  | NNZ | Sub-transmission lines capacity | Firm delivery (summer) | NNZSub-transmission lines capacityFirm delivery (summer)
|  | NNZ | Maximum demand forecast(peak season) | Maximum demand (MVA) | NNZMaximum demand forecast(peak season)Maximum demand (MVA)
|  | NNZ | Maximum demand forecast(peak season) | Power factor (coincident) | NNZMaximum demand forecast(peak season)Power factor (coincident)
|  | NNZ | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | NNZMaximum demand forecast(non-peak season)Maximum demand (MVA)
|  | NNZ | Maximum demand forecast(non-peak season) | Power factor (coincident) | NNZMaximum demand forecast(non-peak season)Power factor (coincident)
|  | NNZ | Hours exceeding | 95% of maximum demand | NNZHours exceeding95% of maximum demand
|  | NNZ | Load transfer capacity (MVA) | 1 | NNZLoad transfer capacity (MVA)1
|  | NNZ | Load transfer capacity (MVA) | 2 | NNZLoad transfer capacity (MVA)2
|  | NNZ | Load transfer capacity (MVA) | 3 | NNZLoad transfer capacity (MVA)3
|  | NNZ | Load transfer capacity (MVA) | 4 | NNZLoad transfer capacity (MVA)4
|  | NNZ | Embedded generation capacity (MVA) | Units less than 100 kVA | NNZEmbedded generation capacity (MVA)Units less than 100 kVA | 0.966
|  | NNZ | Embedded generation capacity (MVA) | Units greater than 100 kVA | NNZEmbedded generation capacity (MVA)Units greater than 100 kVA
|  | RIZ | Substation capacity (winter and summer) (MVA) | Total | RIZSubstation capacity (winter and summer) (MVA)Total | 5 | 5 | 5 | 10[2] | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
|  | RIZ | Substation capacity (winter and summer) (MVA) | Firm delivery | RIZSubstation capacity (winter and summer) (MVA)Firm delivery | 2.5 | 2.5 | 2.5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
|  | RIZ | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | RIZSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 3 | 3 | 3 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5
|  | RIZ | Sub-transmission lines capacity | Total (winter) | RIZSub-transmission lines capacityTotal (winter)
|  | RIZ | Sub-transmission lines capacity | Firm delivery (winter) | RIZSub-transmission lines capacityFirm delivery (winter)
|  | RIZ | Sub-transmission lines capacity | Total (summer) | RIZSub-transmission lines capacityTotal (summer)
|  | RIZ | Sub-transmission lines capacity | Firm delivery (summer) | RIZSub-transmission lines capacityFirm delivery (summer)
|  | RIZ | Maximum demand forecast(peak season) | Maximum demand (MVA) | RIZMaximum demand forecast(peak season)Maximum demand (MVA) | 3.2633 | 2.3693 | 2.234 | 2.1185 | 2.0288 | 1.9743 | 1.9521 | 1.9283 | 1.9158 | 1.912 | 1.9179 | 1.9272
|  | RIZ | Maximum demand forecast(peak season) | Power factor (coincident) | RIZMaximum demand forecast(peak season)Power factor (coincident) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | RIZ | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | RIZMaximum demand forecast(non-peak season)Maximum demand (MVA) | 2.957 | 3.8639 | 3.8858 | 3.8119 | 3.7767 | 3.7757 | 3.8355 | 3.8823 | 3.9407 | 3.9928 | 4.0991 | 4.1762 |  | Winter
|  | RIZ | Maximum demand forecast(non-peak season) | Power factor (coincident) | RIZMaximum demand forecast(non-peak season)Power factor (coincident) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Winter
|  | RIZ | Hours exceeding | 95% of maximum demand | RIZHours exceeding95% of maximum demand | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5
|  | RIZ | Load transfer capacity (MVA) | 1 | RIZLoad transfer capacity (MVA)1
|  | RIZ | Load transfer capacity (MVA) | 2 | RIZLoad transfer capacity (MVA)2
|  | RIZ | Load transfer capacity (MVA) | 3 | RIZLoad transfer capacity (MVA)3
|  | RIZ | Load transfer capacity (MVA) | 4 | RIZLoad transfer capacity (MVA)4
|  | RIZ | Embedded generation capacity (MVA) | Units less than 100 kVA | RIZEmbedded generation capacity (MVA)Units less than 100 kVA | 0.706
|  | RIZ | Embedded generation capacity (MVA) | Units greater than 100 kVA | RIZEmbedded generation capacity (MVA)Units greater than 100 kVA
|  | WYZ | Substation capacity (winter and summer) (MVA) | Total | WYZSubstation capacity (winter and summer) (MVA)Total | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
|  | WYZ | Substation capacity (winter and summer) (MVA) | Firm delivery | WYZSubstation capacity (winter and summer) (MVA)Firm delivery | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  | WYZ | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | WYZSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  | WYZ | Sub-transmission lines capacity | Total (winter) | WYZSub-transmission lines capacityTotal (winter)
|  | WYZ | Sub-transmission lines capacity | Firm delivery (winter) | WYZSub-transmission lines capacityFirm delivery (winter)
|  | WYZ | Sub-transmission lines capacity | Total (summer) | WYZSub-transmission lines capacityTotal (summer)
|  | WYZ | Sub-transmission lines capacity | Firm delivery (summer) | WYZSub-transmission lines capacityFirm delivery (summer)
|  | WYZ | Maximum demand forecast(peak season) | Maximum demand (MVA) | WYZMaximum demand forecast(peak season)Maximum demand (MVA) | 0.58305 | 1.2223 | 1.3054 | 1.3072 | 1.3076 | 1.3151 | 1.3209 | 1.3263 | 1.3302 | 1.3398 | 1.3457 | 1.3624
|  | WYZ | Maximum demand forecast(peak season) | Power factor (coincident) | WYZMaximum demand forecast(peak season)Power factor (coincident) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | WYZ | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | WYZMaximum demand forecast(non-peak season)Maximum demand (MVA) | 1.2994 | 1.1687 | 1.3102 | 1.3173 | 1.321 | 1.3362 | 1.3486 | 1.3601 | 1.3692 | 1.3875 | 1.3996 | 1.4293 |  | Winter
|  | WYZ | Maximum demand forecast(non-peak season) | Power factor (coincident) | WYZMaximum demand forecast(non-peak season)Power factor (coincident) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Winter
|  | WYZ | Hours exceeding | 95% of maximum demand | WYZHours exceeding95% of maximum demand | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5
|  | WYZ | Load transfer capacity (MVA) | 1 | WYZLoad transfer capacity (MVA)1
|  | WYZ | Load transfer capacity (MVA) | 2 | WYZLoad transfer capacity (MVA)2
|  | WYZ | Load transfer capacity (MVA) | 3 | WYZLoad transfer capacity (MVA)3
|  | WYZ | Load transfer capacity (MVA) | 4 | WYZLoad transfer capacity (MVA)4
|  | WYZ | Embedded generation capacity (MVA) | Units less than 100 kVA | WYZEmbedded generation capacity (MVA)Units less than 100 kVA | 0
|  | WYZ | Embedded generation capacity (MVA) | Units greater than 100 kVA | WYZEmbedded generation capacity (MVA)Units greater than 100 kVA

## Distribution feeder max. demand
Distribution feeder maximum demand, (Amps) 2021 50% POE forecast.
|  | Summer | [11 empty] | Winter | [11 empty] | NET DER AVERAGE DAY MAX DEMAND IMPACT (kW) | [9 empty] | NET DER AVERAGE DAY MIN DEMAND IMPACT (kW)
Substation | Feeder | 2020 (Actual) | 2021 (Actual) | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2020 (Actual) | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
Arthurs Lake | 49101 | 44.9844 | 37 | 37.2354 | 37.2354 | 37.2354 | 37.2354 | 37.2354 | 37.2354 | 37.2354 | 37.2354 | 37.2354 | 37.2354 | 37 | 37.1425 | 37.1425 | 37.1425 | 37.1425 | 37.1425 | 37.1425 | 37.1425 | 37.1425 | 37.1425 | 37.1425 | 37.1425 | 0.02752 | 0.057228 | 0.093249 | 0.136 | 0.18235 | 0.23622 | 0.29865 | 0.43851 | 0.55622 | 0.66858 | -0.26961 | -0.33479 | -0.40584 | -0.47416 | -0.53303 | -0.58423 | -0.63045 | -0.66926 | -0.71349 | -0.75089
Avoca | 56001 | 6.6197 | 8 | 8.2083 | 8.2083 | 8.2083 | 8.2083 | 8.2083 | 8.2083 | 8.2083 | 8.2083 | 8.2083 | 8.2083 | 12 | 11.9659 | 11.932 | 11.8981 | 11.8644 | 11.8307 | 11.7971 | 11.7636 | 11.7303 | 11.697 | 11.6638 | 11.6307 | 0.0030425 | 0.0062843 | 0.010317 | 0.015415 | 0.021261 | 0.02843 | 0.037041 | 0.057223 | 0.073976 | 0.090166 | -0.027829 | -0.034256 | -0.041011 | -0.047021 | -0.051665 | -0.055005 | -0.05729 | -0.055758 | -0.055503 | -0.054566
Avoca | 56002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0018896 | 0.0039029 | 0.0064074 | 0.0095733 | 0.013204 | 0.017656 | 0.023004 | 0.035538 | 0.045943 | 0.055998 | -0.017283 | -0.021275 | -0.02547 | -0.029203 | -0.032086 | -0.034161 | -0.03558 | -0.034628 | -0.03447 | -0.033888
Avoca | 56003 | 39.6172 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 51.8524 | 51.7053 | 51.5586 | 51.4122 | 51.2663 | 51.1209 | 50.9758 | 50.8311 | 50.6869 | 50.543 | 50.3996 | 0.017449 | 0.03618 | 0.059557 | 0.0891 | 0.12292 | 0.16429 | 0.21385 | 0.32961 | 0.4258 | 0.51863 | -0.13569 | -0.17345 | -0.21357 | -0.24989 | -0.27865 | -0.30025 | -0.31617 | -0.31193 | -0.31524 | -0.31417
Avoca | 56004 | 155.9456 | 208 | 208.6083 | 208.6083 | 208.6083 | 208.6083 | 208.6083 | 208.6083 | 208.6083 | 208.6083 | 208.6083 | 208.6083 | 121 | 122.8766 | 122.5278 | 122.1801 | 121.8334 | 121.4877 | 121.1429 | 120.7991 | 120.4563 | 120.1145 | 119.7736 | 119.4337 | 0.053737 | 0.10641 | 0.17426 | 0.26459 | 0.37207 | 0.50761 | 0.67313 | 1.0679 | 1.394 | 1.7102 | -0.42686 | -0.52749 | -0.63378 | -0.72731 | -0.79777 | -0.84482 | -0.8724 | -0.8165 | -0.78953 | -0.7512
Bellerive Zone | 27171 | 109.9778 | 102 | 102.5759 | 103.0469 | 103.5202 | 103.9956 | 104.4731 | 104.9529 | 105.4349 | 105.9191 | 106.4055 | 106.8942 | 192.6667 | 200.3732 | 201.203 | 202.0363 | 202.8731 | 203.7133 | 204.557 | 205.4042 | 206.2549 | 207.1092 | 207.9669 | 208.8282 | 0.037939 | 0.079921 | 0.12956 | 0.18525 | 0.2424 | 0.30517 | 0.37543 | 0.52619 | 0.65389 | 0.77345 | -0.37011 | -0.4674 | -0.5748 | -0.68119 | -0.77654 | -0.86453 | -0.94921 | -1.0481 | -1.1481 | -1.2372
Bellerive Zone | 27172 | 14.8333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bellerive Zone | 27173 | 23.8667 | 27 | 27.124 | 27.2486 | 27.3737 | 27.4994 | 27.6257 | 27.7526 | 27.88 | 28.008 | 28.1367 | 28.2659 | 39.3333 | 40.5312 | 40.6991 | 40.8676 | 41.0369 | 41.2068 | 41.3775 | 41.5489 | 41.721 | 41.8938 | 42.0673 | 42.2415 | 0.011523 | 0.023477 | 0.037398 | 0.052826 | 0.068544 | 0.085781 | 0.10494 | 0.14583 | 0.18062 | 0.21323 | -0.14094 | -0.16755 | -0.19625 | -0.22389 | -0.24791 | -0.26939 | -0.28942 | -0.31146 | -0.33351 | -0.35275
Bellerive Zone | 27174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bellerive Zone | 27175 | 87.2833 | 77 | 77.3536 | 77.7088 | 78.0657 | 78.4242 | 78.7844 | 79.1462 | 79.5096 | 79.8748 | 80.2416 | 80.6101 | 155 | 161.4367 | 162.1053 | 162.7767 | 163.4508 | 164.1278 | 164.8075 | 165.4901 | 166.1755 | 166.8637 | 167.5548 | 168.2488 | 0.032047 | 0.067515 | 0.10946 | 0.15651 | 0.20479 | 0.25782 | 0.31719 | 0.44456 | 0.55246 | 0.65348 | -0.31248 | -0.39468 | -0.48542 | -0.57532 | -0.65589 | -0.73024 | -0.80181 | -0.8854 | -0.96988 | -1.0452
Bellerive Zone | 27176 | 0 | 163 | 163.7486 | 164.5005 | 165.256 | 166.0149 | 166.7773 | 167.5432 | 168.3126 | 169.0856 | 169.8621 | 170.6421 | 164.6667 | 169.632 | 170.3345 | 171.04 | 171.7484 | 172.4597 | 173.174 | 173.8912 | 174.6114 | 175.3346 | 176.0607 | 176.7899 | 0.010132 | 0.021359 | 0.034635 | 0.049529 | 0.064814 | 0.081604 | 0.1004 | 0.14073 | 0.17489 | 0.20687 | -0.098867 | -0.12488 | -0.1536 | -0.18205 | -0.20755 | -0.23107 | -0.25371 | -0.28014 | -0.30686 | -0.33069
Bellerive Zone | 27178 | 125.1778 | 91.3333 | 93.9838 | 94.4154 | 94.849 | 95.2845 | 95.7221 | 96.1617 | 96.6033 | 97.0469 | 97.4926 | 97.9403 | 117.3333 | 123.0067 | 123.5162 | 124.0277 | 124.5414 | 125.0572 | 125.5751 | 126.0952 | 126.6175 | 127.1419 | 127.6684 | 128.1972 | 0.023769 | 0.050075 | 0.081182 | 0.11608 | 0.15189 | 0.19122 | 0.23525 | 0.32972 | 0.40975 | 0.48467 | -0.23176 | -0.29273 | -0.36003 | -0.42671 | -0.48647 | -0.54161 | -0.59469 | -0.65669 | -0.71935 | -0.77525
Bridgewater | 48180 | 135.007 | 132.5 | 133.5006 | 134.5087 | 135.5244 | 136.5478 | 137.579 | 138.6179 | 139.6647 | 140.7193 | 141.782 | 142.8526 | 311.2 | 317.0685 | 319.3467 | 321.6412 | 323.9521 | 326.2797 | 328.624 | 330.9852 | 333.3633 | 335.7585 | 338.1709 | 340.6007 | 0.046707 | 0.09636 | 0.15488 | 0.22113 | 0.29001 | 0.36705 | 0.45397 | 0.64248 | 0.8019 | 0.9524 | -0.47298 | -0.58295 | -0.70192 | -0.81642 | -0.9157 | -1.0037 | -1.0851 | -1.1686 | -1.2554 | -1.3305
Bridgewater | 48181 | 39.0951 | 165.5 | 168.0727 | 169.3419 | 170.6207 | 171.9091 | 173.2073 | 174.5153 | 175.8331 | 177.1609 | 178.4987 | 179.8467 | 182.3 | 183.9458 | 185.2675 | 186.5986 | 187.9393 | 189.2897 | 190.6497 | 192.0195 | 193.3992 | 194.7887 | 196.1883 | 197.5979 | 0.0029944 | 0.0062268 | 0.010146 | 0.014798 | 0.019841 | 0.025703 | 0.032496 | 0.047713 | 0.060522 | 0.072747 | -0.029336 | -0.036428 | -0.044158 | -0.051592 | -0.057998 | -0.063569 | -0.068598 | -0.072821 | -0.077634 | -0.081703
Bridgewater | 48182 | 221.5616 | 179.5 | 181.4135 | 182.7834 | 184.1637 | 185.5544 | 186.9556 | 188.3674 | 189.7898 | 191.223 | 192.667 | 194.1219 | 263.9 | 272.8203 | 274.7805 | 276.7548 | 278.7433 | 280.746 | 282.7632 | 284.7948 | 286.8411 | 288.902 | 290.9778 | 293.0685 | 0.057998 | 0.12061 | 0.19652 | 0.28663 | 0.38431 | 0.49783 | 0.62942 | 0.92416 | 1.1722 | 1.409 | -0.5682 | -0.70557 | -0.85531 | -0.99929 | -1.1234 | -1.2313 | -1.3287 | -1.4105 | -1.5037 | -1.5825
Bridgewater | 48183 | 141.8571 | 164.6 | 166.1118 | 167.3662 | 168.63 | 169.9034 | 171.1864 | 172.4792 | 173.7816 | 175.0939 | 176.4161 | 177.7483 | 226.2 | 232.2118 | 234.149 | 235.8314 | 237.5258 | 239.2325 | 240.9513 | 242.6826 | 244.4262 | 246.1824 | 247.9512 | 249.7328 | 0.055927 | 0.11491 | 0.18449 | 0.26376 | 0.34675 | 0.44039 | 0.54674 | 0.77954 | 0.9762 | 1.1626 | -0.58692 | -0.71559 | -0.85388 | -0.98559 | -1.0983 | -1.1965 | -1.2856 | -1.3701 | -1.4599 | -1.5366
Bridgewater | 48184 | 145.7371 | 146.7 | 147.8078 | 148.924 | 150.0486 | 151.1816 | 152.3233 | 153.4735 | 154.6325 | 155.8002 | 156.9767 | 158.1621 | 226.8 | 234.9776 | 236.666 | 238.3664 | 240.0791 | 241.804 | 243.5414 | 245.2912 | 247.0536 | 248.8287 | 250.6165 | 252.4172 | 0.04431 | 0.092142 | 0.15014 | 0.21898 | 0.2936 | 0.38034 | 0.48086 | 0.70604 | 0.89557 | 1.0765 | -0.4341 | -0.53904 | -0.65344 | -0.76344 | -0.85823 | -0.94068 | -1.0151 | -1.0776 | -1.1488 | -1.209
Bridgewater | 48185 | 138.6498 | 128.4 | 129.3696 | 130.3465 | 131.3309 | 132.3226 | 133.3218 | 134.3286 | 135.343 | 136.365 | 137.3948 | 138.4323 | 208.7 | 214.408 | 215.9486 | 217.5001 | 219.0629 | 220.6368 | 222.2221 | 223.8188 | 225.4269 | 227.0466 | 228.6779 | 230.321 | 0.044656 | 0.092796 | 0.15121 | 0.22066 | 0.29604 | 0.38377 | 0.48555 | 0.71377 | 0.90582 | 1.0892 | -0.43599 | -0.54148 | -0.65644 | -0.76693 | -0.86204 | -0.94466 | -1.0191 | -1.0809 | -1.1517 | -1.2113
Bridgewater | 48186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgewater | 48188 | 169.4466 | 68.3 | 68.8158 | 69.3354 | 69.859 | 70.3865 | 70.9181 | 71.4536 | 71.9932 | 72.5368 | 73.0846 | 73.6365 | 113.8 | 116.8643 | 117.704 | 118.5497 | 119.4015 | 120.2594 | 121.1234 | 121.9937 | 122.8702 | 123.753 | 124.6422 | 125.5377 | 0.023991 | 0.049889 | 0.081291 | 0.11856 | 0.15897 | 0.20593 | 0.26035 | 0.38227 | 0.48489 | 0.58285 | -0.23503 | -0.29186 | -0.35379 | -0.41335 | -0.46467 | -0.50931 | -0.5496 | -0.58343 | -0.622 | -0.6546
Bridgewater | 48189 | 68.4008 | 67.7 | 68.2112 | 68.7263 | 69.2453 | 69.7682 | 70.2951 | 70.8259 | 71.3607 | 71.8996 | 72.4426 | 72.9896 | 108.9 | 112.3349 | 113.142 | 113.955 | 114.7737 | 115.5984 | 116.4289 | 117.2655 | 118.108 | 118.9566 | 119.8113 | 120.6722 | 0.020141 | 0.041883 | 0.068245 | 0.099537 | 0.13346 | 0.17288 | 0.21857 | 0.32093 | 0.40708 | 0.48931 | -0.19732 | -0.24502 | -0.29702 | -0.34702 | -0.3901 | -0.42758 | -0.46141 | -0.48981 | -0.52218 | -0.54955
Bridgewater | 48190 | 157.4081 | 116.2 | 117.0775 | 117.9616 | 118.8524 | 119.7499 | 120.6542 | 121.5653 | 122.4833 | 123.4082 | 124.3401 | 125.2791 | 177.2 | 184.6849 | 186.0119 | 187.3483 | 188.6944 | 190.0502 | 191.4157 | 192.791 | 194.1762 | 195.5714 | 196.9766 | 198.3918 | 0.039141 | 0.081394 | 0.13263 | 0.19344 | 0.25935 | 0.33597 | 0.42477 | 0.62368 | 0.7911 | 0.95091 | -0.38346 | -0.47616 | -0.57721 | -0.67438 | -0.75811 | -0.83094 | -0.89668 | -0.95187 | -1.0148 | -1.068
Bridgewater | 48191 | 41.0434 | 41.8 | 42.1157 | 42.4337 | 42.7541 | 43.077 | 43.4023 | 43.73 | 44.0602 | 44.393 | 44.7282 | 45.066 | 65.7 | 67.7116 | 68.1981 | 68.6881 | 69.1816 | 69.6787 | 70.1794 | 70.6836 | 71.1914 | 71.703 | 72.2181 | 72.737 | 0.017263 | 0.035704 | 0.057802 | 0.08358 | 0.11112 | 0.14275 | 0.17911 | 0.25981 | 0.32783 | 0.39258 | -0.17432 | -0.21469 | -0.25844 | -0.30035 | -0.33637 | -0.36774 | -0.39612 | -0.42133 | -0.44915 | -0.4728
Bridgewater | 48192 | 221.5616 | 140.4 | 141.4602 | 142.5285 | 143.6048 | 144.6892 | 145.7818 | 146.8827 | 147.9919 | 149.1094 | 150.2354 | 151.3699 | 241.9 | 251.0391 | 252.8428 | 254.6595 | 256.4892 | 258.3321 | 260.1882 | 262.0577 | 263.9405 | 265.8369 | 267.747 | 269.6707 | 0.072647 | 0.14788 | 0.23458 | 0.32959 | 0.42558 | 0.53029 | 0.64637 | 0.89302 | 1.1024 | 1.2989 | -0.7952 | -0.95929 | -1.134 | -1.2995 | -1.441 | -1.5653 | -1.6789 | -1.8005 | -1.9223 | -2.0278
Burnie | 91001 | 126.1722 | 134.6667 | 134.5759 | 134.3025 | 134.0295 | 133.7572 | 133.4854 | 133.2141 | 132.9434 | 132.6732 | 132.4036 | 132.1346 | 149.3333 | 153.1195 | 152.6801 | 152.2419 | 151.8049 | 151.3692 | 150.9348 | 150.5016 | 150.0696 | 149.6389 | 149.2094 | 148.7812 | 0.032916 | 0.062423 | 0.09986 | 0.14826 | 0.20458 | 0.27425 | 0.35831 | 0.55603 | 0.7199 | 0.87832 | -0.26212 | -0.32107 | -0.38415 | -0.44151 | -0.48709 | -0.52122 | -0.54626 | -0.53621 | -0.53929 | -0.53602
Burnie | 91002 | 83.5667 | 76.6667 | 76.5109 | 76.3554 | 76.2002 | 76.0454 | 75.8908 | 75.7366 | 75.5827 | 75.4291 | 75.2758 | 75.1229 | 55.6667 | 57.2859 | 57.1215 | 56.9575 | 56.794 | 56.631 | 56.4685 | 56.3064 | 56.1448 | 55.9837 | 55.823 | 55.6628 | 0.034701 | 0.065675 | 0.10447 | 0.15364 | 0.21003 | 0.27901 | 0.36165 | 0.55457 | 0.71473 | 0.86925 | -0.28074 | -0.34349 | -0.41051 | -0.47165 | -0.5206 | -0.558 | -0.58634 | -0.58246 | -0.59055 | -0.59191
Burnie | 91003 | 135.8833 | 156 | 155.683 | 155.3666 | 155.0509 | 154.7358 | 154.4214 | 154.1076 | 153.7944 | 153.4819 | 153.17 | 152.8587 | 186.6667 | 192.5209 | 191.9684 | 191.4174 | 190.868 | 190.3202 | 189.774 | 189.2293 | 188.6862 | 188.1447 | 187.6047 | 187.0662 | 0.03257 | 0.062894 | 0.099574 | 0.14222 | 0.18736 | 0.23828 | 0.29651 | 0.42351 | 0.52966 | 0.62901 | -0.3076 | -0.3771 | -0.45453 | -0.53156 | -0.60091 | -0.66481 | -0.72625 | -0.7944 | -0.86461 | -0.92736
Burnie | 91004 | 130.2222 | 132.6667 | 132.3971 | 132.128 | 131.8595 | 131.5916 | 131.3242 | 131.0573 | 130.791 | 130.5252 | 130.2599 | 129.9952 | 142.6667 | 142.2572 | 141.8489 | 141.4418 | 141.0358 | 140.6311 | 140.2274 | 139.825 | 139.4237 | 139.0235 | 138.6245 | 138.2266 | 0.032183 | 0.064582 | 0.1031 | 0.14704 | 0.19293 | 0.24432 | 0.30222 | 0.4274 | 0.53311 | 0.63261 | -0.3173 | -0.39039 | -0.47021 | -0.54762 | -0.61532 | -0.67571 | -0.73176 | -0.78924 | -0.84888 | -0.90093
Burnie | 91005 | 168.2 | 62.3333 | 64.049 | 63.9189 | 63.789 | 63.6594 | 63.53 | 63.4009 | 63.2721 | 63.1435 | 63.0152 | 62.8871 | 98.6667 | 108.7941 | 108.4818 | 108.1705 | 107.86 | 107.5504 | 107.2417 | 106.9339 | 106.627 | 106.321 | 106.0159 | 105.7116 | 0.053021 | 0.10679 | 0.17047 | 0.2426 | 0.31746 | 0.40078 | 0.49424 | 0.69517 | 0.86513 | 1.0249 | -0.52773 | -0.64936 | -0.78208 | -0.91077 | -1.0233 | -1.1239 | -1.2174 | -1.3151 | -1.4155 | -1.5034
Burnie | 91006 | 169.6056 | 142 | 144.807 | 144.5127 | 144.219 | 143.926 | 143.6335 | 143.3416 | 143.0503 | 142.7596 | 142.4695 | 142.18 | 214 | 228.1397 | 227.4849 | 226.832 | 226.181 | 225.5318 | 224.8845 | 224.2391 | 223.5955 | 222.9538 | 222.3139 | 221.6758 | 0.077791 | 0.15659 | 0.24999 | 0.35583 | 0.46569 | 0.58789 | 0.7249 | 1.0192 | 1.268 | 1.5018 | -0.77482 | -0.9535 | -1.1488 | -1.3387 | -1.5054 | -1.6548 | -1.7943 | -1.9417 | -2.0931 | -2.2259
Burnie | 91007 | 95.7389 | 60.3333 | 60.6885 | 60.5652 | 60.4421 | 60.3193 | 60.1967 | 60.0744 | 59.9523 | 59.8305 | 59.7089 | 59.5875 | 99 | 101.0215 | 100.7315 | 100.4424 | 100.1542 | 99.8667 | 99.5801 | 99.2943 | 99.0093 | 98.7251 | 98.4418 | 98.1592 | 0.039863 | 0.077006 | 0.1219 | 0.17398 | 0.229 | 0.29096 | 0.36181 | 0.51584 | 0.64462 | 0.76504 | -0.37759 | -0.46292 | -0.55803 | -0.6528 | -0.73824 | -0.81716 | -0.8932 | -0.97841 | -1.0659 | -1.1442
Burnie | 91008 | 270.7833 | 148.3333 | 153.015 | 152.704 | 152.3937 | 152.084 | 151.775 | 151.4666 | 151.1588 | 150.8516 | 150.545 | 150.2391 | 275.6667 | 282.1608 | 281.351 | 280.5435 | 279.7383 | 278.9354 | 278.1348 | 277.3365 | 276.5406 | 275.7469 | 274.9554 | 274.1663 | 0.089155 | 0.17223 | 0.27263 | 0.38912 | 0.51216 | 0.65074 | 0.80919 | 1.1537 | 1.4417 | 1.711 | -0.84449 | -1.0353 | -1.2481 | -1.46 | -1.6511 | -1.8276 | -1.9977 | -2.1883 | -2.3839 | -2.5591
Burnie | 91009 | 91.3944 | 88 | 89.8122 | 89.6297 | 89.4475 | 89.2658 | 89.0844 | 88.9033 | 88.7227 | 88.5424 | 88.3625 | 88.1829 | 156.3333 | 160.3311 | 159.8709 | 159.4121 | 158.9546 | 158.4983 | 158.0434 | 157.5898 | 157.1375 | 156.6865 | 156.2368 | 155.7884 | 0.079978 | 0.15951 | 0.25413 | 0.36136 | 0.47243 | 0.59541 | 0.73265 | 1.0293 | 1.2792 | 1.5126 | -0.79517 | -0.97796 | -1.1796 | -1.3784 | -1.5557 | -1.7178 | -1.8724 | -2.0463 | -2.2225 | -2.3794
Burnie | 91010 | 97.0833 | 86.6667 | 92.0676 | 91.8805 | 91.6938 | 91.5074 | 91.3215 | 91.1359 | 90.9507 | 90.7659 | 90.5814 | 90.3974 | 156.3333 | 161.5629 | 161.0992 | 160.6369 | 160.1758 | 159.7161 | 159.2577 | 158.8006 | 158.3449 | 157.8904 | 157.4372 | 156.9854 | 0.047502 | 0.091762 | 0.14525 | 0.20732 | 0.27288 | 0.34672 | 0.43114 | 0.61468 | 0.76814 | 0.91163 | -0.44994 | -0.55162 | -0.66496 | -0.77788 | -0.87969 | -0.97374 | -1.0644 | -1.1659 | -1.2701 | -1.3635
Burnie | 91011 | 111.7389 | 101 | 100.7948 | 100.5899 | 100.3855 | 100.1815 | 99.9779 | 99.7748 | 99.572 | 99.3697 | 99.1677 | 98.9662 | 85.3333 | 87.2406 | 86.9902 | 86.7406 | 86.4916 | 86.2434 | 85.9959 | 85.749 | 85.5029 | 85.2575 | 85.0128 | 84.7688 | 0.064024 | 0.12135 | 0.18852 | 0.26343 | 0.34012 | 0.42446 | 0.51825 | 0.71797 | 0.88678 | 1.0448 | -0.58688 | -0.71606 | -0.85596 | -0.99062 | -1.1076 | -1.2115 | -1.3076 | -1.4095 | -1.5125 | -1.6019
Burnie | 91012 | 113.4333 | 113 | 112.7704 | 112.5412 | 112.3125 | 112.0843 | 111.8565 | 111.6292 | 111.4024 | 111.176 | 110.9501 | 110.7246 | 62.3333 | 64.7143 | 64.5286 | 64.3434 | 64.1587 | 63.9746 | 63.791 | 63.6079 | 63.4253 | 63.2433 | 63.0618 | 62.8808 | 0.046068 | 0.091432 | 0.1461 | 0.21036 | 0.27944 | 0.3591 | 0.45083 | 0.65484 | 0.82611 | 0.98891 | -0.43326 | -0.53263 | -0.6404 | -0.74318 | -0.83103 | -0.90668 | -0.9741 | -1.0294 | -1.0918 | -1.1438
Cambridge Zone | 29481 | 42.3839 | 37.3 | 37.7735 | 38.2531 | 38.7387 | 39.2305 | 39.7285 | 40.2329 | 40.7436 | 41.2609 | 41.7847 | 42.3152 | 74.1333 | 77.1965 | 77.969 | 78.7492 | 79.5373 | 80.3332 | 81.1371 | 81.949 | 82.7691 | 83.5974 | 84.4339 | 85.2788 | 0.015277 | 0.031392 | 0.050233 | 0.071183 | 0.092567 | 0.11603 | 0.14211 | 0.198 | 0.24546 | 0.28993 | -0.17736 | -0.21361 | -0.25297 | -0.29117 | -0.32467 | -0.3549 | -0.38334 | -0.41523 | -0.44709 | -0.47535
Cambridge Zone | 29482 | 38.1522 | 42.0333 | 42.567 | 43.1073 | 43.6546 | 44.2088 | 44.77 | 45.3384 | 45.914 | 46.4969 | 47.0871 | 47.6849 | 40.8 | 41.2083 | 41.6207 | 42.0372 | 42.4578 | 42.8827 | 43.3118 | 43.7452 | 44.183 | 44.6251 | 45.0717 | 45.5227 | 0.0068795 | 0.013748 | 0.021669 | 0.030379 | 0.03921 | 0.048885 | 0.059643 | 0.082615 | 0.10201 | 0.12024 | -0.093774 | -0.10867 | -0.12448 | -0.1394 | -0.15209 | -0.16314 | -0.17318 | -0.18364 | -0.19413 | -0.20285
Cambridge Zone | 29483 | 86.0311 | 83.5667 | 84.6276 | 85.7019 | 86.7899 | 87.8917 | 89.0075 | 90.1375 | 91.2818 | 92.4406 | 93.6142 | 94.8026 | 160.3667 | 168.4395 | 170.125 | 171.8275 | 173.5469 | 175.2836 | 177.0377 | 178.8093 | 180.5987 | 182.4059 | 184.2312 | 186.0748 | 0.039033 | 0.078004 | 0.12295 | 0.17236 | 0.22247 | 0.27736 | 0.3384 | 0.46874 | 0.5788 | 0.6822 | -0.53205 | -0.61656 | -0.70628 | -0.79094 | -0.8629 | -0.92563 | -0.98257 | -1.0419 | -1.1015 | -1.1509
Cambridge Zone | 29485 | 98.2194 | 96.9333 | 98.1639 | 99.4101 | 100.6721 | 101.9502 | 103.2445 | 104.5552 | 105.8825 | 107.2267 | 108.5879 | 109.9665 | 94.9333 | 102.0003 | 103.021 | 104.0519 | 105.0932 | 106.1448 | 107.207 | 108.2798 | 109.3634 | 110.4578 | 111.5631 | 112.6796 | 4.8791e-05 | 9.7505e-05 | 0.00015368 | 0.00021546 | 0.00027809 | 0.0003467 | 0.000423 | 0.00058592 | 0.0007235 | 0.00085275 | -0.00066506 | -0.0007707 | -0.00088285 | -0.00098868 | -0.0010786 | -0.001157 | -0.0012282 | -0.0013024 | -0.0013768 | -0.0014387
Cambridge Zone | 29486 | 31.9572 | 43.3 | 44.3773 | 44.9407 | 45.5112 | 46.089 | 46.6741 | 47.2666 | 47.8667 | 48.4744 | 49.0898 | 49.713 | 47.6333 | 48.6364 | 49.1231 | 49.6147 | 50.1111 | 50.6126 | 51.1191 | 51.6306 | 52.1473 | 52.6691 | 53.1962 | 53.7285 | 0.0022932 | 0.0045827 | 0.0072231 | 0.010126 | 0.01307 | 0.016295 | 0.019881 | 0.027538 | 0.034004 | 0.040079 | -0.031258 | -0.036223 | -0.041494 | -0.046468 | -0.050695 | -0.054381 | -0.057726 | -0.061212 | -0.064711 | -0.067617
Cambridge Zone | 29488 | 183.5456 | 222.9 | 223.9236 | 224.952 | 225.985 | 227.0228 | 228.0654 | 229.1127 | 230.1649 | 231.2219 | 232.2837 | 233.3505 | 236.2333 | 241.7538 | 242.7551 | 243.7605 | 244.77 | 245.7838 | 246.8017 | 247.8239 | 248.8503 | 249.8809 | 250.9158 | 251.955 | 0.02399 | 0.047128 | 0.073834 | 0.10326 | 0.13315 | 0.16597 | 0.20252 | 0.28074 | 0.34681 | 0.40893 | -0.30199 | -0.35211 | -0.4053 | -0.45545 | -0.49803 | -0.53507 | -0.56862 | -0.6032 | -0.63805 | -0.6671
Cambridge Zone | 29489 | 79.7356 | 87.5 | 87.9018 | 88.3055 | 88.711 | 89.1184 | 89.5277 | 89.9388 | 90.3519 | 90.7668 | 91.1836 | 91.6024 | 108.1667 | 111.9763 | 112.4401 | 112.9058 | 113.3734 | 113.843 | 114.3145 | 114.7879 | 115.2633 | 115.7407 | 116.22 | 116.7014 | 0.010588 | 0.021159 | 0.033349 | 0.046754 | 0.060345 | 0.075235 | 0.09179 | 0.12714 | 0.157 | 0.18505 | -0.14432 | -0.16724 | -0.19158 | -0.21454 | -0.23406 | -0.25108 | -0.26652 | -0.28262 | -0.29877 | -0.31219
Cambridge Zone | 29490 | 46.4928 | 44.8 | 45.0057 | 45.2124 | 45.42 | 45.6286 | 45.8382 | 46.0487 | 46.2602 | 46.4726 | 46.686 | 46.9004 | 80.1 | 84.171 | 84.5196 | 84.8697 | 85.2212 | 85.5741 | 85.9285 | 86.2844 | 86.6418 | 87.0006 | 87.3609 | 87.7228 | 0.01693 | 0.033834 | 0.053328 | 0.074763 | 0.096497 | 0.12031 | 0.14678 | 0.20331 | 0.25105 | 0.2959 | -0.23078 | -0.26743 | -0.30635 | -0.34307 | -0.37428 | -0.40149 | -0.42619 | -0.45193 | -0.47776 | -0.49921
Cambridge Zone | 29491 | 83.6683 | 73.3 | 73.6366 | 73.9748 | 74.3145 | 74.6558 | 74.9986 | 75.343 | 75.689 | 76.0366 | 76.3858 | 76.7366 | 77.0333 | 81.1726 | 81.5088 | 81.8464 | 82.1854 | 82.5257 | 82.8675 | 83.2107 | 83.5554 | 83.9014 | 84.2489 | 84.5978 | 0.0027323 | 0.0054603 | 0.0086063 | 0.012066 | 0.015573 | 0.019415 | 0.023688 | 0.032811 | 0.040516 | 0.047754 | -0.037243 | -0.043159 | -0.049439 | -0.055366 | -0.060403 | -0.064794 | -0.06878 | -0.072933 | -0.077103 | -0.080565
Cambridge Zone | 29492 | 1.6072 | 2.9667 | 2.9803 | 2.994 | 3.0077 | 3.0215 | 3.0354 | 3.0494 | 3.0634 | 3.0774 | 3.0916 | 3.1058 | 2.7333 | 2.7447 | 2.756 | 2.7674 | 2.7789 | 2.7904 | 2.802 | 2.8136 | 2.8252 | 2.8369 | 2.8487 | 2.8605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chapel Street | 20534 | 49.2056 | 32.3113 | 32.4855 | 32.6243 | 32.7637 | 32.9037 | 33.0443 | 33.1855 | 33.3273 | 33.4697 | 33.6127 | 33.7563 | 65.6404 | 68.2348 | 68.5532 | 68.8732 | 69.1946 | 69.5176 | 69.842 | 70.168 | 70.4955 | 70.8245 | 71.155 | 71.4871 | 0.0094116 | 0.019668 | 0.03199 | 0.046165 | 0.061035 | 0.07783 | 0.096934 | 0.13846 | 0.1735 | 0.20645 | -0.089878 | -0.11358 | -0.13996 | -0.1663 | -0.19009 | -0.21216 | -0.23353 | -0.25809 | -0.28317 | -0.30547
Chapel Street | 20535 | 159.1917 | 117.0805 | 117.8285 | 118.332 | 118.8376 | 119.3454 | 119.8553 | 120.3674 | 120.8818 | 121.3983 | 121.917 | 122.4379 | 245.4294 | 256.9479 | 258.1471 | 259.3519 | 260.5624 | 261.7784 | 263.0002 | 264.2277 | 265.4608 | 266.6998 | 267.9445 | 269.1951 | 0.028899 | 0.060803 | 0.099113 | 0.14313 | 0.18926 | 0.24128 | 0.30042 | 0.4288 | 0.53718 | 0.63916 | -0.2774 | -0.35121 | -0.43339 | -0.5155 | -0.58969 | -0.65858 | -0.72533 | -0.8023 | -0.88091 | -0.9509
Chapel Street | 20536 | 85.8128 | 72.3345 | 72.6436 | 72.954 | 73.2657 | 73.5787 | 73.8931 | 74.2089 | 74.5259 | 74.8444 | 75.1642 | 75.4853 | 148.5668 | 154.4958 | 155.2169 | 155.9413 | 156.6691 | 157.4003 | 158.1349 | 158.8729 | 159.6144 | 160.3594 | 161.1078 | 161.8597 | 0.028328 | 0.059147 | 0.096173 | 0.13878 | 0.18347 | 0.23397 | 0.29141 | 0.41627 | 0.52164 | 0.62072 | -0.27034 | -0.34155 | -0.4208 | -0.49993 | -0.57139 | -0.63768 | -0.70185 | -0.77556 | -0.85085 | -0.91777
Chapel Street | 20537 | 74.7111 | 64.2656 | 64.5402 | 64.816 | 65.0929 | 65.371 | 65.6503 | 65.9309 | 66.2126 | 66.4955 | 66.7796 | 67.065 | 133.0495 | 138.9542 | 139.6027 | 140.2543 | 140.9089 | 141.5665 | 142.2272 | 142.891 | 143.5579 | 144.2279 | 144.9011 | 145.5773 | 0.022733 | 0.046966 | 0.076103 | 0.10969 | 0.145 | 0.18497 | 0.23048 | 0.32961 | 0.41321 | 0.49175 | -0.21522 | -0.2711 | -0.33327 | -0.3953 | -0.45126 | -0.50309 | -0.5532 | -0.61044 | -0.66893 | -0.72078
Chapel Street | 20538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chapel Street | 20539 | 46.5806 | 24.6667 | 24.7721 | 24.8779 | 24.9842 | 25.091 | 25.1982 | 25.3058 | 25.414 | 25.5226 | 25.6316 | 25.7411 | 35.5667 | 36.6756 | 36.8468 | 37.0187 | 37.1915 | 37.3651 | 37.5395 | 37.7147 | 37.8907 | 38.0676 | 38.2452 | 38.4237 | 0.0048871 | 0.010096 | 0.01636 | 0.023581 | 0.031171 | 0.039764 | 0.049547 | 0.070858 | 0.08883 | 0.10571 | -0.046268 | -0.05828 | -0.071645 | -0.08498 | -0.097009 | -0.10815 | -0.11893 | -0.13123 | -0.1438 | -0.15495
Chapel Street | 20540 | 128.5856 | 117.4667 | 117.9686 | 118.4726 | 118.9789 | 119.4872 | 119.9978 | 120.5105 | 121.0254 | 121.5426 | 122.0619 | 122.5834 | 129.8 | 134.9237 | 135.5535 | 136.1861 | 136.8217 | 137.4603 | 138.1018 | 138.7464 | 139.3939 | 140.0445 | 140.6981 | 141.3547 | 0.0049695 | 0.010267 | 0.016636 | 0.023978 | 0.031696 | 0.040434 | 0.050382 | 0.072052 | 0.090327 | 0.1075 | -0.047047 | -0.059263 | -0.072853 | -0.086412 | -0.098644 | -0.10998 | -0.12093 | -0.13344 | -0.14623 | -0.15756
Chapel Street | 20541 | 153.1311 | 151.7 | 152.3482 | 152.9991 | 153.6529 | 154.3094 | 154.9688 | 155.6309 | 156.2959 | 156.9637 | 157.6344 | 158.3079 | 243.4333 | 264.8302 | 266.0662 | 267.308 | 268.5555 | 269.8089 | 271.0682 | 272.3333 | 273.6043 | 274.8813 | 276.1642 | 277.4531 | 0.022167 | 0.046059 | 0.07464 | 0.10734 | 0.1415 | 0.17979 | 0.22335 | 0.31781 | 0.39713 | 0.47193 | -0.20511 | -0.26019 | -0.32127 | -0.38199 | -0.43658 | -0.48701 | -0.5356 | -0.59121 | -0.64793 | -0.69809
Chapel Street | 20544 | 175.2044 | 97.8667 | 98.8439 | 99.2662 | 99.6904 | 100.1163 | 100.5441 | 100.9737 | 101.4052 | 101.8385 | 102.2736 | 102.7106 | 149.6333 | 156.2839 | 157.0133 | 157.7461 | 158.4823 | 159.222 | 159.9651 | 160.7117 | 161.4617 | 162.2153 | 162.9724 | 163.733 | 0.02353 | 0.048611 | 0.078768 | 0.11353 | 0.15007 | 0.19145 | 0.23855 | 0.34115 | 0.42768 | 0.50897 | -0.22276 | -0.2806 | -0.34494 | -0.40915 | -0.46706 | -0.52071 | -0.57258 | -0.63182 | -0.69236 | -0.74603
Chapel Street | 20545 | 84.1417 | 30.7 | 30.8312 | 30.9629 | 31.0952 | 31.2281 | 31.3615 | 31.4955 | 31.6301 | 31.7652 | 31.901 | 32.0373 | 58.7 | 61.2276 | 61.5134 | 61.8005 | 62.0889 | 62.3787 | 62.6698 | 62.9623 | 63.2561 | 63.5514 | 63.848 | 64.146 | 0.011696 | 0.024164 | 0.039154 | 0.056435 | 0.0746 | 0.095164 | 0.11858 | 0.16958 | 0.21259 | 0.253 | -0.11073 | -0.13948 | -0.17147 | -0.20338 | -0.23217 | -0.25884 | -0.28462 | -0.31407 | -0.34416 | -0.37084
Chapel Street | 20547 | 25.2616 | 20.52 | 20.6077 | 20.6957 | 20.7842 | 20.873 | 20.9622 | 21.0517 | 21.1417 | 21.232 | 21.3227 | 21.4138 | 44.6567 | 46.4398 | 46.6566 | 46.8743 | 47.0931 | 47.3129 | 47.5337 | 47.7555 | 47.9784 | 48.2024 | 48.4273 | 48.6533 | 0.042967 | 0.090027 | 0.14652 | 0.21144 | 0.27948 | 0.35625 | 0.44352 | 0.63307 | 0.793 | 0.94341 | -0.40996 | -0.51872 | -0.63974 | -0.76056 | -0.86964 | -0.97083 | -1.0688 | -1.1815 | -1.2966 | -1.3988
Chapel Street | 20548 | 173.2144 | 134.6667 | 135.3892 | 135.9677 | 136.5486 | 137.1321 | 137.718 | 138.3065 | 138.8974 | 139.4909 | 140.0869 | 140.6855 | 315 | 328.0311 | 329.562 | 331.1002 | 332.6455 | 334.198 | 335.7577 | 337.3247 | 338.8991 | 340.4808 | 342.0699 | 343.6664 | 0.037051 | 0.077036 | 0.12473 | 0.17912 | 0.23576 | 0.29932 | 0.37136 | 0.52739 | 0.65855 | 0.78148 | -0.33767 | -0.42959 | -0.53122 | -0.63196 | -0.72224 | -0.80539 | -0.8853 | -0.97693 | -1.0697 | -1.151
Chapel Street | 20549 | 106.7889 | 87.4667 | 87.8404 | 88.2157 | 88.5927 | 88.9712 | 89.3514 | 89.7331 | 90.1166 | 90.5016 | 90.8883 | 91.2767 | 158.8 | 166.0962 | 166.8713 | 167.6502 | 168.4326 | 169.2187 | 170.0085 | 170.8019 | 171.5991 | 172.4 | 173.2046 | 174.013 | 0.030319 | 0.063246 | 0.1025 | 0.14718 | 0.19364 | 0.24537 | 0.3042 | 0.43132 | 0.53825 | 0.63839 | -0.27609 | -0.35198 | -0.43595 | -0.51924 | -0.59393 | -0.66279 | -0.72901 | -0.80487 | -0.88216 | -0.9504
Chapel Street | 20551 | 58.3944 | 59.4667 | 60.0501 | 60.3066 | 60.5643 | 60.8231 | 61.083 | 61.344 | 61.6061 | 61.8693 | 62.1337 | 62.3992 | 58.6 | 58.8735 | 59.1483 | 59.4243 | 59.7017 | 59.9803 | 60.2602 | 60.5415 | 60.824 | 61.1079 | 61.3931 | 61.6796 | 0.0059305 | 0.012252 | 0.019853 | 0.028615 | 0.037825 | 0.048252 | 0.060125 | 0.085985 | 0.10779 | 0.12828 | -0.056145 | -0.070722 | -0.086941 | -0.10312 | -0.11772 | -0.13124 | -0.14431 | -0.15925 | -0.1745 | -0.18803
Chapel Street | 20552 | 106.6783 | 85.9667 | 86.334 | 86.7029 | 87.0733 | 87.4454 | 87.819 | 88.1943 | 88.5711 | 88.9496 | 89.3296 | 89.7113 | 188.1 | 195.8258 | 196.7397 | 197.6579 | 198.5804 | 199.5072 | 200.4384 | 201.3738 | 202.3137 | 203.2579 | 204.2065 | 205.1596 | 0.028527 | 0.058934 | 0.095496 | 0.13764 | 0.18195 | 0.2321 | 0.28921 | 0.41361 | 0.51851 | 0.61706 | -0.27007 | -0.34019 | -0.4182 | -0.49604 | -0.56625 | -0.6313 | -0.69417 | -0.766 | -0.83939 | -0.90446
Chapel Street | 20553 | 107.9606 | 91.5333 | 92.4249 | 92.8198 | 93.2164 | 93.6147 | 94.0147 | 94.4164 | 94.8198 | 95.225 | 95.6318 | 96.0405 | 167.2667 | 172.6765 | 173.4824 | 174.2921 | 175.1055 | 175.9228 | 176.7438 | 177.5687 | 178.3975 | 179.2301 | 180.0666 | 180.907 | 0.041629 | 0.082456 | 0.13 | 0.18223 | 0.23487 | 0.29176 | 0.35445 | 0.48784 | 0.60105 | 0.70654 | -0.3846 | -0.47799 | -0.57987 | -0.67963 | -0.76807 | -0.84903 | -0.92639 | -1.018 | -1.1092 | -1.1901
Chapel Street | 20554 | 103.1372 | 96.9 | 97.314 | 97.7298 | 98.1474 | 98.5668 | 98.988 | 99.4109 | 99.8357 | 100.2623 | 100.6907 | 101.1209 | 140.2667 | 143.7856 | 144.4567 | 145.1309 | 145.8082 | 146.4887 | 147.1724 | 147.8593 | 148.5494 | 149.2427 | 149.9392 | 150.639 | 0.011422 | 0.023596 | 0.038235 | 0.055111 | 0.072848 | 0.092931 | 0.1158 | 0.1656 | 0.2076 | 0.24706 | -0.10813 | -0.13621 | -0.16744 | -0.19861 | -0.22672 | -0.25276 | -0.27794 | -0.3067 | -0.33608 | -0.36213
Claremont Zone | 21081 | 112.15 | 101.6667 | 102.0486 | 102.432 | 102.8169 | 103.2032 | 103.5909 | 103.9801 | 104.3708 | 104.7629 | 105.1565 | 105.5516 | 178 | 185.7015 | 186.4731 | 187.248 | 188.0261 | 188.8074 | 189.592 | 190.3798 | 191.1709 | 191.9653 | 192.763 | 193.564 | 0.033206 | 0.069658 | 0.1129 | 0.16176 | 0.21224 | 0.2681 | 0.33114 | 0.46712 | 0.58175 | 0.68898 | -0.29539 | -0.37938 | -0.47201 | -0.56359 | -0.64545 | -0.72069 | -0.79282 | -0.8756 | -0.95979 | -1.0339
Claremont Zone | 21082 | 26.8722 | 30 | 30.1127 | 30.2259 | 30.3394 | 30.4534 | 30.5678 | 30.6827 | 30.7979 | 30.9137 | 31.0298 | 31.1464 | 49 | 50.6315 | 50.8419 | 51.0532 | 51.2653 | 51.4784 | 51.6923 | 51.9071 | 52.1228 | 52.3394 | 52.5569 | 52.7752 | 0.0078271 | 0.016419 | 0.026612 | 0.038129 | 0.050029 | 0.063194 | 0.078054 | 0.11011 | 0.13713 | 0.1624 | -0.069627 | -0.089424 | -0.11126 | -0.13285 | -0.15214 | -0.16988 | -0.18688 | -0.20639 | -0.22624 | -0.24372
Claremont Zone | 21083 | 153.2667 | 169 | 169.635 | 170.2723 | 170.912 | 171.5542 | 172.1987 | 172.8457 | 173.4951 | 174.1469 | 174.8012 | 175.458 | 195.6667 | 199.7311 | 200.561 | 201.3944 | 202.2313 | 203.0717 | 203.9155 | 204.7629 | 205.6137 | 206.4682 | 207.3261 | 208.1876 | 0.010673 | 0.02239 | 0.036289 | 0.051994 | 0.068222 | 0.086174 | 0.10644 | 0.15014 | 0.18699 | 0.22146 | -0.094945 | -0.12194 | -0.15172 | -0.18116 | -0.20747 | -0.23165 | -0.25483 | -0.28144 | -0.3085 | -0.33234
Claremont Zone | 21084 | 140.9722 | 149 | 149.5598 | 150.1217 | 150.6857 | 151.2519 | 151.8202 | 152.3906 | 152.9631 | 153.5378 | 154.1147 | 154.6937 | 176.3333 | 177.8061 | 178.5449 | 179.2869 | 180.0319 | 180.78 | 181.5312 | 182.2856 | 183.043 | 183.8036 | 184.5674 | 185.3344 | 0.0038627 | 0.0081031 | 0.013133 | 0.018817 | 0.02469 | 0.031187 | 0.03852 | 0.054338 | 0.067673 | 0.080147 | -0.034361 | -0.044132 | -0.054907 | -0.065561 | -0.075083 | -0.083835 | -0.092226 | -0.10185 | -0.11165 | -0.12028
Claremont Zone | 21085 | 107.0611 | 135.3333 | 135.8418 | 136.3522 | 136.8645 | 137.3787 | 137.8948 | 138.4129 | 138.9329 | 139.4549 | 139.9789 | 140.5048 | 269.3333 | 280.7973 | 281.9641 | 283.1358 | 284.3123 | 285.4938 | 286.6801 | 287.8714 | 289.0676 | 290.2688 | 291.475 | 292.6862 | 0.049786 | 0.1044 | 0.16925 | 0.24269 | 0.31876 | 0.40312 | 0.49828 | 0.70436 | 0.87804 | 1.0407 | -0.44493 | -0.57049 | -0.70891 | -0.84559 | -0.96758 | -1.0795 | -1.1865 | -1.3081 | -1.4322 | -1.5414
Claremont Zone | 21086 | 83.5778 | 74 | 74.3401 | 74.6194 | 74.8998 | 75.1812 | 75.4636 | 75.7472 | 76.0317 | 76.3174 | 76.6041 | 76.8919 | 141 | 149.6813 | 150.3033 | 150.9279 | 151.5551 | 152.1848 | 152.8172 | 153.4522 | 154.0899 | 154.7302 | 155.3732 | 156.0188 | 0.024193 | 0.050751 | 0.082256 | 0.11785 | 0.15464 | 0.19533 | 0.24126 | 0.34033 | 0.42384 | 0.50197 | -0.21521 | -0.2764 | -0.34389 | -0.41062 | -0.47026 | -0.52507 | -0.57763 | -0.63793 | -0.69927 | -0.7533
Claremont Zone | 21087 | 64.8167 | 52 | 52.1954 | 52.3915 | 52.5883 | 52.7859 | 52.9842 | 53.1833 | 53.3831 | 53.5837 | 53.785 | 53.9871 | 101 | 104.8686 | 105.3043 | 105.7419 | 106.1813 | 106.6226 | 107.0656 | 107.5105 | 107.9573 | 108.4059 | 108.8564 | 109.3087 | 0.021381 | 0.044851 | 0.072694 | 0.10415 | 0.13666 | 0.17262 | 0.21321 | 0.30077 | 0.37457 | 0.44362 | -0.19019 | -0.24427 | -0.30392 | -0.36289 | -0.41559 | -0.46404 | -0.51048 | -0.56378 | -0.61799 | -0.66573
Claremont Zone | 21088 | 34.6833 | 31.6667 | 31.7856 | 31.9051 | 32.0249 | 32.1453 | 32.266 | 32.3873 | 32.5089 | 32.6311 | 32.7537 | 32.8767 | 62.3333 | 64.802 | 65.0712 | 65.3416 | 65.6132 | 65.8858 | 66.1596 | 66.4345 | 66.7106 | 66.9878 | 67.2662 | 67.5457 | 0.012469 | 0.026157 | 0.042395 | 0.060742 | 0.0797 | 0.10067 | 0.12435 | 0.17541 | 0.21845 | 0.25872 | -0.11092 | -0.14246 | -0.17724 | -0.21164 | -0.24237 | -0.27063 | -0.29771 | -0.32879 | -0.36041 | -0.38826
Claremont Zone | 21089 | 92.7944 | 76.3333 | 76.6201 | 76.908 | 77.197 | 77.487 | 77.7781 | 78.0703 | 78.3637 | 78.6581 | 78.9536 | 79.2502 | 157.6667 | 167.6764 | 168.3732 | 169.0729 | 169.7754 | 170.4809 | 171.1893 | 171.9007 | 172.615 | 173.3323 | 174.0526 | 174.7758 | 0.029142 | 0.061132 | 0.099081 | 0.14196 | 0.18628 | 0.2353 | 0.29064 | 0.41 | 0.51064 | 0.60477 | -0.25926 | -0.33297 | -0.41426 | -0.49462 | -0.56645 | -0.63246 | -0.69575 | -0.76835 | -0.84221 | -0.90726
Derby | 55001 | 120.6667 | 116 | 114.6452 | 113.3063 | 111.983 | 110.6752 | 109.3826 | 108.1051 | 106.8426 | 105.5948 | 104.3616 | 103.1427 | 41 | 40.5449 | 40.0949 | 39.6499 | 39.2098 | 38.7747 | 38.3443 | 37.9187 | 37.4978 | 37.0817 | 36.6701 | 36.2631 | 0.075699 | 0.10439 | 0.1393 | 0.18147 | 0.228 | 0.28311 | 0.34779 | 0.49524 | 0.61831 | 0.73615 | -0.33029 | -0.3903 | -0.45438 | -0.5137 | -0.56246 | -0.60196 | -0.63458 | -0.64918 | -0.67169 | -0.68703
Derby | 55002 | 86.4222 | 37.6667 | 37.2707 | 36.8354 | 36.4052 | 35.98 | 35.5598 | 35.1445 | 34.7341 | 34.3284 | 33.9275 | 33.5313 | 36 | 35.6004 | 35.2053 | 34.8146 | 34.4282 | 34.046 | 33.6682 | 33.2945 | 32.9249 | 32.5595 | 32.1981 | 31.8408 | 0.18711 | 0.2175 | 0.2578 | 0.31383 | 0.38252 | 0.47111 | 0.58076 | 0.84596 | 1.0648 | 1.2783 | -0.42976 | -0.48498 | -0.54311 | -0.59294 | -0.62865 | -0.6493 | -0.65706 | -0.60332 | -0.57113 | -0.53241
Derby | 55003 | 40.4667 | 36.3333 | 36.426 | 36.0005 | 35.5801 | 35.1646 | 34.7539 | 34.348 | 33.9468 | 33.5504 | 33.1585 | 32.7713 | 16.6667 | 16.7296 | 16.5439 | 16.3603 | 16.1787 | 15.9991 | 15.8216 | 15.646 | 15.4723 | 15.3006 | 15.1308 | 14.9628 | 0.023242 | 0.031009 | 0.040822 | 0.0534 | 0.06794 | 0.085828 | 0.10734 | 0.15772 | 0.19968 | 0.24024 | -0.083519 | -0.099242 | -0.11613 | -0.13163 | -0.14411 | -0.1537 | -0.16102 | -0.16002 | -0.16247 | -0.16309
Derwent Bridge | 49621 | 0 | 7.1184 | 7.4313 | 7.414 | 7.3968 | 7.3797 | 7.3625 | 7.3454 | 7.3284 | 7.3114 | 7.2944 | 7.2775 | 9.1939 | 9.6594 | 9.6281 | 9.5969 | 9.5658 | 9.5349 | 9.504 | 9.4732 | 9.4425 | 9.4119 | 9.3814 | 9.3511 | 0.0015391 | 0.0030695 | 0.0050262 | 0.0075858 | 0.010591 | 0.014338 | 0.018887 | 0.029646 | 0.038599 | 0.047291 | -0.012944 | -0.015987 | -0.019253 | -0.022232 | -0.024601 | -0.026373 | -0.02767 | -0.027035 | -0.027165 | -0.02698
Derwent Park Zone | 17100 | 106.2 | 105.3333 | 106.0972 | 106.8666 | 107.6416 | 108.4223 | 109.2086 | 110.0005 | 110.7983 | 111.6018 | 112.4111 | 113.2263 | 131.6667 | 132.5927 | 133.2592 | 133.9291 | 134.6024 | 135.2791 | 135.9592 | 136.6426 | 137.3296 | 138.0199 | 138.7138 | 139.4111 | 0.0015731 | 0.0033115 | 0.0053988 | 0.007797 | 0.01031 | 0.013144 | 0.016365 | 0.023357 | 0.02926 | 0.034814 | -0.015106 | -0.019128 | -0.023607 | -0.028081 | -0.032124 | -0.035879 | -0.039517 | -0.043714 | -0.048 | -0.051816
Derwent Park Zone | 17101 | 114.7611 | 116.3333 | 119.0265 | 119.8896 | 120.7591 | 121.6348 | 122.5169 | 123.4054 | 124.3004 | 125.2018 | 126.1098 | 127.0243 | 117.6667 | 122.1316 | 122.7455 | 123.3626 | 123.9827 | 124.606 | 125.2324 | 125.862 | 126.4947 | 127.1306 | 127.7697 | 128.412 | 0.016834 | 0.034283 | 0.05449 | 0.076759 | 0.099354 | 0.12407 | 0.15152 | 0.20991 | 0.25954 | 0.30617 | -0.18208 | -0.22042 | -0.26149 | -0.30072 | -0.33454 | -0.36452 | -0.39225 | -0.42243 | -0.45271 | -0.47909
Derwent Park Zone | 17102 | 10.3444 | 15.6667 | 15.9385 | 16.0541 | 16.1705 | 16.2878 | 16.4059 | 16.5249 | 16.6447 | 16.7654 | 16.887 | 17.0095 | 17.3333 | 18.174 | 18.2654 | 18.3572 | 18.4495 | 18.5422 | 18.6354 | 18.7291 | 18.8233 | 18.9179 | 19.013 | 19.1086 | 2.6255e-05 | 5.5822e-05 | 9.1298e-05 | 0.00013199 | 0.00017455 | 0.00022245 | 0.00027686 | 0.00039475 | 0.00049433 | 0.00058811 | -0.00025403 | -0.00032256 | -0.00039888 | -0.0004752 | -0.00054422 | -0.00060839 | -0.00067064 | -0.00074279 | -0.00081647 | -0.0008822
Derwent Park Zone | 17103 | 102.1889 | 81.3333 | 81.9232 | 82.5173 | 83.1157 | 83.7185 | 84.3256 | 84.9371 | 85.5531 | 86.1735 | 86.7985 | 87.4279 | 135 | 142.2519 | 142.9671 | 143.6858 | 144.4081 | 145.1341 | 145.8637 | 146.5969 | 147.3339 | 148.0746 | 148.819 | 149.5671 | 0.016663 | 0.034428 | 0.055789 | 0.080413 | 0.10629 | 0.1356 | 0.16896 | 0.24163 | 0.30291 | 0.36049 | -0.15777 | -0.19873 | -0.24431 | -0.28979 | -0.33081 | -0.36882 | -0.40555 | -0.44752 | -0.4904 | -0.52842
Derwent Park Zone | 17104 | 81.2222 | 103.3333 | 105.2256 | 105.9887 | 106.7573 | 107.5315 | 108.3113 | 109.0968 | 109.888 | 110.6849 | 111.4876 | 112.2961 | 115.3333 | 118.1755 | 118.7696 | 119.3666 | 119.9667 | 120.5698 | 121.1759 | 121.7851 | 122.3973 | 123.0126 | 123.631 | 124.2525 | 0.0035707 | 0.0075918 | 0.012416 | 0.01795 | 0.023739 | 0.030254 | 0.037653 | 0.053686 | 0.067229 | 0.079983 | -0.034548 | -0.043868 | -0.054248 | -0.064627 | -0.074013 | -0.082741 | -0.091207 | -0.10102 | -0.11104 | -0.11998
Derwent Park Zone | 17105 | 155.6778 | 132.3333 | 133.579 | 134.5477 | 135.5234 | 136.5063 | 137.4962 | 138.4933 | 139.4977 | 140.5093 | 141.5283 | 142.5547 | 211.3333 | 223.8399 | 224.9652 | 226.0961 | 227.2328 | 228.3751 | 229.5232 | 230.677 | 231.8366 | 233.0021 | 234.1735 | 235.3507 | 0.023908 | 0.049942 | 0.08122 | 0.1172 | 0.15496 | 0.1976 | 0.2461 | 0.35154 | 0.44051 | 0.52418 | -0.22825 | -0.2884 | -0.35536 | -0.42222 | -0.48259 | -0.53861 | -0.59283 | -0.65513 | -0.71877 | -0.77534
Derwent Park Zone | 17106 | 159.0833 | 155.3333 | 156.4598 | 157.5945 | 158.7374 | 159.8885 | 161.048 | 162.216 | 163.3924 | 164.5773 | 165.7708 | 166.973 | 192.3333 | 195.3713 | 196.3534 | 197.3405 | 198.3326 | 199.3296 | 200.3317 | 201.3388 | 202.351 | 203.3682 | 204.3906 | 205.4181 | 0.012813 | 0.027241 | 0.044553 | 0.064409 | 0.085181 | 0.10856 | 0.13511 | 0.19264 | 0.24123 | 0.287 | -0.12397 | -0.15741 | -0.19466 | -0.2319 | -0.26558 | -0.29689 | -0.32727 | -0.36248 | -0.39844 | -0.43051
Derwent Park Zone | 17107 | 92.2 | 89.3333 | 89.9812 | 90.6337 | 91.291 | 91.9531 | 92.6199 | 93.2916 | 93.9681 | 94.6496 | 95.336 | 96.0274 | 122.6667 | 129.1154 | 129.7645 | 130.4169 | 131.0725 | 131.7314 | 132.3936 | 133.0592 | 133.7281 | 134.4004 | 135.076 | 135.7551 | 0.0046664 | 0.0098949 | 0.01617 | 0.023369 | 0.030905 | 0.039389 | 0.049028 | 0.069924 | 0.087572 | 0.10419 | -0.045058 | -0.057171 | -0.07066 | -0.084145 | -0.096339 | -0.10767 | -0.11866 | -0.13139 | -0.14438 | -0.15596
Derwent Park Zone | 17108 | 29.8333 | 28 | 28.2405 | 28.4453 | 28.6515 | 28.8593 | 29.0686 | 29.2794 | 29.4918 | 29.7056 | 29.9211 | 30.138 | 51.3333 | 53.5241 | 53.7932 | 54.0636 | 54.3354 | 54.6085 | 54.8831 | 55.159 | 55.4363 | 55.715 | 55.995 | 56.2765 | 0.00079382 | 0.0016431 | 0.0026642 | 0.0038409 | 0.0050773 | 0.0064765 | 0.0080693 | 0.011538 | 0.014463 | 0.017212 | -0.0075262 | -0.0094854 | -0.011665 | -0.013841 | -0.015803 | -0.017622 | -0.01938 | -0.021391 | -0.023446 | -0.025268
Derwent Park Zone | 17109 | 56.7 | 57 | 57.4541 | 57.8708 | 58.2905 | 58.7132 | 59.139 | 59.5679 | 59.9998 | 60.435 | 60.8732 | 61.3147 | 77 | 79.343 | 79.7418 | 80.1427 | 80.5456 | 80.9505 | 81.3575 | 81.7665 | 82.1775 | 82.5906 | 83.0058 | 83.4231 | 0.0026518 | 0.005638 | 0.0092211 | 0.013331 | 0.01763 | 0.022468 | 0.027963 | 0.03987 | 0.049927 | 0.059399 | -0.025657 | -0.032578 | -0.040287 | -0.047995 | -0.054966 | -0.061447 | -0.067735 | -0.075022 | -0.082464 | -0.089102
Devonport | 80001 | 21.1796 | 71.2 | 73.5541 | 73.8654 | 74.178 | 74.492 | 74.8072 | 75.1238 | 75.4418 | 75.7611 | 76.0818 | 76.4038 | 98.4 | 114.0453 | 114.2846 | 114.5244 | 114.7647 | 115.0054 | 115.2467 | 115.4885 | 115.7308 | 115.9737 | 116.217 | 116.4608 | 0.019822 | 0.041208 | 0.066562 | 0.095094 | 0.12444 | 0.1567 | 0.19252 | 0.26948 | 0.33445 | 0.39503 | -0.20361 | -0.25304 | -0.3076 | -0.36146 | -0.40959 | -0.45376 | -0.49601 | -0.54442 | -0.59323 | -0.63679
Devonport | 80002 | 178.7509 | 186.8 | 188.6406 | 189.439 | 190.2408 | 191.046 | 191.8546 | 192.6666 | 193.482 | 194.3009 | 195.1233 | 195.9491 | 199.9767 | 200.3963 | 201.8668 | 202.2903 | 202.7147 | 203.14 | 203.5662 | 203.9933 | 204.4213 | 204.8502 | 205.28 | 205.7107 | 0.0013748 | 0.002858 | 0.0046164 | 0.0065952 | 0.0086306 | 0.010868 | 0.013352 | 0.01869 | 0.023196 | 0.027397 | -0.014122 | -0.017549 | -0.021333 | -0.025069 | -0.028407 | -0.03147 | -0.034401 | -0.037758 | -0.041143 | -0.044165
Devonport | 80003 | 141.4927 | 151.6 | 152.2416 | 152.886 | 153.5331 | 154.1829 | 154.8354 | 155.4908 | 156.1489 | 156.8097 | 157.4734 | 158.1399 | 151.6 | 151.9181 | 152.2368 | 152.5562 | 152.8763 | 153.1971 | 153.5185 | 153.8406 | 154.1633 | 154.4868 | 154.8109 | 155.1357 | 0.037471 | 0.077897 | 0.12582 | 0.17976 | 0.23523 | 0.29622 | 0.36392 | 0.5094 | 0.63223 | 0.74673 | -0.38489 | -0.47832 | -0.58146 | -0.68327 | -0.77425 | -0.85775 | -0.93762 | -1.0291 | -1.1214 | -1.2037
Devonport | 80004 | 161.6666 | 51.6 | 52.5184 | 52.7407 | 52.9639 | 53.1881 | 53.4132 | 53.6392 | 53.8663 | 54.0942 | 54.3232 | 54.5531 | 100.4 | 104.9515 | 105.8717 | 106.0938 | 106.3164 | 106.5395 | 106.763 | 106.987 | 107.2115 | 107.4364 | 107.6618 | 107.8877 | 0.035584 | 0.073976 | 0.11949 | 0.17071 | 0.22339 | 0.28131 | 0.3456 | 0.48376 | 0.6004 | 0.70914 | -0.36552 | -0.45424 | -0.55218 | -0.64888 | -0.73527 | -0.81457 | -0.89042 | -0.97733 | -1.0649 | -1.1431
Devonport | 80005 | 109.9266 | 90.8 | 91.9024 | 92.2913 | 92.682 | 93.0742 | 93.4682 | 93.8638 | 94.261 | 94.66 | 95.0606 | 95.4629 | 144.8 | 148.2489 | 148.56 | 148.8717 | 149.184 | 149.497 | 149.8107 | 150.125 | 150.44 | 150.7556 | 151.0719 | 151.3889 | 0.09119 | 0.18957 | 0.30621 | 0.43746 | 0.57246 | 0.72088 | 0.88563 | 1.2397 | 1.5386 | 1.8172 | -0.93671 | -1.1641 | -1.4151 | -1.6628 | -1.8842 | -2.0874 | -2.2818 | -2.5045 | -2.729 | -2.9294
Devonport | 80006 | 131.1591 | 124 | 124.5248 | 125.0519 | 125.5811 | 126.1126 | 126.6464 | 127.1824 | 127.7207 | 128.2613 | 128.8041 | 129.3493 | 124.3883 | 124.6493 | 124.9108 | 125.1729 | 125.4355 | 125.6987 | 125.9625 | 126.2267 | 126.4916 | 126.757 | 127.0229 | 127.2894 | 0.027509 | 0.056921 | 0.091724 | 0.13079 | 0.17089 | 0.21489 | 0.26368 | 0.36823 | 0.45661 | 0.53898 | -0.28366 | -0.35157 | -0.42642 | -0.50019 | -0.566 | -0.62629 | -0.68387 | -0.74981 | -0.81613 | -0.87529
Devonport | 80007 | 139.3247 | 85.6 | 85.9623 | 86.3261 | 86.6915 | 87.0584 | 87.4269 | 87.7969 | 88.1685 | 88.5416 | 88.9164 | 89.2927 | 218.7841 | 219.715 | 220.176 | 220.638 | 221.1009 | 221.5648 | 222.0297 | 222.4955 | 222.9623 | 223.4301 | 223.8989 | 224.3687 | 0.051826 | 0.10774 | 0.17403 | 0.24862 | 0.32535 | 0.40971 | 0.50334 | 0.70456 | 0.87444 | 1.0328 | -0.53235 | -0.66157 | -0.80421 | -0.94504 | -1.0709 | -1.1864 | -1.2968 | -1.4234 | -1.551 | -1.6649
Devonport | 80008 | 79.9116 | 73.2 | 73.5098 | 73.8209 | 74.1334 | 74.4471 | 74.7622 | 75.0787 | 75.3964 | 75.7155 | 76.036 | 76.3578 | 151.9799 | 154.3648 | 154.6886 | 155.0132 | 155.3384 | 155.6643 | 155.9909 | 156.3182 | 156.6462 | 156.9749 | 157.3042 | 157.6342 | 0.083158 | 0.17288 | 0.27924 | 0.39893 | 0.52205 | 0.6574 | 0.80764 | 1.1305 | 1.4031 | 1.6572 | -0.85419 | -1.0615 | -1.2904 | -1.5164 | -1.7183 | -1.9036 | -2.0808 | -2.2839 | -2.4887 | -2.6714
Devonport | 80009 | 101.6195 | 77.2 | 77.5267 | 77.8549 | 78.1844 | 78.5153 | 78.8476 | 79.1813 | 79.5164 | 79.853 | 80.191 | 80.5304 | 156 | 159.3719 | 159.7063 | 160.0414 | 160.3772 | 160.7137 | 161.0509 | 161.3888 | 161.7274 | 162.0667 | 162.4067 | 162.7475 | 0.051186 | 0.10641 | 0.17188 | 0.24556 | 0.32134 | 0.40465 | 0.49713 | 0.69587 | 0.86365 | 1.0201 | -0.52578 | -0.65341 | -0.79429 | -0.93338 | -1.0577 | -1.1717 | -1.2808 | -1.4058 | -1.5319 | -1.6444
Devonport | 80010 | 153.4709 | 90.4 | 91.0049 | 91.39 | 91.7768 | 92.1653 | 92.5553 | 92.9471 | 93.3405 | 93.7355 | 94.1322 | 94.5307 | 195.183 | 199.8148 | 200.234 | 200.6542 | 201.0751 | 201.497 | 201.9198 | 202.3434 | 202.768 | 203.1934 | 203.6197 | 204.0469 | 0.0068419 | 0.014224 | 0.022975 | 0.032823 | 0.042952 | 0.054088 | 0.06645 | 0.093014 | 0.11544 | 0.13635 | -0.070279 | -0.087339 | -0.10617 | -0.12476 | -0.14137 | -0.15662 | -0.1712 | -0.18791 | -0.20476 | -0.2198
Devonport | 80011 | 73.9472 | 98.4 | 99.3401 | 99.7605 | 100.1827 | 100.6067 | 101.0326 | 101.4602 | 101.8896 | 102.3208 | 102.7539 | 103.1888 | 137.5903 | 140.9143 | 141.2099 | 141.5062 | 141.8031 | 142.1006 | 142.3987 | 142.6975 | 142.9969 | 143.2969 | 143.5976 | 143.8988 | 0.045821 | 0.095596 | 0.15421 | 0.21984 | 0.28717 | 0.3612 | 0.44345 | 0.61851 | 0.7672 | 0.90602 | -0.49828 | -0.61169 | -0.73556 | -0.85615 | -0.96227 | -1.058 | -1.1479 | -1.2471 | -1.3468 | -1.4348
East Hobart Zone | 14060 | 90.1833 | 81.6667 | 82.2589 | 82.8555 | 83.4563 | 84.0616 | 84.6712 | 85.2852 | 85.9037 | 86.5267 | 87.1542 | 87.7862 | 78.3333 | 83.9792 | 84.4013 | 84.8256 | 85.2521 | 85.6806 | 86.1114 | 86.5443 | 86.9793 | 87.4166 | 87.8561 | 88.2977 | 0.002976 | 0.0058417 | 0.0092903 | 0.013326 | 0.017632 | 0.022631 | 0.028354 | 0.041182 | 0.051705 | 0.061487 | -0.030635 | -0.036995 | -0.043949 | -0.050721 | -0.056658 | -0.061972 | -0.066928 | -0.072021 | -0.077121 | -0.081349
East Hobart Zone | 14061 | 100.4722 | 62 | 62.4496 | 62.9025 | 63.3587 | 63.8182 | 64.281 | 64.7471 | 65.2167 | 65.6897 | 66.166 | 66.6459 | 87 | 89.1293 | 89.5773 | 90.0276 | 90.4802 | 90.9351 | 91.3922 | 91.8517 | 92.3134 | 92.7775 | 93.2439 | 93.7126 | 0.0012555 | 0.0024645 | 0.0039193 | 0.0056219 | 0.0074385 | 0.0095475 | 0.011962 | 0.017374 | 0.021813 | 0.02594 | -0.012924 | -0.015607 | -0.018541 | -0.021398 | -0.023903 | -0.026145 | -0.028235 | -0.030384 | -0.032536 | -0.034319
East Hobart Zone | 14062 | 27.6389 | 26.6667 | 26.8601 | 27.0548 | 27.251 | 27.4487 | 27.6477 | 27.8482 | 28.0502 | 28.2536 | 28.4585 | 28.6649 | 28 | 28.709 | 28.8534 | 28.9984 | 29.1442 | 29.2907 | 29.4379 | 29.5859 | 29.7347 | 29.8841 | 30.0344 | 30.1854 | 0.00025575 | 0.00050202 | 0.00079839 | 0.0011452 | 0.0015152 | 0.0019449 | 0.0024367 | 0.0035391 | 0.0044434 | 0.005284 | -0.0026327 | -0.0031792 | -0.0037769 | -0.0043588 | -0.004869 | -0.0053257 | -0.0057517 | -0.0061893 | -0.0066276 | -0.006991
East Hobart Zone | 14063 | 203.2722 | 94 | 94.6817 | 95.3683 | 96.0599 | 96.7566 | 97.4583 | 98.165 | 98.8769 | 99.594 | 100.3163 | 101.0438 | 155.6667 | 158.0246 | 158.819 | 159.6174 | 160.4199 | 161.2263 | 162.0368 | 162.8514 | 163.6701 | 164.4929 | 165.3198 | 166.1509 | 0.0058358 | 0.011455 | 0.018218 | 0.026131 | 0.034575 | 0.044378 | 0.055601 | 0.080756 | 0.10139 | 0.12057 | -0.060073 | -0.072545 | -0.086182 | -0.09946 | -0.1111 | -0.12152 | -0.13124 | -0.14123 | -0.15123 | -0.15952
East Hobart Zone | 14064 | 10.1833 | 71.7647 | 72.2852 | 72.8094 | 73.3374 | 73.8692 | 74.4049 | 74.9445 | 75.488 | 76.0355 | 76.5869 | 77.1423 | 62.7236 | 63.0389 | 63.3558 | 63.6743 | 63.9944 | 64.3161 | 64.6395 | 64.9644 | 65.291 | 65.6192 | 65.9491 | 66.2806 | 0.001302 | 0.0025557 | 0.0040645 | 0.0058301 | 0.007714 | 0.0099011 | 0.012405 | 0.018017 | 0.022621 | 0.026901 | -0.013403 | -0.016185 | -0.019228 | -0.02219 | -0.024788 | -0.027113 | -0.029281 | -0.031509 | -0.033741 | -0.03559
East Hobart Zone | 14065 | 195.1944 | 199 | 200.4432 | 201.8968 | 203.3609 | 204.8357 | 206.3212 | 207.8175 | 209.3246 | 210.8426 | 212.3716 | 213.9118 | 215.6667 | 219.1661 | 220.2679 | 221.3752 | 222.4881 | 223.6066 | 224.7307 | 225.8604 | 226.9959 | 228.137 | 229.2839 | 230.4365 | 0.0071146 | 0.013965 | 0.02221 | 0.031857 | 0.042151 | 0.054103 | 0.067785 | 0.098452 | 0.12361 | 0.14699 | -0.073237 | -0.088441 | -0.10507 | -0.12125 | -0.13545 | -0.14815 | -0.16 | -0.17218 | -0.18437 | -0.19448
East Hobart Zone | 14066 | 182.4611 | 86 | 86.6237 | 87.2519 | 87.8846 | 88.522 | 89.1639 | 89.8106 | 90.4619 | 91.1179 | 91.7787 | 92.4443 | 96.6667 | 97.9955 | 98.4881 | 98.9832 | 99.4808 | 99.981 | 100.4836 | 100.9887 | 101.4964 | 102.0066 | 102.5194 | 103.0348 | 0.0018135 | 0.0035598 | 0.0056613 | 0.0081205 | 0.010744 | 0.013791 | 0.017278 | 0.025096 | 0.031508 | 0.037469 | -0.018668 | -0.022544 | -0.026782 | -0.030908 | -0.034526 | -0.037764 | -0.040784 | -0.043888 | -0.046996 | -0.049572
East Hobart Zone | 14067 | 55.0833 | 54.3333 | 55.4274 | 55.8293 | 56.2342 | 56.642 | 57.0528 | 57.4665 | 57.8833 | 58.3031 | 58.7259 | 59.1518 | 80.6667 | 81.0722 | 82.1797 | 82.5929 | 83.0081 | 83.4254 | 83.8448 | 84.2663 | 84.6899 | 85.1156 | 85.5435 | 85.9736 | 0.002697 | 0.005294 | 0.0084193 | 0.012077 | 0.015979 | 0.020509 | 0.025696 | 0.037322 | 0.046858 | 0.055723 | -0.027763 | -0.033527 | -0.039829 | -0.045966 | -0.051346 | -0.056162 | -0.060654 | -0.065269 | -0.069891 | -0.073723
East Hobart Zone | 14068 | 165.7667 | 130.6667 | 131.6843 | 132.6393 | 133.6012 | 134.57 | 135.546 | 136.5289 | 137.5191 | 138.5163 | 139.5209 | 140.5327 | 150.6667 | 152.6093 | 153.4465 | 154.2179 | 154.9931 | 155.7723 | 156.5554 | 157.3424 | 158.1334 | 158.9284 | 159.7273 | 160.5303 | 0.0038595 | 0.0075759 | 0.012048 | 0.017282 | 0.022866 | 0.02935 | 0.036772 | 0.053409 | 0.067055 | 0.079741 | -0.03973 | -0.047978 | -0.056997 | -0.065778 | -0.073478 | -0.08037 | -0.086798 | -0.093403 | -0.10002 | -0.1055
East Hobart Zone | 14069 | 0 | 132.6667 | 133.6288 | 134.5979 | 135.574 | 136.5572 | 137.5475 | 138.545 | 139.5497 | 140.5617 | 141.5811 | 142.6079 | 125.3333 | 127.0693 | 127.708 | 128.3501 | 128.9953 | 129.6438 | 130.2955 | 130.9505 | 131.6088 | 132.2704 | 132.9354 | 133.6037 | 0.0023837 | 0.0046962 | 0.0074753 | 0.01072 | 0.014174 | 0.018178 | 0.022756 | 0.033002 | 0.041412 | 0.049227 | -0.02429 | -0.029426 | -0.035039 | -0.040503 | -0.045293 | -0.049582 | -0.053584 | -0.057719 | -0.061858 | -0.065289
East Hobart Zone | 14070 | 165.3611 | 137.3333 | 138.3293 | 139.3324 | 140.3429 | 141.3607 | 142.3858 | 143.4184 | 144.4585 | 145.5061 | 146.5613 | 147.6242 | 174 | 176.3921 | 177.2789 | 178.1701 | 179.0658 | 179.966 | 180.8707 | 181.7799 | 182.6938 | 183.6122 | 184.5353 | 185.4629 | 0.003162 | 0.0062068 | 0.0098709 | 0.014159 | 0.018734 | 0.024046 | 0.030127 | 0.043756 | 0.054937 | 0.06533 | -0.03255 | -0.039307 | -0.046696 | -0.053891 | -0.060199 | -0.065845 | -0.071111 | -0.076523 | -0.081942 | -0.086434
East Hobart Zone | 14071 | 0 | 164.3333 | 165.5251 | 166.7255 | 167.9346 | 169.1525 | 170.3792 | 171.6148 | 172.8593 | 174.1129 | 175.3756 | 176.6474 | 164 | 166.6737 | 167.5116 | 168.3537 | 169.2 | 170.0506 | 170.9055 | 171.7646 | 172.6281 | 173.4959 | 174.3681 | 175.2447 | 2.325e-05 | 4.5638e-05 | 7.2581e-05 | 0.00010411 | 0.00013775 | 0.00017681 | 0.00022152 | 0.00032174 | 0.00040395 | 0.00048037 | -0.00023934 | -0.00028902 | -0.00034335 | -0.00039626 | -0.00044264 | -0.00048416 | -0.00052288 | -0.00056267 | -0.00060251 | -0.00063554
East Hobart Zone | 14072 | 0 | 17 | 17.1233 | 17.2475 | 17.3725 | 17.4985 | 17.6254 | 17.7533 | 17.882 | 18.0117 | 18.1423 | 18.2739 | 19 | 19.1289 | 19.2251 | 19.3217 | 19.4189 | 19.5165 | 19.6146 | 19.7132 | 19.8123 | 19.9119 | 20.012 | 20.1126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Electrona | 33271 | 106.3767 | 114.8886 | 115.3507 | 115.8146 | 116.2804 | 116.748 | 117.2175 | 117.6889 | 118.1622 | 118.6374 | 119.1146 | 119.5936 | 162.9543 | 169.4842 | 170.1643 | 170.8471 | 171.5327 | 172.221 | 172.912 | 173.6059 | 174.3025 | 175.0019 | 175.7041 | 176.4092 | 1.2482 | 1.3477 | 1.4653 | 1.6005 | 1.7433 | 1.906 | 2.0921 | 2.5032 | 2.85 | 3.18 | -2.2731 | -2.4886 | -2.7193 | -2.937 | -3.1211 | -3.2788 | -3.4187 | -3.5403 | -3.6737 | -3.782
Electrona | 33272 | 157.539 | 135.0528 | 136.2341 | 136.782 | 137.3321 | 137.8844 | 138.439 | 138.9957 | 139.5547 | 140.116 | 140.6795 | 141.2452 | 256.9754 | 265.9421 | 267.0092 | 268.0806 | 269.1563 | 270.2364 | 271.3207 | 272.4094 | 273.5025 | 274.6 | 275.7019 | 276.8082 | 0.5084 | 0.58839 | 0.68146 | 0.78489 | 0.89072 | 1.0075 | 1.1381 | 1.4184 | 1.6562 | 1.8804 | -1.2832 | -1.4598 | -1.6491 | -1.8294 | -1.9842 | -2.1203 | -2.2448 | -2.375 | -2.5081 | -2.6206
Electrona | 33273 | 8.6727 | 9.8476 | 9.8872 | 9.927 | 9.9669 | 10.007 | 10.0472 | 10.0876 | 10.1282 | 10.1689 | 10.2098 | 10.2509 | 9.8476 | 9.8871 | 9.9268 | 9.9666 | 10.0066 | 10.0468 | 10.0871 | 10.1276 | 10.1682 | 10.209 | 10.25 | 10.2911 | 0.00028553 | 0.00057541 | 0.0009077 | 0.0012658 | 0.001621 | 0.0020002 | 0.0024135 | 0.0032727 | 0.004011 | 0.004699 | -0.0029712 | -0.0036203 | -0.0043163 | -0.0049842 | -0.0055637 | -0.0060831 | -0.006569 | -0.0071327 | -0.0076864 | -0.0081743
Electrona | 33274 | 170.8212 | 166.9402 | 167.6116 | 168.2857 | 168.9625 | 169.642 | 170.3242 | 171.0092 | 171.697 | 172.3875 | 173.0808 | 173.7768 | 255.0997 | 263.5904 | 264.6481 | 265.7101 | 266.7763 | 267.8468 | 268.9215 | 270.0006 | 271.084 | 272.1718 | 273.2639 | 274.3605 | 0.067958 | 0.13695 | 0.21603 | 0.30128 | 0.38581 | 0.47609 | 0.57448 | 0.77903 | 0.95478 | 1.1186 | -0.70691 | -0.86141 | -1.0271 | -1.1861 | -1.324 | -1.4477 | -1.5634 | -1.6976 | -1.8295 | -1.9457
Electrona | 33275 | 5.6939 | 5.8617 | 5.9188 | 5.9426 | 5.9665 | 5.9905 | 6.0146 | 6.0388 | 6.0631 | 6.0875 | 6.1119 | 6.1365 | 11.9578 | 12.4023 | 12.452 | 12.502 | 12.5522 | 12.6025 | 12.6531 | 12.7039 | 12.7548 | 12.806 | 12.8574 | 12.909 | 0.0047968 | 0.0096669 | 0.015249 | 0.021266 | 0.027232 | 0.033603 | 0.040547 | 0.054981 | 0.067384 | 0.078944 | -0.049916 | -0.060821 | -0.072514 | -0.083734 | -0.09347 | -0.1022 | -0.11036 | -0.11983 | -0.12913 | -0.13733
Electrona | 33276 | 131.9458 | 132.9426 | 134.4992 | 135.0401 | 135.5832 | 136.1285 | 136.6759 | 137.2256 | 137.7775 | 138.3316 | 138.8879 | 139.4465 | 230.0117 | 237.0838 | 238.0352 | 238.9903 | 239.9493 | 240.9121 | 241.8788 | 242.8494 | 243.8239 | 244.8023 | 245.7846 | 246.7708 | 0.36289 | 0.4649 | 0.58248 | 0.71249 | 0.84534 | 0.9923 | 1.1569 | 1.5123 | 1.8121 | 2.0947 | -1.3899 | -1.6049 | -1.8307 | -2.0398 | -2.2138 | -2.3611 | -2.4903 | -2.612 | -2.7398 | -2.8425
Electrona | 33277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emu Bay | 90019 | 60.875 | 391.6 | 389.3928 | 387.1981 | 385.0158 | 382.8457 | 380.6879 | 378.5422 | 376.4086 | 374.2871 | 372.1775 | 370.0798 | 370.1 | 373.3354 | 371.7058 | 370.0833 | 368.4679 | 366.8595 | 365.2581 | 363.6638 | 362.0764 | 360.4959 | 358.9223 | 357.3556 | 0.00014919 | 0.0002882 | 0.0004562 | 0.00065113 | 0.00085703 | 0.0010889 | 0.0013541 | 0.0019305 | 0.0024125 | 0.0028632 | -0.0014131 | -0.0017325 | -0.0020884 | -0.0024431 | -0.0027629 | -0.0030582 | -0.0033428 | -0.0036617 | -0.0039892 | -0.0042823
Emu Bay | 90020 | 78.2833 | 84.8 | 84.8518 | 84.3735 | 83.898 | 83.4251 | 82.9549 | 82.4873 | 82.0224 | 81.5601 | 81.1004 | 80.6433 | 108.4 | 113.9942 | 113.4966 | 113.0012 | 112.5079 | 112.0168 | 111.5279 | 111.041 | 110.5564 | 110.0738 | 109.5933 | 109.1149 | 0.0032822 | 0.0063403 | 0.010036 | 0.014325 | 0.018855 | 0.023956 | 0.02979 | 0.042472 | 0.053075 | 0.06299 | -0.031089 | -0.038114 | -0.045946 | -0.053748 | -0.060783 | -0.067281 | -0.073542 | -0.080558 | -0.087761 | -0.094211
Emu Bay | 90021 | 87.6767 | 62.6 | 62.2472 | 61.8963 | 61.5475 | 61.2006 | 60.8556 | 60.5126 | 60.1716 | 59.8324 | 59.4952 | 59.1598 | 95.7 | 98.4515 | 98.0217 | 97.5938 | 97.1678 | 96.7437 | 96.3214 | 95.901 | 95.4824 | 95.0656 | 94.6506 | 94.2375 | 0.0059377 | 0.01147 | 0.018157 | 0.025915 | 0.03411 | 0.043339 | 0.053892 | 0.076835 | 0.096018 | 0.11395 | -0.056243 | -0.068952 | -0.08312 | -0.097235 | -0.10996 | -0.12172 | -0.13304 | -0.14574 | -0.15877 | -0.17044
Emu Bay | 90023 | 96.8633 | 94.7 | 94.1662 | 93.6355 | 93.1077 | 92.583 | 92.0611 | 91.5423 | 91.0263 | 90.5133 | 90.0031 | 89.4958 | 135.2 | 141.8744 | 141.2551 | 140.6385 | 140.0247 | 139.4134 | 138.8049 | 138.199 | 137.5958 | 136.9952 | 136.3972 | 135.8018 | 0.01468 | 0.028359 | 0.04489 | 0.064072 | 0.084331 | 0.10715 | 0.13324 | 0.18996 | 0.23739 | 0.28173 | -0.13905 | -0.17048 | -0.2055 | -0.2404 | -0.27187 | -0.30093 | -0.32893 | -0.36031 | -0.39253 | -0.42138
Emu Bay | 90024 | 85.615 | 84 | 83.5266 | 83.0558 | 82.5876 | 82.1222 | 81.6593 | 81.199 | 80.7414 | 80.2863 | 79.8338 | 79.3838 | 128.9 | 130.0294 | 129.4618 | 128.8967 | 128.3341 | 127.7739 | 127.2162 | 126.6609 | 126.108 | 125.5575 | 125.0095 | 124.4638 | 0.0049829 | 0.0096258 | 0.015237 | 0.021748 | 0.028625 | 0.03637 | 0.045226 | 0.06448 | 0.080578 | 0.09563 | -0.047198 | -0.057865 | -0.069754 | -0.081599 | -0.09228 | -0.10214 | -0.11165 | -0.1223 | -0.13324 | -0.14303
Geilston Bay Zone | 26161 | 120.65 | 81.3333 | 81.7068 | 82.0821 | 82.459 | 82.8377 | 83.2181 | 83.6003 | 83.9842 | 84.3699 | 84.7573 | 85.1466 | 154.6667 | 163.9483 | 164.6273 | 165.3091 | 165.9938 | 166.6813 | 167.3716 | 168.0648 | 168.7609 | 169.4598 | 170.1616 | 170.8664 | 0.027715 | 0.059353 | 0.096797 | 0.13893 | 0.18232 | 0.23018 | 0.28372 | 0.3993 | 0.49747 | 0.58967 | -0.27426 | -0.34699 | -0.4272 | -0.50657 | -0.57763 | -0.64315 | -0.70618 | -0.77925 | -0.8538 | -0.92055
Geilston Bay Zone | 26162 | 106.4778 | 93 | 94.1273 | 94.5596 | 94.9939 | 95.4301 | 95.8683 | 96.3086 | 96.7509 | 97.1952 | 97.6416 | 98.09 | 174.3333 | 184.143 | 184.9057 | 185.6715 | 186.4405 | 187.2126 | 187.988 | 188.7666 | 189.5484 | 190.3334 | 191.1217 | 191.9132 | 0.030739 | 0.065819 | 0.10729 | 0.15386 | 0.2017 | 0.25433 | 0.31324 | 0.43995 | 0.54711 | 0.64745 | -0.30545 | -0.38649 | -0.47581 | -0.56409 | -0.643 | -0.71559 | -0.78525 | -0.86591 | -0.94751 | -1.02
Geilston Bay Zone | 26163 | 64.8 | 56.3333 | 56.7462 | 57.0068 | 57.2685 | 57.5315 | 57.7957 | 58.0612 | 58.3278 | 58.5957 | 58.8648 | 59.1351 | 110.6667 | 115.9174 | 116.3975 | 116.8796 | 117.3637 | 117.8497 | 118.3378 | 118.8279 | 119.3201 | 119.8143 | 120.3105 | 120.8088 | 0.019779 | 0.042353 | 0.069039 | 0.099004 | 0.12979 | 0.16365 | 0.20156 | 0.28309 | 0.35205 | 0.41662 | -0.19655 | -0.24869 | -0.30617 | -0.36297 | -0.41375 | -0.46046 | -0.50528 | -0.55718 | -0.60969 | -0.65637
Geilston Bay Zone | 26164 | 116.2833 | 105 | 105.4822 | 105.9666 | 106.4532 | 106.9421 | 107.4332 | 107.9266 | 108.4222 | 108.9201 | 109.4203 | 109.9228 | 219.6667 | 229.7347 | 230.6862 | 231.6416 | 232.601 | 233.5643 | 234.5316 | 235.503 | 236.4783 | 237.4577 | 238.4412 | 239.4287 | 0.045264 | 0.096921 | 0.15799 | 0.22656 | 0.29701 | 0.37451 | 0.46125 | 0.64784 | 0.80564 | 0.95339 | -0.44978 | -0.56912 | -0.70064 | -0.83064 | -0.94683 | -1.0537 | -1.1563 | -1.2751 | -1.3952 | -1.502
Geilston Bay Zone | 26165 | 106.1611 | 98.6667 | 100.2113 | 100.6715 | 101.1338 | 101.5983 | 102.0648 | 102.5335 | 103.0044 | 103.4774 | 103.9526 | 104.43 | 139 | 149.3122 | 149.9306 | 150.5516 | 151.1751 | 151.8012 | 152.4299 | 153.0612 | 153.6951 | 154.3317 | 154.9709 | 155.6127 | 0.0094159 | 0.020159 | 0.032861 | 0.047122 | 0.061773 | 0.07789 | 0.09593 | 0.13473 | 0.16755 | 0.19828 | -0.093552 | -0.11837 | -0.14573 | -0.17276 | -0.19693 | -0.21917 | -0.2405 | -0.26521 | -0.2902 | -0.31242
Geilston Bay Zone | 26166 | 48.6167 | 49.6667 | 49.8948 | 50.1239 | 50.3541 | 50.5853 | 50.8176 | 51.051 | 51.2854 | 51.521 | 51.7576 | 51.9952 | 93 | 96.6531 | 97.0534 | 97.4553 | 97.859 | 98.2643 | 98.6712 | 99.0799 | 99.4902 | 99.9023 | 100.3161 | 100.7315 | 0.017527 | 0.037531 | 0.061179 | 0.087732 | 0.11501 | 0.14502 | 0.17861 | 0.25086 | 0.31197 | 0.36918 | -0.17417 | -0.22038 | -0.27131 | -0.32165 | -0.36664 | -0.40804 | -0.44775 | -0.49375 | -0.54028 | -0.58164
Geilston Bay Zone | 26167 | 124.4444 | 119.3333 | 120.3958 | 120.9487 | 121.5042 | 122.0622 | 122.6227 | 123.1858 | 123.7515 | 124.3199 | 124.8908 | 125.4643 | 206.3333 | 214.6561 | 215.5451 | 216.4378 | 217.3342 | 218.2343 | 219.1381 | 220.0457 | 220.9571 | 221.8722 | 222.7911 | 223.7138 | 0.023093 | 0.050186 | 0.082495 | 0.11913 | 0.15706 | 0.19905 | 0.24651 | 0.34851 | 0.43523 | 0.5167 | -0.22047 | -0.28361 | -0.35385 | -0.42405 | -0.48757 | -0.54671 | -0.60417 | -0.67166 | -0.74078 | -0.803
Geilston Bay Zone | 26169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
George Town | 53001 | 75.5828 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.053801 | 0.10878 | 0.1715 | 0.23866 | 0.30489 | 0.37522 | 0.45144 | 0.60862 | 0.74247 | 0.86659 | -0.54602 | -0.66845 | -0.79884 | -0.92252 | -1.0286 | -1.1222 | -1.2083 | -1.3055 | -1.4003 | -1.4824
George Town | 53002 | 65.0447 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 6.4896e-05 | 0.00011941 | 0.00018517 | 0.00026422 | 0.00035132 | 0.00045465 | 0.00057613 | 0.00085426 | 0.0010857 | 0.0013076 | -0.00054485 | -0.0006562 | -0.00077303 | -0.00087848 | -0.0009623 | -0.0010269 | -0.0010767 | -0.001085 | -0.0011068 | -0.0011168
George Town | 53003 | 81.4753 | 84 | 84.0827 | 84.0827 | 84.0827 | 84.0827 | 84.0827 | 84.0827 | 84.0827 | 84.0827 | 84.0827 | 84.0827 | 144 | 145.8988 | 145.8988 | 145.8988 | 145.8988 | 145.8988 | 145.8988 | 145.8988 | 145.8988 | 145.8988 | 145.8988 | 145.8988 | 0.10082 | 0.19315 | 0.3006 | 0.41871 | 0.53791 | 0.66702 | 0.80895 | 1.1064 | 1.3596 | 1.5959 | -1.0155 | -1.2256 | -1.4532 | -1.6732 | -1.8654 | -2.0378 | -2.1988 | -2.3789 | -2.5574 | -2.7135
George Town | 53004 | 41.7172 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 55 | 56.1247 | 56.1247 | 56.1247 | 56.1247 | 56.1247 | 56.1247 | 56.1247 | 56.1247 | 56.1247 | 56.1247 | 56.1247 | 0.034004 | 0.068694 | 0.10829 | 0.1507 | 0.19255 | 0.237 | 0.2852 | 0.38465 | 0.46932 | 0.54786 | -0.34496 | -0.42222 | -0.50452 | -0.5826 | -0.64956 | -0.70869 | -0.76306 | -0.82437 | -0.88419 | -0.93599
George Town | 53006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.3654e-05 | 0.00017943 | 0.00027924 | 0.00038896 | 0.00049967 | 0.0006196 | 0.00075143 | 0.0010277 | 0.0012629 | 0.0014823 | -0.00094324 | -0.0011383 | -0.0013498 | -0.0015542 | -0.0017327 | -0.0018929 | -0.0020425 | -0.0022098 | -0.0023756 | -0.0025207
George Town | 53007 | 52.4011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00014048 | 0.00026914 | 0.00041885 | 0.00058343 | 0.00074951 | 0.0009294 | 0.0011271 | 0.0015416 | 0.0018943 | 0.0022235 | -0.0014149 | -0.0017075 | -0.0020247 | -0.0023313 | -0.002599 | -0.0028393 | -0.0030637 | -0.0033147 | -0.0035635 | -0.0037811
George Town | 53008 | 102.5111 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 74 | 74.4246 | 74.4246 | 74.4246 | 74.4246 | 74.4246 | 74.4246 | 74.4246 | 74.4246 | 74.4246 | 74.4246 | 74.4246 | 0.08205 | 0.15146 | 0.23501 | 0.33497 | 0.44463 | 0.57421 | 0.72614 | 1.0729 | 1.3616 | 1.6383 | -0.70184 | -0.84443 | -0.9943 | -1.1301 | -1.2387 | -1.3233 | -1.3895 | -1.4066 | -1.4398 | -1.4577
George Town | 53009 | 86.2789 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 159 | 161.3419 | 161.3419 | 161.3419 | 161.3419 | 161.3419 | 161.3419 | 161.3419 | 161.3419 | 161.3419 | 161.3419 | 161.3419 | 0.087149 | 0.17263 | 0.27087 | 0.37707 | 0.48271 | 0.59573 | 0.71889 | 0.97445 | 1.1919 | 1.3938 | -0.88186 | -1.0737 | -1.2793 | -1.4758 | -1.6454 | -1.796 | -1.9354 | -2.0922 | -2.2459 | -2.3798
George Town | 53010 | 151.1394 | 189 | 190.0394 | 190.0394 | 190.0394 | 190.0394 | 190.0394 | 190.0394 | 190.0394 | 190.0394 | 190.0394 | 190.0394 | 245 | 248.8726 | 248.8726 | 248.8726 | 248.8726 | 248.8726 | 248.8726 | 248.8726 | 248.8726 | 248.8726 | 248.8726 | 248.8726 | 0.0020604 | 0.0039474 | 0.0061432 | 0.008557 | 0.010993 | 0.013631 | 0.016531 | 0.022609 | 0.027783 | 0.032612 | -0.020751 | -0.025044 | -0.029696 | -0.034192 | -0.038119 | -0.041643 | -0.044934 | -0.048616 | -0.052264 | -0.055456
Gordon | 49801 | 9.7898 | 8.3538 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 12.9402 | 13.6069 | 13.6069 | 13.6069 | 13.6069 | 13.6069 | 13.6069 | 13.6069 | 13.6069 | 13.6069 | 13.6069 | 13.6069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gretna Rural Zone | 37001 | 19.0111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5861 | 3.8066 | 3.8066 | 3.8066 | 3.8066 | 3.8066 | 3.8066 | 3.8066 | 3.8066 | 3.8066 | 3.8066 | 3.8066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gretna Rural Zone | 37002 | 98.3944 | 61.6667 | 61.6667 | 61.6667 | 61.6667 | 61.6667 | 61.6667 | 61.6667 | 61.6667 | 61.6667 | 61.6667 | 61.6667 | 18.6667 | 18.9947 | 18.9947 | 18.9947 | 18.9947 | 18.9947 | 18.9947 | 18.9947 | 18.9947 | 18.9947 | 18.9947 | 18.9947 | 0.0068321 | 0.013626 | 0.022311 | 0.033673 | 0.047014 | 0.063648 | 0.083839 | 0.1316 | 0.17134 | 0.20993 | -0.057458 | -0.070968 | -0.085466 | -0.09869 | -0.10921 | -0.11707 | -0.12283 | -0.12001 | -0.12058 | -0.11977
Hadspen | 67081 | 91.4017 | 74 | 74.2794 | 74.5599 | 74.8414 | 75.124 | 75.4076 | 75.6923 | 75.9781 | 76.265 | 76.5529 | 76.842 | 129 | 135.2864 | 135.6236 | 135.9616 | 136.3004 | 136.6401 | 136.9806 | 137.322 | 137.6643 | 138.0074 | 138.3513 | 138.6961 | 0.038756 | 0.074331 | 0.11606 | 0.16249 | 0.2098 | 0.26145 | 0.31847 | 0.44078 | 0.54309 | 0.63786 | -0.37221 | -0.45333 | -0.54177 | -0.62787 | -0.70364 | -0.77215 | -0.83667 | -0.90956 | -0.98154 | -1.0445
Hadspen | 67082 | 137.4444 | 106 | 106.4002 | 106.802 | 107.2052 | 107.61 | 108.0163 | 108.4241 | 108.8335 | 109.2444 | 109.6569 | 110.0709 | 116 | 118.0134 | 118.3075 | 118.6024 | 118.8979 | 119.1943 | 119.4913 | 119.7891 | 120.0877 | 120.387 | 120.687 | 120.9878 | 0.11368 | 0.19477 | 0.29052 | 0.40031 | 0.5161 | 0.64781 | 0.79817 | 1.13 | 1.4087 | 1.6732 | -0.97511 | -1.1497 | -1.3354 | -1.5089 | -1.6537 | -1.7754 | -1.8809 | -1.9638 | -2.056 | -2.1285
Hadspen | 67083 | 214.7206 | 120 | 120.6001 | 121.0555 | 121.5126 | 121.9713 | 122.4319 | 122.8941 | 123.3581 | 123.8239 | 124.2914 | 124.7607 | 128 | 130.3463 | 130.6712 | 130.9968 | 131.3233 | 131.6506 | 131.9787 | 132.3076 | 132.6374 | 132.9679 | 133.2993 | 133.6315 | 0.020732 | 0.03939 | 0.061099 | 0.085105 | 0.10951 | 0.1362 | 0.16578 | 0.22853 | 0.28155 | 0.3311 | -0.21177 | -0.25349 | -0.29837 | -0.34123 | -0.37816 | -0.41072 | -0.44058 | -0.4721 | -0.50365 | -0.53061
Hadspen | 67084 | 150.3664 | 186 | 188.0448 | 188.7548 | 189.4675 | 190.1829 | 190.9009 | 191.6217 | 192.3452 | 193.0715 | 193.8004 | 194.5322 | 155 | 155.3863 | 155.7736 | 156.1618 | 156.551 | 156.9411 | 157.3323 | 157.7244 | 158.1175 | 158.5115 | 158.9066 | 159.3026 | 0.021012 | 0.037734 | 0.057631 | 0.080697 | 0.10525 | 0.1334 | 0.16571 | 0.23741 | 0.29759 | 0.3548 | -0.19332 | -0.2294 | -0.26798 | -0.30412 | -0.33439 | -0.35985 | -0.38192 | -0.39863 | -0.41763 | -0.43258
Hadspen | 67085 | 70.2528 | 68 | 68.4323 | 68.6907 | 68.95 | 69.2104 | 69.4717 | 69.734 | 69.9973 | 70.2616 | 70.5269 | 70.7931 | 110 | 112.6757 | 112.9565 | 113.238 | 113.5202 | 113.8032 | 114.0868 | 114.3711 | 114.6562 | 114.9419 | 115.2284 | 115.5155 | 0.028332 | 0.054425 | 0.085021 | 0.11902 | 0.1536 | 0.19129 | 0.23289 | 0.32194 | 0.39642 | 0.46534 | -0.27028 | -0.3299 | -0.39497 | -0.4584 | -0.51431 | -0.56497 | -0.6128 | -0.66726 | -0.72097 | -0.76799
Hadspen | 67086 | 122.9939 | 85 | 85.6121 | 85.9354 | 86.2598 | 86.5855 | 86.9124 | 87.2406 | 87.57 | 87.9006 | 88.2325 | 88.5656 | 177 | 180.6523 | 181.1025 | 181.5539 | 182.0064 | 182.46 | 182.9147 | 183.3706 | 183.8276 | 184.2857 | 184.745 | 185.2054 | 0.080619 | 0.15487 | 0.24193 | 0.33866 | 0.43707 | 0.54431 | 0.6627 | 0.91608 | 1.128 | 1.3241 | -0.76907 | -0.93874 | -1.1239 | -1.3044 | -1.4635 | -1.6076 | -1.7437 | -1.8987 | -2.0515 | -2.1853
Hadspen | 67087 | 179.2914 | 174 | 175.357 | 176.0191 | 176.6837 | 177.3508 | 178.0204 | 178.6925 | 179.3672 | 180.0445 | 180.7243 | 181.4066 | 200 | 203.5455 | 204.7528 | 205.2631 | 205.7747 | 206.2875 | 206.8016 | 207.317 | 207.8337 | 208.3517 | 208.8709 | 209.3915 | 0.097632 | 0.18804 | 0.29434 | 0.41431 | 0.53869 | 0.67745 | 0.8335 | 1.171 | 1.4553 | 1.7227 | -1.055 | -1.2551 | -1.4704 | -1.6754 | -1.851 | -2.0041 | -2.1427 | -2.2774 | -2.4167 | -2.5333
Hadspen | 67088 | 43.3614 | 42 | 42.3875 | 42.5475 | 42.7081 | 42.8694 | 43.0313 | 43.1937 | 43.3568 | 43.5205 | 43.6848 | 43.8498 | 89 | 89.2508 | 89.4732 | 89.6962 | 89.9198 | 90.1439 | 90.3685 | 90.5938 | 90.8195 | 91.0459 | 91.2728 | 91.5003 | 0.64675 | 0.69521 | 0.75179 | 0.81452 | 0.87832 | 0.94802 | 1.025 | 1.188 | 1.3248 | 1.4519 | -1.1999 | -1.3093 | -1.4278 | -1.5419 | -1.6414 | -1.7302 | -1.8129 | -1.9047 | -1.9952 | -2.072
Hadspen | 67089 | 51.1967 | 47 | 47.6339 | 47.8138 | 47.9943 | 48.1755 | 48.3574 | 48.54 | 48.7233 | 48.9073 | 49.0919 | 49.2773 | 136 | 140.943 | 141.2943 | 141.6464 | 141.9994 | 142.3533 | 142.7081 | 143.0638 | 143.4203 | 143.7777 | 144.1361 | 144.4953 | 0.052368 | 0.1006 | 0.15715 | 0.21999 | 0.28391 | 0.35357 | 0.43047 | 0.59506 | 0.73272 | 0.86012 | -0.49957 | -0.60978 | -0.73005 | -0.84728 | -0.95063 | -1.0443 | -1.1327 | -1.2333 | -1.3326 | -1.4195
Hadspen | 67090 | 157.9622 | 163 | 166.157 | 166.7844 | 167.4141 | 168.0462 | 168.6807 | 169.3176 | 169.9569 | 170.5986 | 171.2427 | 171.8893 | 235 | 235.5857 | 236.1728 | 236.7614 | 237.3515 | 237.943 | 238.536 | 239.1305 | 239.7265 | 240.3239 | 240.9229 | 241.5233 | 0.098667 | 0.19263 | 0.30437 | 0.43358 | 0.57076 | 0.72749 | 0.90689 | 1.3038 | 1.6366 | 1.9524 | -0.94854 | -1.1523 | -1.3705 | -1.5759 | -1.7489 | -1.8956 | -2.0241 | -2.1272 | -2.2415 | -2.3345
Hadspen | 67091 | 64.0836 | 67 | 66.7529 | 67.005 | 67.258 | 67.5119 | 67.7668 | 68.0227 | 68.2795 | 68.5373 | 68.7961 | 69.0558 | 132 | 134.8977 | 135.2339 | 135.5709 | 135.9088 | 136.2475 | 136.5871 | 136.9275 | 137.2687 | 137.6108 | 137.9538 | 138.2976 | 0.051173 | 0.10006 | 0.15802 | 0.22328 | 0.29038 | 0.36408 | 0.44702 | 0.62364 | 0.77132 | 0.90812 | -0.56274 | -0.67558 | -0.80012 | -0.92317 | -1.0332 | -1.1345 | -1.2315 | -1.3442 | -1.4552 | -1.5546
Howrah Zone | 22323 | 66.7528 | 60.6667 | 61.6583 | 62.441 | 63.2337 | 64.0365 | 64.8494 | 65.6727 | 66.5064 | 67.3507 | 68.2057 | 69.0716 | 105.9667 | 111.3695 | 112.484 | 113.6096 | 114.7465 | 115.8947 | 117.0545 | 118.2259 | 119.4089 | 120.6039 | 121.8107 | 123.0297 | 0.017677 | 0.037241 | 0.060375 | 0.086327 | 0.11296 | 0.14221 | 0.17496 | 0.24522 | 0.30473 | 0.36045 | -0.17236 | -0.2177 | -0.26776 | -0.31735 | -0.36179 | -0.4028 | -0.44228 | -0.48838 | -0.53498 | -0.57655
Howrah Zone | 22324 | 72.3022 | 74.2 | 75.4885 | 76.4468 | 77.4173 | 78.4001 | 79.3954 | 80.4033 | 81.4241 | 82.4578 | 83.5046 | 84.5647 | 117.9 | 127.5163 | 128.7924 | 130.0812 | 131.3829 | 132.6977 | 134.0256 | 135.3668 | 136.7214 | 138.0896 | 139.4714 | 140.8671 | 0.020918 | 0.043569 | 0.070325 | 0.10036 | 0.13122 | 0.1652 | 0.20313 | 0.28498 | 0.35434 | 0.41937 | -0.21441 | -0.26647 | -0.32376 | -0.38032 | -0.43081 | -0.47722 | -0.52173 | -0.57315 | -0.62517 | -0.67169
Howrah Zone | 22325 | 85.8122 | 80.7667 | 81.792 | 82.8304 | 83.8819 | 84.9468 | 86.0252 | 87.1173 | 88.2233 | 89.3433 | 90.4775 | 91.6261 | 165.9333 | 174.1466 | 175.8893 | 177.6494 | 179.4271 | 181.2227 | 183.0361 | 184.8678 | 186.7178 | 188.5862 | 190.4734 | 192.3795 | 0.031376 | 0.066099 | 0.10716 | 0.15322 | 0.20049 | 0.25241 | 0.31054 | 0.43523 | 0.54087 | 0.63976 | -0.30592 | -0.3864 | -0.47524 | -0.56326 | -0.64213 | -0.71493 | -0.785 | -0.86683 | -0.94954 | -1.0233
Howrah Zone | 22326 | 30.3761 | 28.6667 | 29.0306 | 29.3991 | 29.7724 | 30.1503 | 30.5331 | 30.9207 | 31.3133 | 31.7108 | 32.1134 | 32.521 | 52.4 | 54.7456 | 55.2934 | 55.8468 | 56.4056 | 56.9701 | 57.5402 | 58.116 | 58.6975 | 59.2849 | 59.8782 | 60.4774 | 0.0093532 | 0.019607 | 0.031833 | 0.045685 | 0.06002 | 0.075873 | 0.093784 | 0.13226 | 0.16496 | 0.19566 | -0.085883 | -0.10981 | -0.13644 | -0.16306 | -0.18715 | -0.20958 | -0.23139 | -0.25703 | -0.28324 | -0.30682
Howrah Zone | 22328 | 88.0033 | 80.3667 | 81.3869 | 82.4201 | 83.4665 | 84.5261 | 85.5992 | 86.6859 | 87.7863 | 88.9008 | 90.0294 | 91.1723 | 166.6333 | 173.7035 | 175.4417 | 177.1974 | 178.9706 | 180.7615 | 182.5704 | 184.3974 | 186.2427 | 188.1064 | 189.9888 | 191.89 | 0.030284 | 0.0638 | 0.10343 | 0.14789 | 0.19352 | 0.24363 | 0.29973 | 0.42009 | 0.52205 | 0.6175 | -0.29528 | -0.37296 | -0.45871 | -0.54366 | -0.61979 | -0.69005 | -0.75768 | -0.83667 | -0.9165 | -0.98772
Howrah Zone | 22329 | 111.7378 | 103.9667 | 105.2865 | 106.6232 | 107.9768 | 109.3475 | 110.7357 | 112.1415 | 113.5652 | 115.0069 | 116.4669 | 117.9455 | 211.6333 | 224.0083 | 226.2499 | 228.514 | 230.8007 | 233.1104 | 235.4431 | 237.7992 | 240.1788 | 242.5823 | 245.0098 | 247.4616 | 0.036013 | 0.075863 | 0.12298 | 0.17585 | 0.23009 | 0.28968 | 0.35638 | 0.49949 | 0.62072 | 0.73422 | -0.35129 | -0.44364 | -0.54558 | -0.64658 | -0.73709 | -0.82061 | -0.90101 | -0.99489 | -1.0898 | -1.1744
Howrah Zone | 22330 | 7.5306 | 7.2333 | 7.3419 | 7.4351 | 7.5295 | 7.6251 | 7.7219 | 7.82 | 7.9192 | 8.0198 | 8.1216 | 8.2247 | 12.9667 | 13.5296 | 13.665 | 13.8017 | 13.9398 | 14.0793 | 14.2202 | 14.3625 | 14.5062 | 14.6514 | 14.798 | 14.9461 | 0.0020333 | 0.0042625 | 0.0069201 | 0.0099315 | 0.013048 | 0.016494 | 0.020388 | 0.028751 | 0.035861 | 0.042535 | -0.01867 | -0.023872 | -0.02966 | -0.035447 | -0.040684 | -0.045562 | -0.050301 | -0.055876 | -0.061574 | -0.066701
Howrah Zone | 22331 | 111.0217 | 109.4333 | 110.8226 | 112.2295 | 113.6543 | 115.0971 | 116.5583 | 118.038 | 119.5365 | 121.0541 | 122.5909 | 124.1472 | 205.7667 | 214.9724 | 217.1236 | 219.2964 | 221.4909 | 223.7073 | 225.946 | 228.207 | 230.4907 | 232.7972 | 235.1268 | 237.4797 | 0.037847 | 0.079732 | 0.12926 | 0.18483 | 0.24184 | 0.30448 | 0.37459 | 0.52502 | 0.65245 | 0.77175 | -0.36902 | -0.46609 | -0.57325 | -0.67942 | -0.77457 | -0.86237 | -0.94689 | -1.0456 | -1.1454 | -1.2344
Huon River | 38422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00026215 | 0.00050237 | 0.00078565 | 0.0011076 | 0.0014439 | 0.0018224 | 0.0022516 | 0.0031885 | 0.0039825 | 0.0047358 | -0.0025183 | -0.0030478 | -0.003618 | -0.0041619 | -0.004628 | -0.0050347 | -0.0054034 | -0.0057548 | -0.0061269 | -0.0064464
Huon River | 38423 | 56.0658 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 65.6 | 67.0939 | 67.0939 | 67.0939 | 67.0939 | 67.0939 | 67.0939 | 67.0939 | 67.0939 | 67.0939 | 67.0939 | 67.0939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kermandie | 31002 | 126.0701 | 105.2755 | 105.8712 | 106.4703 | 107.0728 | 107.6786 | 108.2879 | 108.9007 | 109.5169 | 110.1366 | 110.7598 | 111.3866 | 117.6241 | 119.1791 | 119.7788 | 120.3815 | 120.9873 | 121.5961 | 122.208 | 122.823 | 123.441 | 124.0622 | 124.6865 | 125.3139 | 0.022521 | 0.043303 | 0.067783 | 0.095565 | 0.12455 | 0.15714 | 0.19408 | 0.27465 | 0.34296 | 0.40776 | -0.21488 | -0.26064 | -0.30985 | -0.35675 | -0.39689 | -0.43187 | -0.46354 | -0.49369 | -0.52562 | -0.55302
Kermandie | 31007 | 94.5851 | 92.6143 | 93.3669 | 93.8952 | 94.4265 | 94.9608 | 95.4981 | 96.0385 | 96.582 | 97.1285 | 97.6781 | 98.2308 | 133.9586 | 138.1821 | 138.8775 | 139.5763 | 140.2787 | 140.9846 | 141.694 | 142.407 | 143.1236 | 143.8439 | 144.5677 | 145.2952 | 0.051332 | 0.10244 | 0.16217 | 0.22903 | 0.29791 | 0.3744 | 0.4602 | 0.64523 | 0.80153 | 0.94873 | -0.5206 | -0.63315 | -0.75358 | -0.86751 | -0.96442 | -1.0483 | -1.1236 | -1.1961 | -1.2711 | -1.3342
Kermandie | 31008 | 120.6461 | 128.2532 | 129.0743 | 129.8047 | 130.5392 | 131.2779 | 132.0207 | 132.7677 | 133.519 | 134.2745 | 135.0343 | 135.7984 | 159.6718 | 163.2546 | 164.0761 | 164.9017 | 165.7315 | 166.5655 | 167.4037 | 168.2461 | 169.0927 | 169.9436 | 170.7988 | 171.6583 | 0.053798 | 0.10734 | 0.17036 | 0.2417 | 0.31593 | 0.39908 | 0.49298 | 0.69699 | 0.86941 | 1.0324 | -0.5359 | -0.65414 | -0.78134 | -0.9024 | -1.006 | -1.0961 | -1.1775 | -1.2552 | -1.3367 | -1.4062
Kermandie | 31010 | 79.6066 | 59.0074 | 59.4876 | 59.8242 | 60.1628 | 60.5032 | 60.8455 | 61.1898 | 61.5361 | 61.8843 | 62.2345 | 62.5866 | 77.2958 | 81.303 | 81.8584 | 82.2703 | 82.6843 | 83.1004 | 83.5186 | 83.9388 | 84.3612 | 84.7857 | 85.2124 | 85.6412 | 0.024333 | 0.048174 | 0.075946 | 0.10692 | 0.13873 | 0.17397 | 0.21343 | 0.29839 | 0.3701 | 0.43757 | -0.24684 | -0.29909 | -0.35482 | -0.40735 | -0.45186 | -0.49025 | -0.52457 | -0.5575 | -0.59145 | -0.61986
Kingston (11 kV) | 34251 | 88.425 | 76.2 | 76.7946 | 77.1377 | 77.4823 | 77.8284 | 78.176 | 78.5252 | 78.876 | 79.2283 | 79.5822 | 79.9377 | 154.9 | 159.2284 | 159.9076 | 160.5897 | 161.2747 | 161.9626 | 162.6535 | 163.3473 | 164.0441 | 164.7438 | 165.4465 | 166.1522 | 0.037144 | 0.074473 | 0.1176 | 0.1644 | 0.21105 | 0.26095 | 0.31538 | 0.42992 | 0.52751 | 0.61828 | -0.36205 | -0.44727 | -0.53967 | -0.62955 | -0.70868 | -0.78067 | -0.84901 | -0.93012 | -1.01 | -1.0808
Kingston (11 kV) | 34252 | 163.7524 | 131.7 | 132.5824 | 133.1747 | 133.7695 | 134.3671 | 134.9673 | 135.5702 | 136.1758 | 136.7841 | 137.3951 | 138.0088 | 289.1 | 300.4582 | 301.7398 | 303.0269 | 304.3195 | 305.6176 | 306.9212 | 308.2304 | 309.5452 | 310.8656 | 312.1916 | 313.5232 | 0.068902 | 0.13677 | 0.21646 | 0.30529 | 0.39606 | 0.49559 | 0.60617 | 0.84268 | 1.0442 | 1.2332 | -0.64568 | -0.80101 | -0.97082 | -1.137 | -1.2839 | -1.4175 | -1.5441 | -1.6877 | -1.8327 | -1.9612
Kingston (11 kV) | 34253 | 72.9516 | 62.7 | 63.0525 | 63.3341 | 63.617 | 63.9012 | 64.1867 | 64.4734 | 64.7614 | 65.0507 | 65.3412 | 65.6331 | 146.8 | 152.2296 | 152.879 | 153.5311 | 154.186 | 154.8437 | 155.5041 | 156.1675 | 156.8336 | 157.5026 | 158.1744 | 158.8491 | 0.03634 | 0.072705 | 0.11477 | 0.16047 | 0.20601 | 0.25471 | 0.30776 | 0.41969 | 0.51485 | 0.60329 | -0.36497 | -0.44845 | -0.53921 | -0.62782 | -0.70612 | -0.77765 | -0.84582 | -0.92739 | -1.0075 | -1.0787
Kingston (11 kV) | 34254 | 8.5267 | 11.2 | 11.25 | 11.3003 | 11.3508 | 11.4015 | 11.4524 | 11.5036 | 11.5549 | 11.6066 | 11.6584 | 11.7105 | 20.9 | 20.9891 | 21.0787 | 21.1686 | 21.2589 | 21.3496 | 21.4406 | 21.5321 | 21.6239 | 21.7162 | 21.8088 | 21.9018 | 3.8243e-05 | 7.5287e-05 | 0.00011753 | 0.00016269 | 0.00020714 | 0.00025426 | 0.00030536 | 0.00041054 | 0.00050108 | 0.00058592 | -0.00080901 | -0.00089167 | -0.00098002 | -0.0010646 | -0.0011377 | -0.0012032 | -0.0012644 | -0.001336 | -0.0014062 | -0.001467
Kingston (11 kV) | 34255 | 155.3749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kingston (11 kV) | 34256 | 92.5982 | 78.9 | 79.5259 | 79.8812 | 80.238 | 80.5964 | 80.9564 | 81.3181 | 81.6813 | 82.0462 | 82.4127 | 82.7808 | 173.6 | 179.8926 | 180.66 | 181.4306 | 182.2045 | 182.9817 | 183.7622 | 184.546 | 185.3332 | 186.1238 | 186.9177 | 187.715 | 0.041987 | 0.083923 | 0.1326 | 0.18579 | 0.23908 | 0.29638 | 0.35907 | 0.49185 | 0.6047 | 0.70978 | -0.3988 | -0.49511 | -0.6 | -0.70251 | -0.79317 | -0.87596 | -0.95486 | -1.0484 | -1.1409 | -1.2229
Kingston (11 kV) | 34257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kingston (11 kV) | 34258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kingston (11 kV) | 34259 | 154.4756 | 125.3 | 126.6845 | 127.2504 | 127.8189 | 128.3898 | 128.9633 | 129.5394 | 130.118 | 130.6993 | 131.2831 | 131.8695 | 261.3 | 277.0917 | 278.2736 | 279.4606 | 280.6527 | 281.8498 | 283.0521 | 284.2594 | 285.472 | 286.6897 | 287.9126 | 289.1407 | 0.068943 | 0.13782 | 0.21746 | 0.30389 | 0.38998 | 0.48199 | 0.58222 | 0.79341 | 0.97312 | 1.1402 | -0.73034 | -0.88825 | -1.0598 | -1.2271 | -1.3749 | -1.5097 | -1.6381 | -1.7916 | -1.9417 | -2.0757
Kingston (11 kV) | 34260 | 62.3027 | 62.2 | 62.4778 | 62.7569 | 63.0373 | 63.3189 | 63.6017 | 63.8858 | 64.1712 | 64.4578 | 64.7458 | 65.035 | 91.2 | 95.7145 | 96.1227 | 96.5328 | 96.9445 | 97.358 | 97.7733 | 98.1904 | 98.6092 | 99.0299 | 99.4523 | 99.8765 | 0.017034 | 0.033788 | 0.053416 | 0.075224 | 0.097446 | 0.12175 | 0.14871 | 0.20621 | 0.25526 | 0.30124 | -0.1763 | -0.21457 | -0.25633 | -0.29712 | -0.33313 | -0.36583 | -0.39681 | -0.43201 | -0.46725 | -0.49866
Kingston (11 kV) | 34261 | 39.5686 | 52.3 | 52.5336 | 52.7683 | 53.004 | 53.2408 | 53.4786 | 53.7175 | 53.9574 | 54.1985 | 54.4406 | 54.6837 | 57.6 | 59.3086 | 59.5616 | 59.8157 | 60.0708 | 60.3271 | 60.5844 | 60.8428 | 61.1023 | 61.363 | 61.6247 | 61.8876 | 0.016168 | 0.032092 | 0.050792 | 0.071636 | 0.092936 | 0.11629 | 0.14224 | 0.19774 | 0.24504 | 0.28938 | -0.15151 | -0.18796 | -0.2278 | -0.26679 | -0.30126 | -0.3326 | -0.36232 | -0.39601 | -0.43005 | -0.46018
Kingston (11 kV) | 34262 | 91.4072 | 98.1 | 99.6386 | 100.0837 | 100.5307 | 100.9798 | 101.4309 | 101.884 | 102.3391 | 102.7962 | 103.2554 | 103.7166 | 142.9 | 150.7018 | 151.3446 | 151.9901 | 152.6385 | 153.2896 | 153.9434 | 154.6001 | 155.2595 | 155.9218 | 156.5869 | 157.2548 | 0.010922 | 0.021676 | 0.034302 | 0.04837 | 0.062741 | 0.078495 | 0.095992 | 0.1334 | 0.16529 | 0.19518 | -0.1037 | -0.12831 | -0.1552 | -0.18152 | -0.20478 | -0.22592 | -0.24597 | -0.26871 | -0.29165 | -0.31198
Kingston (11 kV) | 34263 | 95.3781 | 83 | 84.9726 | 85.3521 | 85.7334 | 86.1164 | 86.501 | 86.8874 | 87.2756 | 87.6654 | 88.057 | 88.4504 | 150.3 | 157.2095 | 157.8801 | 158.5535 | 159.2298 | 159.909 | 160.5911 | 161.2762 | 161.9641 | 162.655 | 163.3488 | 164.0455 | 0.036655 | 0.072794 | 0.11508 | 0.16194 | 0.20958 | 0.26157 | 0.31911 | 0.44173 | 0.54629 | 0.6442 | -0.37304 | -0.45566 | -0.54581 | -0.63387 | -0.71163 | -0.78233 | -0.84935 | -0.92602 | -1.0027 | -1.0709
Kingston (11 kV) | 34264 | 96.8344 | 171.3 | 175.1218 | 175.904 | 176.6898 | 177.4791 | 178.2719 | 179.0682 | 179.8681 | 180.6716 | 181.4786 | 182.2893 | 143 | 145.344 | 145.964 | 146.5866 | 147.2119 | 147.8398 | 148.4704 | 149.1037 | 149.7397 | 150.3785 | 151.0199 | 151.6641 | 0.13422 | 0.17776 | 0.22881 | 0.28624 | 0.34564 | 0.41187 | 0.48648 | 0.64801 | 0.78499 | 0.91457 | -0.54621 | -0.64239 | -0.7458 | -0.8445 | -0.92924 | -1.0035 | -1.0713 | -1.1392 | -1.211 | -1.2716
Knights Road | 30603 | 188.3733 | 186.6 | 188.4494 | 190.3171 | 192.2033 | 194.1082 | 196.032 | 197.9748 | 199.9369 | 201.9185 | 203.9197 | 205.9407 | 257.8 | 261.7403 | 263.8683 | 266.0136 | 268.1763 | 270.3566 | 272.5546 | 274.7705 | 277.0044 | 279.2564 | 281.5268 | 283.8156 | 0.06297 | 0.12067 | 0.18871 | 0.26605 | 0.34683 | 0.43774 | 0.54083 | 0.76587 | 0.95659 | 1.1375 | -0.60489 | -0.73209 | -0.86904 | -0.99969 | -1.1117 | -1.2093 | -1.2979 | -1.3823 | -1.4717 | -1.5484
Knights Road | 30604 | 258.9867 | 235.3 | 237.632 | 239.9872 | 242.3657 | 244.7677 | 247.1936 | 249.6435 | 252.1177 | 254.6164 | 257.1399 | 259.6884 | 252.4593 | 254.9405 | 257.0131 | 259.1027 | 261.2092 | 263.3328 | 265.4738 | 267.6321 | 269.8079 | 272.0015 | 274.2129 | 276.4423 | 0.031884 | 0.061098 | 0.095549 | 0.1347 | 0.1756 | 0.22162 | 0.27381 | 0.38772 | 0.48426 | 0.57585 | -0.3063 | -0.3707 | -0.44004 | -0.50618 | -0.56286 | -0.61231 | -0.65714 | -0.69985 | -0.7451 | -0.78393
Knights Road | 30605 | 242.3783 | 111.9 | 113.9057 | 115.0346 | 116.1747 | 117.326 | 118.4889 | 119.6632 | 120.8492 | 122.0469 | 123.2565 | 124.4781 | 182.2 | 192.608 | 194.1739 | 195.7526 | 197.344 | 198.9485 | 200.5659 | 202.1965 | 203.8404 | 205.4976 | 207.1684 | 208.8527 | 0.054457 | 0.10399 | 0.16175 | 0.22644 | 0.29319 | 0.36754 | 0.4512 | 0.63245 | 0.78553 | 0.93006 | -0.53441 | -0.64216 | -0.75693 | -0.86502 | -0.95648 | -1.0353 | -1.1057 | -1.1723 | -1.2418 | -1.3
Knights Road | 30606 | 114.4533 | 105.3 | 106.6526 | 107.7097 | 108.7772 | 109.8552 | 110.944 | 112.0435 | 113.154 | 114.2755 | 115.408 | 116.5518 | 177.5 | 181.6458 | 183.1226 | 184.6114 | 186.1123 | 187.6254 | 189.1509 | 190.6887 | 192.239 | 193.8019 | 195.3775 | 196.9659 | 0.057825 | 0.11196 | 0.17557 | 0.24754 | 0.32243 | 0.4065 | 0.50167 | 0.70906 | 0.88502 | 1.0519 | -0.54096 | -0.65978 | -0.78728 | -0.90843 | -1.0118 | -1.1017 | -1.1829 | -1.2599 | -1.3416 | -1.4115
Knights Road | 30607 | 130.9383 | 88.2 | 89.0741 | 89.957 | 90.8485 | 91.7489 | 92.6582 | 93.5765 | 94.504 | 95.4406 | 96.3865 | 97.3418 | 147.8 | 154.3696 | 155.6247 | 156.8899 | 158.1654 | 159.4513 | 160.7477 | 162.0546 | 163.3721 | 164.7003 | 166.0393 | 167.3892 | 0.19681 | 0.27357 | 0.36375 | 0.46589 | 0.57237 | 0.69214 | 0.82798 | 1.1247 | 1.3764 | 1.6154 | -0.87329 | -1.0409 | -1.2202 | -1.39 | -1.5343 | -1.659 | -1.7708 | -1.8744 | -1.9876 | -2.0815
Knights Road | 30608 | 252.8767 | 201 | 203.6921 | 205.7109 | 207.7496 | 209.8086 | 211.888 | 213.988 | 216.1088 | 218.2507 | 220.4137 | 222.5982 | 236.1 | 241.6831 | 244.348 | 246.3346 | 248.3373 | 250.3563 | 252.3917 | 254.4436 | 256.5123 | 258.5978 | 260.7002 | 262.8197 | 0.042312 | 0.081083 | 0.1268 | 0.17877 | 0.23305 | 0.29413 | 0.36341 | 0.51462 | 0.64277 | 0.76435 | -0.40645 | -0.49192 | -0.58394 | -0.67173 | -0.74697 | -0.81261 | -0.87211 | -0.92882 | -0.98888 | -1.0404
Meadowbank | 45001 | 75.6292 | 83 | 82.911 | 82.8221 | 82.7332 | 82.6445 | 82.5559 | 82.4673 | 82.3789 | 82.2905 | 82.2023 | 82.1141 | 24 | 24.6473 | 24.6014 | 24.5555 | 24.5098 | 24.4642 | 24.4186 | 24.3731 | 24.3277 | 24.2824 | 24.2372 | 24.1921 | 0.0067945 | 0.013551 | 0.022189 | 0.033488 | 0.046755 | 0.063298 | 0.083379 | 0.13088 | 0.1704 | 0.20877 | -0.057142 | -0.070578 | -0.084997 | -0.098148 | -0.10861 | -0.11643 | -0.12215 | -0.11935 | -0.11992 | -0.11911
Meadowbank | 45002 | 75.9169 | 97 | 97.2198 | 97.1155 | 97.0114 | 96.9073 | 96.8034 | 96.6996 | 96.5959 | 96.4923 | 96.3888 | 96.2854 | 65 | 64.879 | 64.7581 | 64.6375 | 64.5172 | 64.397 | 64.2771 | 64.1574 | 64.0379 | 63.9187 | 63.7996 | 63.6808 | 0.026396 | 0.054646 | 0.089093 | 0.13044 | 0.1757 | 0.2288 | 0.29073 | 0.43058 | 0.54807 | 0.6605 | -0.25437 | -0.31573 | -0.3825 | -0.44638 | -0.50101 | -0.54796 | -0.58972 | -0.62136 | -0.6591 | -0.69041
Meadowbank | 45003 | 95.5233 | 99 | 98.8938 | 98.7878 | 98.6818 | 98.576 | 98.4703 | 98.3647 | 98.2592 | 98.1538 | 98.0485 | 97.9434 | 72 | 71.8659 | 71.7321 | 71.5985 | 71.4652 | 71.3321 | 71.1992 | 71.0666 | 70.9343 | 70.8022 | 70.6704 | 70.5387 | 0.030144 | 0.060118 | 0.09844 | 0.14857 | 0.20743 | 0.28082 | 0.36991 | 0.58063 | 0.75597 | 0.92621 | -0.25351 | -0.31312 | -0.37708 | -0.43543 | -0.48182 | -0.51652 | -0.54192 | -0.5295 | -0.53203 | -0.52842
Mowbray | 62004 | 137.1517 | 102.5202 | 106.1224 | 107.3353 | 108.562 | 109.8028 | 111.0577 | 112.327 | 113.6108 | 114.9092 | 116.2225 | 117.5509 | 228.9696 | 234.117 | 235.254 | 236.3966 | 237.5447 | 238.6984 | 239.8577 | 241.0226 | 242.1932 | 243.3694 | 244.5514 | 245.7391 | 0.041863 | 0.087154 | 0.14121 | 0.2026 | 0.26624 | 0.33665 | 0.41592 | 0.58605 | 0.72924 | 0.86267 | -0.47504 | -0.57989 | -0.69623 | -0.81177 | -0.91568 | -1.0116 | -1.104 | -1.2105 | -1.3175 | -1.414
Mowbray | 62005 | 102.4599 | 115.4232 | 117.1309 | 118.4696 | 119.8235 | 121.193 | 122.5781 | 123.9791 | 125.396 | 126.8292 | 128.2787 | 129.7448 | 177.5922 | 178.5051 | 179.3721 | 180.2432 | 181.1186 | 181.9983 | 182.8822 | 183.7704 | 184.6629 | 185.5598 | 186.461 | 187.3666 | 0.023333 | 0.048577 | 0.078704 | 0.11292 | 0.1484 | 0.18764 | 0.23182 | 0.32665 | 0.40645 | 0.48082 | -0.26477 | -0.32321 | -0.38805 | -0.45245 | -0.51037 | -0.56385 | -0.61536 | -0.67469 | -0.73435 | -0.78809
Mowbray | 62006 | 73.0113 | 81.5235 | 82.9991 | 83.9477 | 84.9071 | 85.8775 | 86.859 | 87.8517 | 88.8558 | 89.8713 | 90.8985 | 91.9373 | 118.9422 | 123.6504 | 124.2509 | 124.8544 | 125.4607 | 126.0701 | 126.6824 | 127.2976 | 127.9159 | 128.5371 | 129.1614 | 129.7887 | 0.038123 | 0.076243 | 0.12137 | 0.1721 | 0.22424 | 0.28153 | 0.34546 | 0.48251 | 0.59753 | 0.7044 | -0.3975 | -0.48522 | -0.5818 | -0.67689 | -0.76164 | -0.83924 | -0.91331 | -0.99821 | -1.0828 | -1.1581
Mowbray | 62008 | 91.0008 | 53.7234 | 54.6066 | 55.2307 | 55.862 | 56.5004 | 57.1461 | 57.7993 | 58.4599 | 59.128 | 59.8038 | 60.4873 | 114.4848 | 115.0924 | 115.6514 | 116.2131 | 116.7775 | 117.3447 | 117.9146 | 118.4873 | 119.0627 | 119.641 | 120.222 | 120.8059 | 0.038564 | 0.080274 | 0.13005 | 0.18659 | 0.24519 | 0.31002 | 0.383 | 0.53966 | 0.67149 | 0.79435 | -0.43746 | -0.53401 | -0.64115 | -0.74755 | -0.84322 | -0.93158 | -1.0167 | -1.1147 | -1.2132 | -1.302
Mowbray | 62009 | 91.392 | 108.9717 | 110.2171 | 111.4768 | 112.7509 | 114.0395 | 115.3429 | 116.6611 | 117.9944 | 119.343 | 120.707 | 122.0865 | 136.3026 | 139.0651 | 139.7405 | 140.4192 | 141.1012 | 141.7865 | 142.4751 | 143.1671 | 143.8624 | 144.5611 | 145.2632 | 145.9687 | 0.032306 | 0.063657 | 0.10064 | 0.14206 | 0.18447 | 0.23093 | 0.28259 | 0.39328 | 0.48606 | 0.57215 | -0.32614 | -0.39811 | -0.47709 | -0.55459 | -0.6234 | -0.68617 | -0.74586 | -0.81413 | -0.88194 | -0.94194
Mowbray | 62010 | 61.6276 | 70.6146 | 71.4217 | 72.2379 | 73.0635 | 73.8986 | 74.7432 | 75.5974 | 76.4614 | 77.3353 | 78.2192 | 79.1131 | 128.3262 | 131.865 | 132.5054 | 133.1489 | 133.7956 | 134.4454 | 135.0984 | 135.7545 | 136.4138 | 137.0764 | 137.7421 | 138.4111 | 0.0556 | 0.11575 | 0.18753 | 0.26906 | 0.35358 | 0.44708 | 0.55234 | 0.77827 | 0.96841 | 1.1456 | -0.63086 | -0.7701 | -0.9246 | -1.078 | -1.216 | -1.3435 | -1.4662 | -1.6075 | -1.7497 | -1.8777
Mowbray | 62013 | 185.9441 | 128.3262 | 131.8928 | 133.4002 | 134.9249 | 136.4669 | 138.0266 | 139.6041 | 141.1996 | 142.8134 | 144.4456 | 146.0965 | 169.1466 | 169.9681 | 172.8936 | 173.7333 | 174.577 | 175.4249 | 176.2769 | 177.133 | 177.9933 | 178.8578 | 179.7264 | 180.5993 | 0.035237 | 0.072872 | 0.11773 | 0.1686 | 0.22125 | 0.27945 | 0.34488 | 0.48529 | 0.60341 | 0.71343 | -0.39436 | -0.4814 | -0.57786 | -0.67354 | -0.75945 | -0.83869 | -0.9149 | -1.0026 | -1.0907 | -1.1699
New Norfolk | 39010 | 45.8864 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 77.5 | 79.9371 | 79.9371 | 79.9371 | 79.9371 | 79.9371 | 79.9371 | 79.9371 | 79.9371 | 79.9371 | 79.9371 | 79.9371 | 0.035099 | 0.070001 | 0.11462 | 0.17299 | 0.24153 | 0.32698 | 0.43071 | 0.67608 | 0.88023 | 1.0785 | -0.29518 | -0.36459 | -0.43907 | -0.50701 | -0.56103 | -0.60142 | -0.631 | -0.61654 | -0.61949 | -0.61528
New Norfolk | 39011 | 59.9949 | 35.8 | 35.874 | 35.874 | 35.874 | 35.874 | 35.874 | 35.874 | 35.874 | 35.874 | 35.874 | 35.874 | 58.7 | 60.1749 | 60.1749 | 60.1749 | 60.1749 | 60.1749 | 60.1749 | 60.1749 | 60.1749 | 60.1749 | 60.1749 | 60.1749 | 0.029505 | 0.058845 | 0.096356 | 0.14542 | 0.20304 | 0.27487 | 0.36208 | 0.56834 | 0.73996 | 0.9066 | -0.24814 | -0.30649 | -0.3691 | -0.42621 | -0.47162 | -0.50558 | -0.53045 | -0.51829 | -0.52077 | -0.51723
New Norfolk | 39012 | 63.8649 | 41.6 | 41.6 | 41.6 | 41.6 | 41.6 | 41.6 | 41.6 | 41.6 | 41.6 | 41.6 | 41.6 | 68.6 | 70.9038 | 70.9038 | 70.9038 | 70.9038 | 70.9038 | 70.9038 | 70.9038 | 70.9038 | 70.9038 | 70.9038 | 70.9038 | 0.020909 | 0.041701 | 0.068283 | 0.10306 | 0.14388 | 0.19479 | 0.25659 | 0.40276 | 0.52438 | 0.64247 | -0.17585 | -0.21719 | -0.26156 | -0.30203 | -0.33422 | -0.35828 | -0.3759 | -0.36729 | -0.36904 | -0.36654
New Norfolk | 39013 | 36.664 | 13.5 | 13.5648 | 13.5648 | 13.5648 | 13.5648 | 13.5648 | 13.5648 | 13.5648 | 13.5648 | 13.5648 | 13.5648 | 24.1 | 24.8062 | 24.8062 | 24.8062 | 24.8062 | 24.8062 | 24.8062 | 24.8062 | 24.8062 | 24.8062 | 24.8062 | 24.8062 | 0.014085 | 0.028079 | 0.045956 | 0.06931 | 0.096705 | 0.13084 | 0.17225 | 0.27016 | 0.35163 | 0.43073 | -0.11856 | -0.14642 | -0.17632 | -0.2036 | -0.22532 | -0.2416 | -0.25356 | -0.24804 | -0.24945 | -0.24798
New Norfolk | 39565 | 88.3916 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 143.4 | 145.7121 | 145.7121 | 145.7121 | 145.7121 | 145.7121 | 145.7121 | 145.7121 | 145.7121 | 145.7121 | 145.7121 | 145.7121 | 0.063403 | 0.12645 | 0.20705 | 0.3125 | 0.4363 | 0.59067 | 0.77805 | 1.2213 | 1.5901 | 1.9482 | -0.53322 | -0.6586 | -0.79314 | -0.91586 | -1.0135 | -1.0864 | -1.1398 | -1.1137 | -1.1191 | -1.1115
New Norfolk | 39568 | 157.9354 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 27.1 | 27.4381 | 27.4381 | 27.4381 | 27.4381 | 27.4381 | 27.4381 | 27.4381 | 27.4381 | 27.4381 | 27.4381 | 27.4381 | 0.0086289 | 0.01788 | 0.029146 | 0.042634 | 0.057368 | 0.074616 | 0.094709 | 0.13999 | 0.17806 | 0.21446 | -0.083494 | -0.10364 | -0.12557 | -0.14658 | -0.16459 | -0.18011 | -0.19398 | -0.20478 | -0.2175 | -0.22812
New Norfolk | 39569 | 203.7322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00018769 | 0.00037433 | 0.00061295 | 0.00092509 | 0.0012916 | 0.0017486 | 0.0023033 | 0.0036154 | 0.0047071 | 0.0057672 | -0.0015785 | -0.0019497 | -0.002348 | -0.0027113 | -0.0030002 | -0.0032162 | -0.0033743 | -0.003297 | -0.0033128 | -0.0032903
New Norfolk | 39570 | 36.6694 | 209.3 | 209.3 | 209.3 | 209.3 | 209.3 | 209.3 | 209.3 | 209.3 | 209.3 | 209.3 | 209.3 | 148.8 | 149.5547 | 149.5547 | 149.5547 | 149.5547 | 149.5547 | 149.5547 | 149.5547 | 149.5547 | 149.5547 | 149.5547 | 149.5547 | 0.00090093 | 0.0017968 | 0.0029422 | 0.0044405 | 0.0061996 | 0.0083931 | 0.011056 | 0.017354 | 0.022594 | 0.027683 | -0.0075768 | -0.0093584 | -0.01127 | -0.013014 | -0.014401 | -0.015438 | -0.016197 | -0.015826 | -0.015901 | -0.015793
New Norfolk | 39571 | 96.7582 | 108.5 | 108.5 | 108.5 | 108.5 | 108.5 | 108.5 | 108.5 | 108.5 | 108.5 | 108.5 | 108.5 | 63.4 | 65.4886 | 65.4886 | 65.4886 | 65.4886 | 65.4886 | 65.4886 | 65.4886 | 65.4886 | 65.4886 | 65.4886 | 65.4886 | 0.032621 | 0.065059 | 0.10653 | 0.16078 | 0.22448 | 0.3039 | 0.40031 | 0.62836 | 0.8181 | 1.0023 | -0.27434 | -0.33885 | -0.40808 | -0.47122 | -0.52143 | -0.55897 | -0.58646 | -0.57302 | -0.57576 | -0.57185
New Town Zone | 16091 | 126.8389 | 109 | 109.7905 | 110.5867 | 111.3887 | 112.1965 | 113.0101 | 113.8297 | 114.6552 | 115.4866 | 116.3242 | 117.1678 | 190.6667 | 199.0723 | 200.0731 | 201.0789 | 202.0897 | 203.1056 | 204.1267 | 205.1529 | 206.1842 | 207.2207 | 208.2624 | 209.3094 | 0.030325 | 0.064474 | 0.10545 | 0.15244 | 0.20161 | 0.25693 | 0.31977 | 0.45594 | 0.57095 | 0.67926 | -0.29341 | -0.37256 | -0.46071 | -0.54885 | -0.62857 | -0.70269 | -0.77459 | -0.85792 | -0.94303 | -1.0189
New Town Zone | 16092 | 90.5944 | 87.3333 | 88.4179 | 89.0591 | 89.705 | 90.3555 | 91.0108 | 91.6708 | 92.3356 | 93.0052 | 93.6797 | 94.3591 | 127.6667 | 134.0518 | 134.7257 | 135.403 | 136.0837 | 136.7678 | 137.4554 | 138.1464 | 138.8409 | 139.5388 | 140.2403 | 140.9453 | 0.016803 | 0.035726 | 0.05843 | 0.084471 | 0.11171 | 0.14237 | 0.17719 | 0.25264 | 0.31637 | 0.37639 | -0.16258 | -0.20644 | -0.25529 | -0.30413 | -0.3483 | -0.38937 | -0.42921 | -0.47539 | -0.52254 | -0.56461
New Town Zone | 16093 | 109.7778 | 91.3333 | 91.9957 | 92.6628 | 93.3348 | 94.0117 | 94.6935 | 95.3802 | 96.0719 | 96.7686 | 97.4704 | 98.1773 | 120.6667 | 126.0779 | 126.7117 | 127.3487 | 127.9889 | 128.6323 | 129.279 | 129.9289 | 130.582 | 131.2385 | 131.8983 | 132.5613 | 0.0075352 | 0.016021 | 0.026202 | 0.03788 | 0.050096 | 0.063844 | 0.079459 | 0.11329 | 0.14187 | 0.16879 | -0.072907 | -0.092574 | -0.11448 | -0.13638 | -0.15619 | -0.17461 | -0.19247 | -0.21318 | -0.23433 | -0.25319
New Town Zone | 16094 | 162.6833 | 148.3333 | 149.409 | 150.4926 | 151.584 | 152.6832 | 153.7905 | 154.9058 | 156.0292 | 157.1607 | 158.3005 | 159.4485 | 230.6667 | 238.7016 | 239.9016 | 241.1076 | 242.3197 | 243.5379 | 244.7622 | 245.9926 | 247.2293 | 248.4721 | 249.7212 | 250.9766 | 0.028352 | 0.060267 | 0.098557 | 0.14247 | 0.1884 | 0.24009 | 0.2988 | 0.426 | 0.53344 | 0.63462 | -0.27411 | -0.34807 | -0.43044 | -0.51279 | -0.58726 | -0.65649 | -0.72365 | -0.80147 | -0.88093 | -0.95181
New Town Zone | 16095 | 72.7944 | 69.6667 | 70.1719 | 70.6808 | 71.1934 | 71.7097 | 72.2297 | 72.7535 | 73.2811 | 73.8126 | 74.3479 | 74.887 | 82.6667 | 84.6828 | 85.1085 | 85.5364 | 85.9664 | 86.3985 | 86.8329 | 87.2694 | 87.7081 | 88.149 | 88.5922 | 89.0375 | 0.0049461 | 0.010371 | 0.016843 | 0.02422 | 0.031898 | 0.040505 | 0.050257 | 0.071355 | 0.089105 | 0.10576 | -0.045561 | -0.058057 | -0.071887 | -0.085615 | -0.097937 | -0.10931 | -0.12026 | -0.13286 | -0.14564 | -0.15688
New Town Zone | 16096 | 121.3611 | 127.3333 | 129.9045 | 130.8466 | 131.7955 | 132.7513 | 133.714 | 134.6837 | 135.6604 | 136.6443 | 137.6352 | 138.6333 | 200.3333 | 208.6314 | 209.6802 | 210.7343 | 211.7937 | 212.8584 | 213.9284 | 215.0039 | 216.0847 | 217.171 | 218.2628 | 219.36 | 0.032885 | 0.067591 | 0.10898 | 0.15632 | 0.20576 | 0.26156 | 0.32488 | 0.46268 | 0.57817 | 0.68594 | -0.30589 | -0.38503 | -0.47218 | -0.55811 | -0.63465 | -0.70465 | -0.77142 | -0.84648 | -0.92222 | -0.98775
New Town Zone | 16097 | 72.5556 | 49.6667 | 50.0269 | 50.3897 | 50.7551 | 51.1232 | 51.4939 | 51.8673 | 52.2435 | 52.6224 | 53.004 | 53.3884 | 57.3333 | 58.3615 | 58.6549 | 58.9497 | 59.2461 | 59.5439 | 59.8432 | 60.1441 | 60.4464 | 60.7503 | 61.0557 | 61.3626 | 0.0063577 | 0.013246 | 0.021442 | 0.030755 | 0.040424 | 0.051244 | 0.063488 | 0.089955 | 0.11218 | 0.133 | -0.057219 | -0.073039 | -0.090495 | -0.10776 | -0.1232 | -0.1374 | -0.15101 | -0.16665 | -0.18241 | -0.19619
New Town Zone | 16098 | 135.2333 | 117.6667 | 118.6355 | 119.4958 | 120.3624 | 121.2353 | 122.1145 | 123.0001 | 123.8921 | 124.7906 | 125.6955 | 126.6071 | 225.3333 | 235.1722 | 236.3545 | 237.5427 | 238.7368 | 239.937 | 241.1432 | 242.3554 | 243.5738 | 244.7983 | 246.0289 | 247.2657 | 0.032431 | 0.068106 | 0.11071 | 0.15932 | 0.20996 | 0.26679 | 0.33121 | 0.47063 | 0.588 | 0.69817 | -0.30128 | -0.38351 | -0.4746 | -0.56511 | -0.64643 | -0.72154 | -0.79394 | -0.8773 | -0.96193 | -1.0365
Newton | 96202 | 88.0117 | 99.1 | 100.0687 | 100.0687 | 100.0687 | 100.0687 | 100.0687 | 100.0687 | 100.0687 | 100.0687 | 100.0687 | 100.0687 | 98.5667 | 99.7231 | 99.7231 | 99.7231 | 99.7231 | 99.7231 | 99.7231 | 99.7231 | 99.7231 | 99.7231 | 99.7231 | 99.7231 | 1.8738e-05 | 3.8838e-05 | 6.4843e-05 | 9.8929e-05 | 0.00013875 | 0.00018787 | 0.00024683 | 0.00038464 | 0.00049784 | 0.00060605 | -0.00016123 | -0.00020268 | -0.00024863 | -0.00029287 | -0.00033085 | -0.00036297 | -0.00039111 | -0.00040442 | -0.00042529 | -0.00044116
North Hobart | 18131A | 149.5337 | 148 | 150.3335 | 152.7038 | 155.1115 | 157.5571 | 160.0413 | 162.5647 | 165.1278 | 167.7314 | 170.376 | 173.0623 | 168.4 | 175.6762 | 177.411 | 179.163 | 180.9323 | 182.719 | 184.5234 | 186.3456 | 188.1858 | 190.0442 | 191.9209 | 193.8162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
North Hobart | 18131B | 204.6419 | 176.6 | 179.3845 | 182.2128 | 185.0857 | 188.004 | 190.9682 | 193.9792 | 197.0377 | 200.1444 | 203.3 | 206.5055 | 173.4 | 181.6572 | 183.4511 | 185.2628 | 187.0923 | 188.9398 | 190.8057 | 192.6899 | 194.5928 | 196.5144 | 198.4551 | 200.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
North Hobart | 18132A | 14.2323 | 11 | 11.1734 | 11.3496 | 11.5286 | 11.7103 | 11.895 | 12.0825 | 12.273 | 12.4665 | 12.6631 | 12.8627 | 32 | 32.316 | 32.6351 | 32.9574 | 33.2829 | 33.6116 | 33.9435 | 34.2787 | 34.6172 | 34.959 | 35.3043 | 35.6529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
North Hobart | 18132B | 79.0479 | 54.8 | 55.664 | 56.5417 | 57.4332 | 58.3387 | 59.2585 | 60.1929 | 61.1419 | 62.106 | 63.0852 | 64.0798 | 55.4 | 56.9488 | 57.5111 | 58.0791 | 58.6526 | 59.2318 | 59.8167 | 60.4075 | 61.004 | 61.6064 | 62.2148 | 62.8292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
North Hobart | 18133A | 75.2424 | 52.4 | 53.2262 | 54.0654 | 54.9179 | 55.7837 | 56.6633 | 57.5567 | 58.4642 | 59.386 | 60.3223 | 61.2734 | 53.6 | 55.4299 | 55.9773 | 56.5301 | 57.0884 | 57.6521 | 58.2215 | 58.7964 | 59.377 | 59.9634 | 60.5555 | 61.1535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
North Hobart | 18133B | 28.2573 | 29.8 | 30.2699 | 30.7471 | 31.2319 | 31.7243 | 32.2245 | 32.7326 | 33.2487 | 33.7729 | 34.3054 | 34.8463 | 44.6 | 45.0404 | 45.4852 | 45.9344 | 46.388 | 46.8461 | 47.3087 | 47.7759 | 48.2477 | 48.7242 | 49.2053 | 49.6912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
North Hobart | 18134A | 127.555 | 41 | 41.6464 | 42.3031 | 42.9701 | 43.6476 | 44.3358 | 45.0348 | 45.7449 | 46.4661 | 47.1988 | 47.9429 | 225.4 | 234.0397 | 236.3509 | 238.6849 | 241.042 | 243.4223 | 245.8262 | 248.2538 | 250.7053 | 253.1811 | 255.6813 | 258.2062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
North Hobart | 18134B | 71.3778 | 20 | 20.5965 | 20.9212 | 21.2511 | 21.5862 | 21.9265 | 22.2722 | 22.6234 | 22.9801 | 23.3424 | 23.7105 | 46.2 | 49.8153 | 50.3073 | 50.8041 | 51.3058 | 51.8124 | 52.3241 | 52.8408 | 53.3626 | 53.8896 | 54.4218 | 54.9592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
North Hobart | 18135A | 3.6686 | 15.2 | 15.4397 | 15.6831 | 15.9304 | 16.1815 | 16.4367 | 16.6958 | 16.9591 | 17.2265 | 17.4981 | 17.774 | 23.8 | 25.6338 | 25.887 | 26.1426 | 26.4008 | 26.6615 | 26.9248 | 27.1907 | 27.4592 | 27.7303 | 28.0042 | 28.2807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
North Hobart | 18135B | 72.1899 | 77 | 78.2141 | 79.4473 | 80.6999 | 81.9723 | 83.2647 | 84.5776 | 85.9111 | 87.2657 | 88.6416 | 90.0392 | 111.4 | 115.2903 | 116.4289 | 117.5786 | 118.7397 | 119.9123 | 121.0965 | 122.2923 | 123.5 | 124.7196 | 125.9512 | 127.195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
North Hobart | 18136A | 230.0486 | 52 | 53.4221 | 54.2644 | 55.12 | 55.9891 | 56.8718 | 57.7685 | 58.6794 | 59.6046 | 60.5443 | 61.4989 | 110.6 | 112.8683 | 113.9829 | 115.1085 | 116.2452 | 117.3932 | 118.5525 | 119.7232 | 120.9055 | 122.0995 | 123.3052 | 124.5229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
North Hobart | 18136B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
North Hobart | 18141A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
North Hobart | 18141B | 204.9145 | 105.8 | 107.4681 | 109.1626 | 110.8838 | 112.6321 | 114.4079 | 116.2118 | 118.0441 | 119.9053 | 121.7958 | 123.7162 | 159.8 | 162.3296 | 163.9327 | 165.5515 | 167.1864 | 168.8374 | 170.5047 | 172.1885 | 173.8889 | 175.6061 | 177.3402 | 179.0915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
North Hobart | 18142A | 17.1397 | 15.6 | 16.0687 | 16.322 | 16.5794 | 16.8408 | 17.1063 | 17.376 | 17.65 | 17.9283 | 18.211 | 18.4981 | 28.6 | 30.4135 | 30.7138 | 31.0171 | 31.3235 | 31.6328 | 31.9452 | 32.2606 | 32.5792 | 32.9009 | 33.2258 | 33.5539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
North Hobart | 18142B | 33.7589 | 29.4 | 29.8635 | 30.3344 | 30.8127 | 31.2985 | 31.792 | 32.2933 | 32.8024 | 33.3196 | 33.845 | 34.3786 | 41 | 42.877 | 43.3004 | 43.728 | 44.1599 | 44.596 | 45.0364 | 45.4811 | 45.9302 | 46.3838 | 46.8419 | 47.3044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
North Hobart | 18143A | 45.1111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 28.9552 | 29.2412 | 29.5299 | 29.8216 | 30.1161 | 30.4135 | 30.7138 | 31.0171 | 31.3234 | 31.6327 | 31.9451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
North Hobart | 18143B | 139.7786 | 119.2 | 121.5794 | 123.4964 | 125.4435 | 127.4214 | 129.4304 | 131.4712 | 133.5441 | 135.6497 | 137.7884 | 139.9609 | 262.2 | 271.1256 | 273.8031 | 276.5069 | 279.2375 | 281.995 | 284.7798 | 287.5921 | 290.4321 | 293.3002 | 296.1966 | 299.1216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
North Hobart | 18144A | 120.3196 | 53.6 | 55.2047 | 56.0751 | 56.9593 | 57.8574 | 58.7696 | 59.6962 | 60.6374 | 61.5935 | 62.5646 | 63.5511 | 110.6 | 117.1472 | 118.304 | 119.4723 | 120.6521 | 121.8436 | 123.0468 | 124.2619 | 125.489 | 126.7283 | 127.9798 | 129.2436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
North Hobart | 18144B | 94.6102 | 95.8 | 97.3105 | 98.8448 | 100.4033 | 101.9863 | 103.5943 | 105.2277 | 106.8868 | 108.5721 | 110.2839 | 112.0228 | 146.2 | 152.9949 | 154.5058 | 156.0316 | 157.5724 | 159.1285 | 160.6999 | 162.2869 | 163.8895 | 165.5079 | 167.1424 | 168.7929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
North Hobart | 18145A | 46.8279 | 49.2 | 50.6465 | 51.445 | 52.2561 | 53.08 | 53.917 | 54.7671 | 55.6306 | 56.5077 | 57.3987 | 58.3037 | 68.8 | 70.6843 | 71.3823 | 72.0872 | 72.7991 | 73.518 | 74.244 | 74.9772 | 75.7176 | 76.4653 | 77.2204 | 77.983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
North Hobart | 18145B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
North Hobart | 18146A | 137.2792 | 109.8 | 112.1463 | 113.9145 | 115.7106 | 117.535 | 119.3882 | 121.2706 | 123.1826 | 125.1248 | 127.0977 | 129.1016 | 198.4 | 208.5889 | 210.6488 | 212.729 | 214.8298 | 216.9513 | 219.0937 | 221.2573 | 223.4423 | 225.6488 | 227.8771 | 230.1275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
North Hobart | 18146B | 139.7626 | 169.6 | 173.1726 | 175.903 | 178.6765 | 181.4937 | 184.3553 | 187.262 | 190.2146 | 193.2137 | 196.2601 | 199.3545 | 304.8 | 323.6974 | 326.894 | 330.1222 | 333.3822 | 336.6744 | 339.9992 | 343.3567 | 346.7475 | 350.1717 | 353.6297 | 357.1219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Norwood | 65060 | 84.6551 | 32.8824 | 32.8824 | 32.8824 | 32.8824 | 32.8824 | 32.8824 | 32.8824 | 32.8824 | 32.8824 | 32.8824 | 32.8824 | 22.9018 | 22.9114 | 22.9114 | 22.9114 | 22.9114 | 22.9114 | 22.9114 | 22.9114 | 22.9114 | 22.9114 | 22.9114 | 22.9114 | 0.0078918 | 0.015453 | 0.024423 | 0.034534 | 0.044937 | 0.05638 | 0.069255 | 0.096682 | 0.11961 | 0.14088 | -0.087679 | -0.10514 | -0.12443 | -0.14351 | -0.16059 | -0.17632 | -0.19142 | -0.20896 | -0.22626 | -0.24175
Norwood | 65061 | 58.7133 | 56.1284 | 56.1284 | 56.1284 | 56.1284 | 56.1284 | 56.1284 | 56.1284 | 56.1284 | 56.1284 | 56.1284 | 56.1284 | 102.1091 | 102.1521 | 102.1521 | 102.1521 | 102.1521 | 102.1521 | 102.1521 | 102.1521 | 102.1521 | 102.1521 | 102.1521 | 102.1521 | 0.034417 | 0.067417 | 0.10658 | 0.15073 | 0.19617 | 0.24618 | 0.30243 | 0.42228 | 0.52249 | 0.61548 | -0.38351 | -0.45975 | -0.54398 | -0.62731 | -0.70196 | -0.77069 | -0.83669 | -0.91341 | -0.98905 | -1.0568
Norwood | 65062 | 133.3524 | 64.7571 | 64.814 | 64.814 | 64.814 | 64.814 | 64.814 | 64.814 | 64.814 | 64.814 | 64.814 | 64.814 | 133.2507 | 133.3086 | 133.3086 | 133.3086 | 133.3086 | 133.3086 | 133.3086 | 133.3086 | 133.3086 | 133.3086 | 133.3086 | 133.3086 | 0.048559 | 0.095058 | 0.15022 | 0.21238 | 0.27633 | 0.34667 | 0.4258 | 0.59436 | 0.7353 | 0.86597 | -0.53856 | -0.64594 | -0.76455 | -0.88183 | -0.98683 | -1.0835 | -1.1762 | -1.284 | -1.3902 | -1.4854
Norwood | 65063 | 30.7031 | 25.1396 | 25.4184 | 25.4184 | 25.4184 | 25.4184 | 25.4184 | 25.4184 | 25.4184 | 25.4184 | 25.4184 | 25.4184 | 58.0567 | 59.6866 | 59.6866 | 59.6866 | 59.6866 | 59.6866 | 59.6866 | 59.6866 | 59.6866 | 59.6866 | 59.6866 | 59.6866 | 0.019528 | 0.037255 | 0.058059 | 0.081235 | 0.10488 | 0.13074 | 0.15932 | 0.22066 | 0.27197 | 0.31953 | -0.18567 | -0.22602 | -0.27 | -0.31277 | -0.35037 | -0.38432 | -0.41624 | -0.45211 | -0.48758 | -0.51855
Norwood | 65064 | 48.9016 | 39.6302 | 39.8226 | 39.8226 | 39.8226 | 39.8226 | 39.8226 | 39.8226 | 39.8226 | 39.8226 | 39.8226 | 39.8226 | 124.0531 | 126.7133 | 126.7133 | 126.7133 | 126.7133 | 126.7133 | 126.7133 | 126.7133 | 126.7133 | 126.7133 | 126.7133 | 126.7133 | 0.040472 | 0.078152 | 0.12248 | 0.17194 | 0.22241 | 0.27755 | 0.33879 | 0.46964 | 0.57907 | 0.68038 | -0.40334 | -0.48971 | -0.58428 | -0.67684 | -0.75882 | -0.83344 | -0.90422 | -0.98532 | -1.0653 | -1.1358
Norwood | 65065 | 110.6362 | 120.2 | 121.3804 | 121.3804 | 121.3804 | 121.3804 | 121.3804 | 121.3804 | 121.3804 | 121.3804 | 121.3804 | 121.3804 | 180.4 | 188.9869 | 188.9869 | 188.9869 | 188.9869 | 188.9869 | 188.9869 | 188.9869 | 188.9869 | 188.9869 | 188.9869 | 188.9869 | 0.036126 | 0.070335 | 0.11095 | 0.15681 | 0.20411 | 0.25621 | 0.3149 | 0.44035 | 0.54519 | 0.64241 | -0.3998 | -0.47857 | -0.5655 | -0.65134 | -0.72806 | -0.79852 | -0.86597 | -0.94363 | -1.0204 | -1.089
Norwood | 65066 | 71.0626 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 131.6 | 133.5239 | 133.5239 | 133.5239 | 133.5239 | 133.5239 | 133.5239 | 133.5239 | 133.5239 | 133.5239 | 133.5239 | 133.5239 | 0.074519 | 0.13685 | 0.21087 | 0.29703 | 0.38921 | 0.49557 | 0.61818 | 0.89245 | 1.121 | 1.3383 | -0.88184 | -1.0131 | -1.1518 | -1.2798 | -1.385 | -1.4711 | -1.5433 | -1.5893 | -1.6439 | -1.6823
Norwood | 65067 | 46.8298 | 50.2 | 50.2 | 50.2 | 50.2 | 50.2 | 50.2 | 50.2 | 50.2 | 50.2 | 50.2 | 50.2 | 66.2 | 66.2091 | 66.2091 | 66.2091 | 66.2091 | 66.2091 | 66.2091 | 66.2091 | 66.2091 | 66.2091 | 66.2091 | 66.2091 | 0.043192 | 0.076936 | 0.11871 | 0.17131 | 0.2315 | 0.30522 | 0.3937 | 0.60109 | 0.77256 | 0.93804 | -0.34421 | -0.41019 | -0.47902 | -0.53967 | -0.58596 | -0.61865 | -0.64029 | -0.62238 | -0.61696 | -0.60443
Palmerston | 51001 | 5.5803 | 28.2141 | 29.7289 | 29.7289 | 29.7289 | 29.7289 | 29.7289 | 29.7289 | 29.7289 | 29.7289 | 29.7289 | 29.7289 | 30.9496 | 30.9496 | 30.9496 | 30.9496 | 30.9496 | 30.9496 | 30.9496 | 30.9496 | 30.9496 | 30.9496 | 30.9496 | 30.9496 | 0.00029553 | 0.00053156 | 0.00082427 | 0.0011863 | 0.0015925 | 0.0020794 | 0.0026548 | 0.003975 | 0.0050756 | 0.0061315 | -0.0032358 | -0.0037341 | -0.0042744 | -0.0047829 | -0.0052083 | -0.0055592 | -0.0058558 | -0.0059953 | -0.0062016 | -0.0063477
Palmerston | 51002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0028896 | 0.0051975 | 0.0080595 | 0.011599 | 0.015572 | 0.020332 | 0.025958 | 0.038867 | 0.049628 | 0.059952 | -0.031639 | -0.036511 | -0.041794 | -0.046766 | -0.050925 | -0.054357 | -0.057257 | -0.05862 | -0.060638 | -0.062066
Palmerston | 51003 | 249.7994 | 188.6675 | 189.1575 | 189.1575 | 189.1575 | 189.1575 | 189.1575 | 189.1575 | 189.1575 | 189.1575 | 189.1575 | 189.1575 | 71.5905 | 71.5905 | 72.0805 | 72.0805 | 72.0805 | 72.0805 | 72.0805 | 72.0805 | 72.0805 | 72.0805 | 72.0805 | 72.0805 | 0.017994 | 0.033316 | 0.052434 | 0.076477 | 0.10386 | 0.13715 | 0.17688 | 0.26915 | 0.3458 | 0.41961 | -0.18716 | -0.21853 | -0.25218 | -0.28316 | -0.30832 | -0.32806 | -0.34364 | -0.34518 | -0.35197 | -0.35512
Palmerston | 51004 | 102.8579 | 89.957 | 89.957 | 89.957 | 89.957 | 89.957 | 89.957 | 89.957 | 89.957 | 89.957 | 89.957 | 89.957 | 36.8894 | 37.2187 | 37.2187 | 37.2187 | 37.2187 | 37.2187 | 37.2187 | 37.2187 | 37.2187 | 37.2187 | 37.2187 | 37.2187 | 0.028202 | 0.053286 | 0.083235 | 0.118 | 0.15501 | 0.19734 | 0.24582 | 0.35305 | 0.443 | 0.52827 | -0.30673 | -0.36142 | -0.42033 | -0.47616 | -0.52359 | -0.56426 | -0.60033 | -0.63054 | -0.66374 | -0.69062
Port Latta | 94001 | 111.2787 | 107.6 | 107.9383 | 107.9383 | 107.9383 | 107.9383 | 107.9383 | 107.9383 | 107.9383 | 107.9383 | 107.9383 | 107.9383 | 58 | 58.3877 | 58.3877 | 58.3877 | 58.3877 | 58.3877 | 58.3877 | 58.3877 | 58.3877 | 58.3877 | 58.3877 | 58.3877 | 0.026235 | 0.053613 | 0.087709 | 0.13004 | 0.17764 | 0.23472 | 0.30213 | 0.45669 | 0.58531 | 0.70849 | -0.26227 | -0.32035 | -0.38371 | -0.44389 | -0.49484 | -0.53761 | -0.57457 | -0.59515 | -0.62348 | -0.64581
Port Latta | 94002 | 115.1722 | 195.6 | 198.4134 | 198.4134 | 198.4134 | 198.4134 | 198.4134 | 198.4134 | 198.4134 | 198.4134 | 198.4134 | 198.4134 | 129.1993 | 128.68 | 128.68 | 128.68 | 128.68 | 128.68 | 128.68 | 128.68 | 128.68 | 128.68 | 128.68 | 128.68 | 0.094982 | 0.18428 | 0.29494 | 0.43245 | 0.58758 | 0.77468 | 0.99681 | 1.5097 | 1.9368 | 2.3477 | -0.81433 | -0.9995 | -1.1982 | -1.382 | -1.5323 | -1.6518 | -1.7479 | -1.7702 | -1.8214 | -1.8531
Queenstown | 98001 | 45.1403 | 42.6572 | 42.51 | 42.1305 | 41.7543 | 41.3816 | 41.0121 | 40.646 | 40.2831 | 39.9234 | 39.567 | 39.2138 | 53.9855 | 54.3658 | 53.987 | 53.6107 | 53.2371 | 52.8661 | 52.4977 | 52.1319 | 51.7686 | 51.4078 | 51.0496 | 50.6938 | 0.015455 | 0.030348 | 0.05112 | 0.08194 | 0.1212 | 0.17313 | 0.23822 | 0.39793 | 0.52812 | 0.65492 | -0.11285 | -0.13778 | -0.16414 | -0.18614 | -0.201 | -0.20768 | -0.20724 | -0.16811 | -0.14246 | -0.11353
Queenstown | 98002 | 50.5571 | 43.5947 | 44.6815 | 44.2826 | 43.8872 | 43.4954 | 43.1071 | 42.7222 | 42.3408 | 41.9628 | 41.5882 | 41.2169 | 63.2045 | 61.0361 | 60.6108 | 60.1884 | 59.7689 | 59.3524 | 58.9388 | 58.5281 | 58.1202 | 57.7152 | 57.3129 | 56.9135 | 0.015571 | 0.032275 | 0.053884 | 0.08221 | 0.1153 | 0.15612 | 0.20511 | 0.31964 | 0.41371 | 0.50363 | -0.13399 | -0.16843 | -0.20662 | -0.24338 | -0.27493 | -0.30163 | -0.32501 | -0.33607 | -0.35342 | -0.36661
Queenstown | 98003 | 28.2415 | 26.4068 | 26.7514 | 26.5126 | 26.2759 | 26.0413 | 25.8088 | 25.5784 | 25.35 | 25.1237 | 24.8994 | 24.6771 | 37.1102 | 37.3417 | 37.0815 | 36.823 | 36.5664 | 36.3116 | 36.0586 | 35.8073 | 35.5577 | 35.3099 | 35.0639 | 34.8195 | 0.012172 | 0.024535 | 0.041054 | 0.064046 | 0.09215 | 0.12818 | 0.17253 | 0.27921 | 0.36665 | 0.45127 | -0.090772 | -0.11383 | -0.13875 | -0.16122 | -0.17874 | -0.19103 | -0.1991 | -0.18669 | -0.18215 | -0.17479
Railton | 85001 | 131.5049 | 109.4 | 112.9253 | 112.9253 | 112.9253 | 112.9253 | 112.9253 | 112.9253 | 112.9253 | 112.9253 | 112.9253 | 112.9253 | 190.3 | 195.0522 | 195.0522 | 195.0522 | 195.0522 | 195.0522 | 195.0522 | 195.0522 | 195.0522 | 195.0522 | 195.0522 | 195.0522 | 0.11127 | 0.22644 | 0.36308 | 0.52083 | 0.68818 | 0.87945 | 1.0985 | 1.5838 | 1.9912 | 2.3781 | -1.1977 | -1.4459 | -1.7107 | -1.9586 | -2.1661 | -2.3406 | -2.4919 | -2.6086 | -2.74 | -2.8442
Railton | 85002 | 168.2973 | 161.4 | 161.4 | 161.4 | 161.4 | 161.4 | 161.4 | 161.4 | 161.4 | 161.4 | 161.4 | 161.4 | 151.6 | 152.8407 | 152.8407 | 152.8407 | 152.8407 | 152.8407 | 152.8407 | 152.8407 | 152.8407 | 152.8407 | 152.8407 | 152.8407 | 0.086832 | 0.17279 | 0.27606 | 0.39802 | 0.53007 | 0.68386 | 0.86236 | 1.264 | 1.6005 | 1.9218 | -0.87433 | -1.0573 | -1.2526 | -1.4342 | -1.5846 | -1.7085 | -1.813 | -1.876 | -1.9554 | -2.0149
Railton | 85003 | 103.6683 | 80.6 | 81.1075 | 81.1075 | 81.1075 | 81.1075 | 81.1075 | 81.1075 | 81.1075 | 81.1075 | 81.1075 | 81.1075 | 93.2 | 95.2774 | 95.7849 | 95.7849 | 95.7849 | 95.7849 | 95.7849 | 95.7849 | 95.7849 | 95.7849 | 95.7849 | 95.7849 | 0.056202 | 0.11499 | 0.18492 | 0.26539 | 0.35032 | 0.44664 | 0.55626 | 0.79675 | 0.99898 | 1.1903 | -0.60063 | -0.72996 | -0.86964 | -1.0028 | -1.1168 | -1.2157 | -1.3048 | -1.3856 | -1.472 | -1.5451
Railton | 85004 | 180.8012 | 122.3 | 122.6535 | 122.6535 | 122.6535 | 122.6535 | 122.6535 | 122.6535 | 122.6535 | 122.6535 | 122.6535 | 122.6535 | 77 | 77 | 77.3535 | 77.3535 | 77.3535 | 77.3535 | 77.3535 | 77.3535 | 77.3535 | 77.3535 | 77.3535 | 77.3535 | 0.022311 | 0.046669 | 0.075175 | 0.10692 | 0.13938 | 0.17503 | 0.21465 | 0.29894 | 0.37022 | 0.43691 | -0.25222 | -0.30707 | -0.36642 | -0.4235 | -0.47302 | -0.51699 | -0.5576 | -0.60071 | -0.64411 | -0.68169
Railton | 85005 | 300.8468 | 335.2 | 345.9045 | 345.9045 | 345.9045 | 345.9045 | 345.9045 | 345.9045 | 345.9045 | 345.9045 | 345.9045 | 345.9045 | 328.5 | 330.5948 | 330.5948 | 330.5948 | 330.5948 | 330.5948 | 330.5948 | 330.5948 | 330.5948 | 330.5948 | 330.5948 | 330.5948 | 4.0308e-05 | 8.3895e-05 | 0.00013446 | 0.00018989 | 0.00024576 | 0.00030627 | 0.00037286 | 0.00051258 | 0.00063156 | 0.0007427 | -0.00041469 | -0.00051318 | -0.00061944 | -0.00072148 | -0.00080999 | -0.00088875 | -0.0009617 | -0.0010416 | -0.0011215 | -0.0011913
Railton | 85006 | 245.1891 | 237.6 | 240.4523 | 240.4523 | 240.4523 | 240.4523 | 240.4523 | 240.4523 | 240.4523 | 240.4523 | 240.4523 | 240.4523 | 173.8 | 191.292 | 191.292 | 191.292 | 191.292 | 191.292 | 191.292 | 191.292 | 191.292 | 191.292 | 191.292 | 191.292 | 0.10827 | 0.21497 | 0.34356 | 0.49637 | 0.66271 | 0.85743 | 1.0842 | 1.5967 | 2.0256 | 2.4357 | -1.082 | -1.3079 | -1.549 | -1.7725 | -1.9569 | -2.1076 | -2.2335 | -2.302 | -2.3926 | -2.4587
Railton | 85007 | 310.8741 | 410.5 | 410.5 | 410.5 | 410.5 | 410.5 | 410.5 | 410.5 | 410.5 | 410.5 | 410.5 | 410.5 | 415.5 | 418.931 | 418.931 | 418.931 | 418.931 | 418.931 | 418.931 | 418.931 | 418.931 | 418.931 | 418.931 | 418.931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Railton | 85008 | 107.2553 | 96 | 96.49 | 96.49 | 96.49 | 96.49 | 96.49 | 96.49 | 96.49 | 96.49 | 96.49 | 96.49 | 175.8 | 178.5506 | 179.0406 | 179.0406 | 179.0406 | 179.0406 | 179.0406 | 179.0406 | 179.0406 | 179.0406 | 179.0406 | 179.0406 | 0.062839 | 0.13148 | 0.21185 | 0.30144 | 0.39312 | 0.49391 | 0.60597 | 0.84454 | 1.0462 | 1.2349 | -0.7136 | -0.86817 | -1.0355 | -1.1964 | -1.336 | -1.4601 | -1.5747 | -1.6961 | -1.8185 | -1.9244
Richmond Rural Zone | 40001 | 25.7833 | 23.8333 | 23.8333 | 23.8333 | 23.8333 | 23.8333 | 23.8333 | 23.8333 | 23.8333 | 23.8333 | 23.8333 | 23.8333 | 34.4 | 36.0037 | 36.0037 | 36.0037 | 36.0037 | 36.0037 | 36.0037 | 36.0037 | 36.0037 | 36.0037 | 36.0037 | 36.0037 | 0.01268 | 0.023733 | 0.036525 | 0.050703 | 0.065197 | 0.081213 | 0.099142 | 0.13776 | 0.1704 | 0.20117 | -0.12348 | -0.14733 | -0.17262 | -0.19641 | -0.21653 | -0.23393 | -0.24957 | -0.26511 | -0.281 | -0.29447
Richmond Rural Zone | 40002 | 92.4556 | 82.6333 | 82.6333 | 82.6333 | 82.6333 | 82.6333 | 82.6333 | 82.6333 | 82.6333 | 82.6333 | 82.6333 | 82.6333 | 99.6333 | 103.0654 | 103.0654 | 103.0654 | 103.0654 | 103.0654 | 103.0654 | 103.0654 | 103.0654 | 103.0654 | 103.0654 | 103.0654 | 0.036099 | 0.074247 | 0.12078 | 0.17758 | 0.24092 | 0.3168 | 0.40666 | 0.61368 | 0.78678 | 0.95366 | -0.35366 | -0.43173 | -0.51433 | -0.58966 | -0.65017 | -0.69741 | -0.73448 | -0.741 | -0.75895 | -0.76907
Richmond Rural Zone | 40003 | 64.34 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 13.2333 | 13.3655 | 13.3655 | 13.3655 | 13.3655 | 13.3655 | 13.3655 | 13.3655 | 13.3655 | 13.3655 | 13.3655 | 13.3655 | 0.0054521 | 0.01069 | 0.016721 | 0.023339 | 0.030037 | 0.037363 | 0.045504 | 0.062866 | 0.077581 | 0.091417 | -0.05732 | -0.068667 | -0.080704 | -0.092052 | -0.10169 | -0.11008 | -0.11769 | -0.12561 | -0.1336 | -0.14044
Rokeby | 28221 | 70.7185 | 63.4 | 63.8969 | 64.1995 | 64.5034 | 64.8088 | 65.1157 | 65.424 | 65.7337 | 66.045 | 66.3577 | 66.6718 | 132.4 | 137.337 | 138.012 | 138.6902 | 139.3718 | 140.0568 | 140.7451 | 141.4368 | 142.1319 | 142.8304 | 143.5324 | 144.2378 | 0.022266 | 0.046677 | 0.07578 | 0.10876 | 0.14288 | 0.18062 | 0.22325 | 0.31484 | 0.39269 | 0.46577 | -0.20447 | -0.26143 | -0.32482 | -0.38819 | -0.44553 | -0.49894 | -0.55084 | -0.61189 | -0.67427 | -0.73041
Rokeby | 28222 | 100.1066 | 94.6 | 95.3935 | 95.8452 | 96.299 | 96.7549 | 97.213 | 97.6733 | 98.1357 | 98.6004 | 99.0672 | 99.5362 | 180.3 | 185.8123 | 186.7255 | 187.6432 | 188.5654 | 189.4921 | 190.4234 | 191.3592 | 192.2997 | 193.2448 | 194.1945 | 195.1489 | 0.062327 | 0.12233 | 0.19122 | 0.26599 | 0.34073 | 0.42133 | 0.50985 | 0.69554 | 0.85373 | 1.0021 | -0.61563 | -0.74784 | -0.88896 | -1.0235 | -1.1393 | -1.242 | -1.3372 | -1.444 | -1.55 | -1.6423
Rokeby | 28223 | 153.8451 | 158.3 | 159.6874 | 160.4434 | 161.2031 | 161.9663 | 162.7332 | 163.5037 | 164.2778 | 165.0556 | 165.8371 | 166.6222 | 284.2 | 295.2398 | 296.6908 | 298.1489 | 299.6142 | 301.0867 | 302.5664 | 304.0534 | 305.5477 | 307.0493 | 308.5583 | 310.0747 | 0.06384 | 0.12966 | 0.20652 | 0.29157 | 0.37791 | 0.47207 | 0.57626 | 0.7982 | 0.98718 | 1.1641 | -0.68989 | -0.83952 | -1.0023 | -1.1609 | -1.3006 | -1.4272 | -1.547 | -1.6837 | -1.82 | -1.9413
Rokeby | 28224 | 77.1976 | 86.3 | 86.7086 | 87.1191 | 87.5316 | 87.946 | 88.3624 | 88.7808 | 89.2012 | 89.6235 | 90.0478 | 90.4742 | 138.6 | 143.4202 | 144.1251 | 144.8334 | 145.5452 | 146.2605 | 146.9793 | 147.7016 | 148.4275 | 149.157 | 149.89 | 150.6267 | 0.02581 | 0.054105 | 0.08784 | 0.12606 | 0.16562 | 0.20937 | 0.25879 | 0.36495 | 0.4552 | 0.53992 | -0.23699 | -0.30301 | -0.37649 | -0.44995 | -0.51642 | -0.57833 | -0.63849 | -0.70926 | -0.78158 | -0.84665
Rokeby | 28225 | 4.1885 | 4.9 | 4.9295 | 4.9528 | 4.9763 | 4.9998 | 5.0235 | 5.0473 | 5.0712 | 5.0952 | 5.1193 | 5.1436 | 5.8 | 5.8733 | 5.9021 | 5.9311 | 5.9603 | 5.9896 | 6.019 | 6.0486 | 6.0783 | 6.1082 | 6.1382 | 6.1684 | 0.00034404 | 0.0007245 | 0.0011747 | 0.0016801 | 0.0021991 | 0.0027695 | 0.0034086 | 0.0047796 | 0.0059414 | 0.0070294 | -0.0033391 | -0.0042213 | -0.0051959 | -0.0061621 | -0.0070287 | -0.007829 | -0.0085999 | -0.0095008 | -0.010412 | -0.011226
Rokeby | 28228 | 60.3383 | 60.3 | 60.5855 | 60.8723 | 61.1606 | 61.4501 | 61.7411 | 62.0334 | 62.3271 | 62.6222 | 62.9187 | 63.2166 | 112.4 | 117.8531 | 118.4323 | 119.0143 | 119.5992 | 120.187 | 120.7777 | 121.3713 | 121.9678 | 122.5672 | 123.1695 | 123.7749 | 0.020252 | 0.042454 | 0.068924 | 0.098917 | 0.12996 | 0.16428 | 0.20306 | 0.28636 | 0.35718 | 0.42365 | -0.18596 | -0.23776 | -0.29542 | -0.35306 | -0.40521 | -0.45379 | -0.501 | -0.55653 | -0.61327 | -0.66434
Rokeby | 28229 | 6.8339 | 7.2 | 7.2662 | 7.3006 | 7.3352 | 7.3699 | 7.4048 | 7.4398 | 7.4751 | 7.5104 | 7.546 | 7.5817 | 13.4 | 13.9525 | 14.0211 | 14.09 | 14.1592 | 14.2288 | 14.2987 | 14.369 | 14.4396 | 14.5106 | 14.5819 | 14.6536 | 0.0020062 | 0.0042056 | 0.0068279 | 0.009799 | 0.012874 | 0.016274 | 0.020116 | 0.028368 | 0.035383 | 0.041968 | -0.018421 | -0.023554 | -0.029265 | -0.034975 | -0.040142 | -0.044954 | -0.049631 | -0.055131 | -0.060753 | -0.065811
Rokeby | 28230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rokeby | 28231 | 138.0716 | 161.5 | 165.3339 | 166.1167 | 166.9032 | 167.6935 | 168.4874 | 169.2852 | 170.0867 | 170.892 | 171.7011 | 172.514 | 254.5 | 263.6844 | 264.9803 | 266.2826 | 267.5913 | 268.9064 | 270.2279 | 271.556 | 272.8906 | 274.2317 | 275.5794 | 276.9338 | 0.036456 | 0.076781 | 0.12449 | 0.17804 | 0.23301 | 0.29343 | 0.36109 | 0.50627 | 0.62928 | 0.74446 | -0.35428 | -0.44777 | -0.55103 | -0.65338 | -0.74516 | -0.82991 | -0.91153 | -1.0069 | -1.1033 | -1.1894
Rokeby | 28232 | 110.2741 | 103.3 | 104.26 | 104.7536 | 105.2496 | 105.7479 | 106.2486 | 106.7517 | 107.2571 | 107.7649 | 108.2751 | 108.7878 | 193.6 | 201.5046 | 202.495 | 203.4901 | 204.4902 | 205.4952 | 206.5051 | 207.52 | 208.5399 | 209.5647 | 210.5947 | 211.6296 | 0.073264 | 0.13946 | 0.21624 | 0.3006 | 0.38582 | 0.47848 | 0.58085 | 0.79676 | 0.98158 | 1.1553 | -0.65845 | -0.80674 | -0.96681 | -1.1213 | -1.2559 | -1.3769 | -1.4901 | -1.6176 | -1.7459 | -1.8589
Rosebery (22 kV) | 97001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.8 | 36.374 | 36.374 | 36.374 | 36.374 | 36.374 | 36.374 | 36.374 | 36.374 | 36.374 | 36.374 | 36.374 | 2.092e-05 | 4.3124e-05 | 7.2067e-05 | 0.0001106 | 0.00015618 | 0.00021304 | 0.00028182 | 0.00044402 | 0.00057709 | 0.00070493 | -0.00016488 | -0.0002095 | -0.00025857 | -0.00030493 | -0.00034369 | -0.00037506 | -0.00040098 | -0.00040447 | -0.00041793 | -0.00042591
Rosebery (22 kV) | 97002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.2 | 36.8103 | 36.8103 | 36.8103 | 36.8103 | 36.8103 | 36.8103 | 36.8103 | 36.8103 | 36.8103 | 36.8103 | 36.8103 | 0.024542 | 0.049013 | 0.080751 | 0.12293 | 0.17287 | 0.23534 | 0.3111 | 0.49034 | 0.63781 | 0.77998 | -0.19087 | -0.23934 | -0.29197 | -0.34066 | -0.38021 | -0.41073 | -0.43427 | -0.4285 | -0.43489 | -0.43536
Rosebery (44 kV) | 97013 | 0 | 30.16 | 30.16 | 30.16 | 30.16 | 30.16 | 30.16 | 30.16 | 30.16 | 30.16 | 30.16 | 30.16 | 23.07 | 23.07 | 23.07 | 23.07 | 23.07 | 23.07 | 23.07 | 23.07 | 23.07 | 23.07 | 23.07 | 23.07 | 0.00033808 | 0.00059326 | 0.0010189 | 0.0018044 | 0.0029297 | 0.0045646 | 0.0067263 | 0.012289 | 0.016825 | 0.021335 | -0.0007686 | -0.00094784 | -0.0010703 | -0.00098539 | -0.0006686 | -4.4228e-05 | 0.00030892 | 0.00043093 | 0.00053772 | 0.00063947
Rosebery (44 kV) | 97014 | 0 | 220.87 | 220.87 | 220.87 | 220.87 | 220.87 | 220.87 | 220.87 | 220.87 | 220.87 | 220.87 | 220.87 | 209.54 | 212.34 | 212.34 | 212.34 | 212.34 | 212.34 | 212.34 | 212.34 | 212.34 | 212.34 | 212.34 | 212.34 | 2.092e-05 | 4.3124e-05 | 7.2067e-05 | 0.0001106 | 0.00015618 | 0.00021304 | 0.00028182 | 0.00044402 | 0.00057709 | 0.00070493 | -0.00016488 | -0.0002095 | -0.00025857 | -0.00030493 | -0.00034369 | -0.00037506 | -0.00040098 | -0.00040447 | -0.00041793 | -0.00042591
Rosny Park Zone | 23340 | 166.6539 | 87.6 | 88.7121 | 89.8383 | 90.9788 | 92.1338 | 93.3035 | 94.488 | 95.6875 | 96.9023 | 98.1324 | 99.3782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0037327 | 0.0078637 | 0.012749 | 0.018229 | 0.023852 | 0.030029 | 0.036944 | 0.051779 | 0.064345 | 0.076111 | -0.036395 | -0.045969 | -0.056538 | -0.067009 | -0.076393 | -0.085053 | -0.093389 | -0.10312 | -0.11296 | -0.12174
Rosny Park Zone | 23341 | 75.2072 | 63.8667 | 64.8699 | 65.6934 | 66.5274 | 67.372 | 68.2272 | 69.0934 | 69.9705 | 70.8588 | 71.7584 | 72.6694 | 129.4 | 135.4134 | 136.7685 | 138.1371 | 139.5195 | 140.9156 | 142.3258 | 143.75 | 145.1885 | 146.6414 | 148.1089 | 149.591 | 0.023453 | 0.049408 | 0.080099 | 0.11453 | 0.14986 | 0.18867 | 0.23212 | 0.32533 | 0.40428 | 0.47821 | -0.22867 | -0.28883 | -0.35523 | -0.42102 | -0.47998 | -0.53439 | -0.58676 | -0.64793 | -0.70975 | -0.76491
Rosny Park Zone | 23342 | 134.49 | 123.0333 | 125.3254 | 126.9164 | 128.5276 | 130.1593 | 131.8117 | 133.485 | 135.1797 | 136.8958 | 138.6337 | 140.3937 | 199.2667 | 209.3365 | 211.4313 | 213.5471 | 215.684 | 217.8424 | 220.0223 | 222.2241 | 224.4479 | 226.6939 | 228.9625 | 231.2537 | 0.029449 | 0.062815 | 0.10226 | 0.14655 | 0.19203 | 0.24205 | 0.29804 | 0.41839 | 0.52022 | 0.61556 | -0.29132 | -0.36846 | -0.45351 | -0.53762 | -0.61284 | -0.6821 | -0.7486 | -0.82577 | -0.90382 | -0.97325
Rosny Park Zone | 23343 | 133.8356 | 131.3 | 132.9669 | 134.6549 | 136.3644 | 138.0955 | 139.8487 | 141.6241 | 143.422 | 145.2427 | 147.0866 | 148.9539 | 186.3333 | 200.1697 | 202.1728 | 204.1959 | 206.2393 | 208.3032 | 210.3876 | 212.493 | 214.6194 | 216.7671 | 218.9363 | 221.1272 | 0.02877 | 0.06061 | 0.09826 | 0.1405 | 0.18384 | 0.23145 | 0.28474 | 0.39909 | 0.49595 | 0.58663 | -0.28052 | -0.35431 | -0.43577 | -0.51648 | -0.5888 | -0.65555 | -0.7198 | -0.79483 | -0.87067 | -0.93834
Rosny Park Zone | 23346 | 0 | 27 | 27.3428 | 27.6899 | 28.0414 | 28.3974 | 28.7579 | 29.123 | 29.4927 | 29.8671 | 30.2463 | 30.6303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rosny Park Zone | 23347 | 69.3872 | 69.0667 | 70.5289 | 71.4243 | 72.331 | 73.2493 | 74.1792 | 75.1209 | 76.0746 | 77.0403 | 78.0184 | 79.0088 | 127.1333 | 133.4102 | 134.7452 | 136.0936 | 137.4555 | 138.831 | 140.2203 | 141.6235 | 143.0407 | 144.4721 | 145.9179 | 147.3781 | 0.0191 | 0.040248 | 0.065256 | 0.093313 | 0.12211 | 0.15374 | 0.18915 | 0.26512 | 0.32948 | 0.38973 | -0.18632 | -0.23533 | -0.28942 | -0.34302 | -0.39104 | -0.43536 | -0.47801 | -0.52781 | -0.57815 | -0.62305
Rosny Park Zone | 23348 | 88.9817 | 80.0667 | 81.3937 | 82.427 | 83.4734 | 84.5331 | 85.6063 | 86.6931 | 87.7937 | 88.9082 | 90.0369 | 91.1799 | 160.2667 | 167.643 | 169.3206 | 171.015 | 172.7263 | 174.4548 | 176.2006 | 177.9638 | 179.7447 | 181.5434 | 183.3601 | 185.195 | 0.029721 | 0.063637 | 0.10373 | 0.14876 | 0.19501 | 0.24589 | 0.30284 | 0.42535 | 0.52895 | 0.62596 | -0.29532 | -0.37367 | -0.46003 | -0.54538 | -0.62167 | -0.69186 | -0.7592 | -0.83719 | -0.91609 | -0.98622
Sandy Bay Zone | 12017 | 116.37 | 109.3333 | 110.3723 | 110.787 | 111.2033 | 111.6211 | 112.0404 | 112.4614 | 112.8839 | 113.308 | 113.7337 | 114.161 | 196.7333 | 202.003 | 202.8424 | 203.6853 | 204.5317 | 205.3817 | 206.2351 | 207.0921 | 207.9526 | 208.8168 | 209.6845 | 210.5558 | 0.054293 | 0.1022 | 0.15831 | 0.22072 | 0.28435 | 0.35401 | 0.43138 | 0.59827 | 0.73831 | 0.8689 | -0.48637 | -0.59536 | -0.71406 | -0.82978 | -0.93171 | -1.0241 | -1.1116 | -1.2111 | -1.3103 | -1.3971
Sandy Bay Zone | 12018 | 104.95 | 69.2333 | 69.6416 | 69.9033 | 70.1659 | 70.4295 | 70.6941 | 70.9597 | 71.2264 | 71.494 | 71.7626 | 72.0322 | 151.7333 | 153.5387 | 154.1768 | 154.8174 | 155.4608 | 156.1068 | 156.7554 | 157.4068 | 158.0609 | 158.7177 | 159.3773 | 160.0395 | 0.032969 | 0.062147 | 0.097004 | 0.13712 | 0.17927 | 0.22736 | 0.282 | 0.40239 | 0.50217 | 0.59488 | -0.27392 | -0.33975 | -0.41199 | -0.48283 | -0.54554 | -0.60245 | -0.65631 | -0.71561 | -0.7749 | -0.8252
Sandy Bay Zone | 12019 | 98.7094 | 107.3 | 108.7889 | 109.1977 | 109.6079 | 110.0197 | 110.4331 | 110.848 | 111.2645 | 111.6825 | 112.1021 | 112.5233 | 192.8 | 208.0616 | 208.9262 | 209.7944 | 210.6662 | 211.5416 | 212.4206 | 213.3033 | 214.1897 | 215.0797 | 215.9735 | 216.8709 | 0.040231 | 0.075837 | 0.11837 | 0.16733 | 0.21875 | 0.27745 | 0.34412 | 0.49103 | 0.61279 | 0.72592 | -0.33426 | -0.41459 | -0.50274 | -0.58919 | -0.66571 | -0.73516 | -0.80089 | -0.87324 | -0.9456 | -1.007
Sandy Bay Zone | 12030 | 117.0328 | 82.3667 | 83.9583 | 84.2738 | 84.5904 | 84.9082 | 85.2272 | 85.5474 | 85.8688 | 86.1914 | 86.5153 | 86.8403 | 222.2333 | 225.5485 | 226.4858 | 227.4269 | 228.372 | 229.3209 | 230.2739 | 231.2307 | 232.1916 | 233.1565 | 234.1253 | 235.0982 | 0.040111 | 0.078033 | 0.12275 | 0.17308 | 0.22494 | 0.28228 | 0.34682 | 0.48661 | 0.60333 | 0.71227 | -0.34853 | -0.43464 | -0.5287 | -0.62061 | -0.7017 | -0.77524 | -0.84478 | -0.92276 | -1.0013 | -1.0693
Sandy Bay Zone | 12031 | 148.5406 | 96.4333 | 97.262 | 97.6274 | 97.9942 | 98.3624 | 98.7319 | 99.1029 | 99.4752 | 99.849 | 100.2241 | 100.6007 | 239.2667 | 246.5688 | 247.5934 | 248.6222 | 249.6554 | 250.6928 | 251.7345 | 252.7806 | 253.831 | 254.8858 | 255.9449 | 257.0085 | 0.054259 | 0.10695 | 0.16861 | 0.23706 | 0.30675 | 0.38294 | 0.46736 | 0.6481 | 0.80123 | 0.94451 | -0.48512 | -0.60519 | -0.73599 | -0.8635 | -0.9758 | -1.0776 | -1.1738 | -1.2831 | -1.3931 | -1.4896
Sandy Bay Zone | 12032 | 68.5322 | 62.1667 | 62.5736 | 62.8087 | 63.0447 | 63.2816 | 63.5193 | 63.758 | 63.9975 | 64.238 | 64.4793 | 64.7216 | 118.5333 | 122.1057 | 122.6131 | 123.1226 | 123.6343 | 124.148 | 124.6639 | 125.1819 | 125.7021 | 126.2245 | 126.749 | 127.2757 | 0.025917 | 0.048885 | 0.076321 | 0.10789 | 0.14106 | 0.17891 | 0.2219 | 0.31662 | 0.39513 | 0.46808 | -0.21543 | -0.26725 | -0.3241 | -0.37986 | -0.4292 | -0.47398 | -0.51636 | -0.56302 | -0.60967 | -0.64923
Sandy Bay Zone | 12033 | 40.3833 | 30.4 | 30.6797 | 30.7949 | 30.9106 | 31.0268 | 31.1433 | 31.2604 | 31.3778 | 31.4957 | 31.614 | 31.7328 | 68.1 | 70.2694 | 70.5613 | 70.8546 | 71.149 | 71.4446 | 71.7415 | 72.0396 | 72.339 | 72.6396 | 72.9414 | 73.2445 | 0.013323 | 0.025103 | 0.039124 | 0.055161 | 0.071921 | 0.090874 | 0.1124 | 0.15941 | 0.19863 | 0.23509 | -0.11232 | -0.13894 | -0.16811 | -0.19668 | -0.22195 | -0.24488 | -0.26658 | -0.29058 | -0.31464 | -0.33514
Sandy Bay Zone | 12034 | 0.023333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandy Bay Zone | 12035 | 107.7383 | 80.2 | 81.2345 | 81.5397 | 81.846 | 82.1535 | 82.4622 | 82.772 | 83.083 | 83.3951 | 83.7085 | 84.023 | 223.4 | 231.38 | 232.3415 | 233.307 | 234.2765 | 235.25 | 236.2276 | 237.2092 | 238.1949 | 239.1847 | 240.1786 | 241.1766 | 0.031639 | 0.059639 | 0.09309 | 0.13159 | 0.17203 | 0.21819 | 0.27062 | 0.38615 | 0.48191 | 0.57088 | -0.26287 | -0.32604 | -0.39536 | -0.46335 | -0.52353 | -0.57814 | -0.62983 | -0.68673 | -0.74363 | -0.7919
Sandy Bay Zone | 12036 | 153.7844 | 141.9667 | 142.5001 | 143.0354 | 143.5728 | 144.1123 | 144.6537 | 145.1972 | 145.7427 | 146.2903 | 146.8399 | 147.3916 | 200.2 | 206.4474 | 207.3053 | 208.1668 | 209.0318 | 209.9004 | 210.7726 | 211.6485 | 212.5279 | 213.4111 | 214.2979 | 215.1884 | 7.1906e-05 | 0.00013554 | 0.00021157 | 0.00029906 | 0.00039098 | 0.00049589 | 0.00061505 | 0.00087761 | 0.0010952 | 0.0012974 | -0.00059743 | -0.00074101 | -0.00089856 | -0.0010531 | -0.0011898 | -0.001314 | -0.0014314 | -0.0015608 | -0.0016901 | -0.0017998
Sandy Bay Zone | 12037 | 119.0361 | 109.1 | 109.5099 | 109.9213 | 110.3343 | 110.7489 | 111.165 | 111.5826 | 112.0019 | 112.4227 | 112.845 | 113.269 | 143.7333 | 149.1527 | 149.7725 | 150.3949 | 151.0198 | 151.6474 | 152.2776 | 152.9103 | 153.5457 | 154.1838 | 154.8245 | 155.4678 | 0.0084849 | 0.015994 | 0.024965 | 0.035289 | 0.046136 | 0.058515 | 0.072576 | 0.10356 | 0.12924 | 0.1531 | -0.070496 | -0.087439 | -0.10603 | -0.12426 | -0.1404 | -0.15505 | -0.16891 | -0.18417 | -0.19943 | -0.21237
Sandy Bay Zone | 12038 | 91.7244 | 97.4333 | 98.4381 | 98.8079 | 99.1791 | 99.5518 | 99.9258 | 100.3012 | 100.6781 | 101.0563 | 101.436 | 101.8171 | 213.6 | 221.1997 | 222.1189 | 223.0419 | 223.9687 | 224.8994 | 225.834 | 226.7724 | 227.7147 | 228.661 | 229.6112 | 230.5653 | 0.034555 | 0.066063 | 0.10317 | 0.14483 | 0.18767 | 0.23494 | 0.28806 | 0.40294 | 0.49893 | 0.58847 | -0.30476 | -0.37636 | -0.45453 | -0.53089 | -0.59828 | -0.65941 | -0.71725 | -0.78241 | -0.84771 | -0.90447
Sandy Bay Zone | 12039 | 119.015 | 105.8667 | 106.2644 | 106.6637 | 107.0644 | 107.4667 | 107.8704 | 108.2757 | 108.6825 | 109.0909 | 109.5007 | 109.9121 | 196.7 | 203.5824 | 204.4284 | 205.2779 | 206.1309 | 206.9875 | 207.8476 | 208.7113 | 209.5786 | 210.4495 | 211.324 | 212.2021 | 0.041002 | 0.077987 | 0.12212 | 0.17283 | 0.22604 | 0.28671 | 0.35558 | 0.50724 | 0.63293 | 0.74967 | -0.34292 | -0.42629 | -0.51766 | -0.60717 | -0.68631 | -0.75806 | -0.8259 | -0.90061 | -0.97517 | -1.0383
Savage River | 95001 | 25.3 | 24 | 24.9206 | 24.9206 | 24.9206 | 24.9206 | 24.9206 | 24.9206 | 24.9206 | 24.9206 | 24.9206 | 24.9206 | 32.8 | 33.9432 | 33.9432 | 33.9432 | 33.9432 | 33.9432 | 33.9432 | 33.9432 | 33.9432 | 33.9432 | 33.9432 | 33.9432 | 0.011228 | 0.021197 | 0.033998 | 0.05095 | 0.071054 | 0.09634 | 0.12718 | 0.20061 | 0.26136 | 0.32034 | -0.085333 | -0.1045 | -0.12475 | -0.1426 | -0.15609 | -0.16519 | -0.17063 | -0.1606 | -0.15597 | -0.14928
Scottsdale | 54003 | 161.4444 | 157.3333 | 157.3874 | 157.3874 | 157.3874 | 157.3874 | 157.3874 | 157.3874 | 157.3874 | 157.3874 | 157.3874 | 157.3874 | 143.6667 | 146.1405 | 146.1405 | 146.1405 | 146.1405 | 146.1405 | 146.1405 | 146.1405 | 146.1405 | 146.1405 | 146.1405 | 146.1405 | 0.08086 | 0.15989 | 0.25718 | 0.37652 | 0.50968 | 0.66867 | 0.85617 | 1.2856 | 1.6437 | 1.9871 | -0.66484 | -0.83099 | -1.0099 | -1.177 | -1.3155 | -1.4285 | -1.5227 | -1.5638 | -1.6278 | -1.6734
Scottsdale | 54004 | 14.3333 | 18 | 18.2606 | 18.2606 | 18.2606 | 18.2606 | 18.2606 | 18.2606 | 18.2606 | 18.2606 | 18.2606 | 18.2606 | 20.6667 | 20.6667 | 20.6667 | 20.6667 | 20.6667 | 20.6667 | 20.6667 | 20.6667 | 20.6667 | 20.6667 | 20.6667 | 20.6667 | 0.0051568 | 0.010876 | 0.01767 | 0.02552 | 0.033852 | 0.043374 | 0.05428 | 0.078425 | 0.098715 | 0.11799 | -0.062688 | -0.075065 | -0.088303 | -0.10073 | -0.11115 | -0.11995 | -0.12762 | -0.1336 | -0.14032 | -0.14563
Scottsdale | 54005 | 95.6944 | 96.3333 | 96.3333 | 96.3333 | 96.3333 | 96.3333 | 96.3333 | 96.3333 | 96.3333 | 96.3333 | 96.3333 | 96.3333 | 86.6667 | 88.225 | 88.225 | 88.225 | 88.225 | 88.225 | 88.225 | 88.225 | 88.225 | 88.225 | 88.225 | 88.225 | 0.088129 | 0.16025 | 0.24478 | 0.34082 | 0.44139 | 0.55515 | 0.68456 | 0.96924 | 1.2081 | 1.4343 | -0.79334 | -0.94684 | -1.109 | -1.2593 | -1.3837 | -1.4875 | -1.5767 | -1.6468 | -1.7237 | -1.7842
Scottsdale | 54006 | 5.2444 | 3.3333 | 3.3552 | 3.3552 | 3.3552 | 3.3552 | 3.3552 | 3.3552 | 3.3552 | 3.3552 | 3.3552 | 3.3552 | 3.3333 | 3.3333 | 3.3333 | 3.3333 | 3.3333 | 3.3333 | 3.3333 | 3.3333 | 3.3333 | 3.3333 | 3.3333 | 3.3333 | 0.0041605 | 0.0087029 | 0.014098 | 0.020331 | 0.026946 | 0.034506 | 0.043164 | 0.062331 | 0.078438 | 0.093736 | -0.049899 | -0.059727 | -0.070237 | -0.080097 | -0.088372 | -0.095355 | -0.10143 | -0.10618 | -0.11151 | -0.11571
Scottsdale | 54007 | 63.3333 | 58.6667 | 58.7638 | 58.7638 | 58.7638 | 58.7638 | 58.7638 | 58.7638 | 58.7638 | 58.7638 | 58.7638 | 58.7638 | 103 | 104.8026 | 104.8026 | 104.8026 | 104.8026 | 104.8026 | 104.8026 | 104.8026 | 104.8026 | 104.8026 | 104.8026 | 104.8026 | 0.037542 | 0.079177 | 0.12864 | 0.18579 | 0.24644 | 0.31576 | 0.39516 | 0.57094 | 0.71865 | 0.85894 | -0.45637 | -0.54647 | -0.64285 | -0.73328 | -0.80919 | -0.87326 | -0.92904 | -0.97263 | -1.0216 | -1.0602
Smithton | 93001 | 199.5537 | 109.6117 | 109.3501 | 109.3501 | 109.3501 | 109.3501 | 109.3501 | 109.3501 | 109.3501 | 109.3501 | 109.3501 | 109.3501 | 41.0165 | 41.0165 | 41.0165 | 41.0165 | 41.0165 | 41.0165 | 41.0165 | 41.0165 | 41.0165 | 41.0165 | 41.0165 | 41.0165 | 0.0080013 | 0.016954 | 0.02777 | 0.040444 | 0.053997 | 0.069505 | 0.087241 | 0.12631 | 0.15911 | 0.1901 | -0.096146 | -0.11614 | -0.13809 | -0.15941 | -0.17806 | -0.19462 | -0.2099 | -0.22451 | -0.24007 | -0.25359
Smithton | 93002 | 179.6288 | 175.9413 | 176.0583 | 176.0583 | 176.0583 | 176.0583 | 176.0583 | 176.0583 | 176.0583 | 176.0583 | 176.0583 | 176.0583 | 90.08 | 90.08 | 90.08 | 90.08 | 90.08 | 90.08 | 90.08 | 90.08 | 90.08 | 90.08 | 90.08 | 90.08 | 0.024951 | 0.05287 | 0.086599 | 0.12612 | 0.16839 | 0.21675 | 0.27206 | 0.3939 | 0.49616 | 0.59283 | -0.29982 | -0.36218 | -0.43062 | -0.49711 | -0.55526 | -0.6069 | -0.65456 | -0.70012 | -0.74864 | -0.7908
Smithton | 93003 | 131.2854 | 126.1746 | 128.9746 | 128.9746 | 128.9746 | 128.9746 | 128.9746 | 128.9746 | 128.9746 | 128.9746 | 128.9746 | 128.9746 | 45.3135 | 45.3135 | 48.1135 | 48.1135 | 48.1135 | 48.1135 | 48.1135 | 48.1135 | 48.1135 | 48.1135 | 48.1135 | 48.1135 | 0.032926 | 0.069768 | 0.11428 | 0.16643 | 0.22221 | 0.28602 | 0.35901 | 0.5198 | 0.65474 | 0.78231 | -0.39565 | -0.47794 | -0.56825 | -0.65599 | -0.73274 | -0.80087 | -0.86378 | -0.92389 | -0.98792 | -1.0436
Smithton | 93004 | 91.9929 | 109.6898 | 114.4758 | 114.4758 | 114.4758 | 114.4758 | 114.4758 | 114.4758 | 114.4758 | 114.4758 | 114.4758 | 114.4758 | 50.6261 | 50.6261 | 50.6261 | 50.6261 | 50.6261 | 50.6261 | 50.6261 | 50.6261 | 50.6261 | 50.6261 | 50.6261 | 50.6261 | 0.0078171 | 0.016564 | 0.027131 | 0.039513 | 0.052754 | 0.067905 | 0.085232 | 0.12341 | 0.15544 | 0.18573 | -0.093932 | -0.11347 | -0.13491 | -0.15574 | -0.17396 | -0.19014 | -0.20507 | -0.21934 | -0.23454 | -0.24775
Smithton | 93005 | 155.0736 | 102.971 | 105.435 | 105.435 | 105.435 | 105.435 | 105.435 | 105.435 | 105.435 | 105.435 | 105.435 | 105.435 | 77.4235 | 77.4235 | 77.4235 | 77.4235 | 77.4235 | 77.4235 | 77.4235 | 77.4235 | 77.4235 | 77.4235 | 77.4235 | 77.4235 | 0.035085 | 0.074341 | 0.12177 | 0.17734 | 0.23677 | 0.30477 | 0.38254 | 0.55387 | 0.69766 | 0.83358 | -0.42159 | -0.50927 | -0.6055 | -0.69899 | -0.78077 | -0.85337 | -0.92039 | -0.98445 | -1.0527 | -1.112
Smithton | 93006 | 66.5444 | 67.5014 | 67.5014 | 67.5014 | 67.5014 | 67.5014 | 67.5014 | 67.5014 | 67.5014 | 67.5014 | 67.5014 | 67.5014 | 50.548 | 50.548 | 50.548 | 50.548 | 50.548 | 50.548 | 50.548 | 50.548 | 50.548 | 50.548 | 50.548 | 50.548 | 2.632e-05 | 5.577e-05 | 9.1349e-05 | 0.00013304 | 0.00017762 | 0.00022864 | 0.00028698 | 0.00041551 | 0.00052337 | 0.00062534 | -0.00031627 | -0.00038205 | -0.00045424 | -0.00052438 | -0.00058572 | -0.00064019 | -0.00069047 | -0.00073852 | -0.0007897 | -0.00083417
Sorell | 41511 | 70.8182 | 72.7733 | 72.7733 | 72.7733 | 72.7733 | 72.7733 | 72.7733 | 72.7733 | 72.7733 | 72.7733 | 72.7733 | 72.7733 | 129.3748 | 133.77 | 133.77 | 133.77 | 133.77 | 133.77 | 133.77 | 133.77 | 133.77 | 133.77 | 133.77 | 133.77 | 0.06029 | 0.12445 | 0.19972 | 0.28292 | 0.36709 | 0.45825 | 0.55891 | 0.77246 | 0.95475 | 1.1251 | -0.57452 | -0.72414 | -0.88905 | -1.0524 | -1.199 | -1.3347 | -1.4657 | -1.6227 | -1.78 | -1.9212
Sorell | 41512 | 112.2908 | 80.8592 | 80.8592 | 80.8592 | 80.8592 | 80.8592 | 80.8592 | 80.8592 | 80.8592 | 80.8592 | 80.8592 | 80.8592 | 104.2967 | 108.7384 | 108.7384 | 108.7384 | 108.7384 | 108.7384 | 108.7384 | 108.7384 | 108.7384 | 108.7384 | 108.7384 | 108.7384 | 0.01895 | 0.037212 | 0.058439 | 0.081912 | 0.10579 | 0.13195 | 0.16102 | 0.2229 | 0.2755 | 0.32494 | -0.18776 | -0.22835 | -0.27204 | -0.31399 | -0.35034 | -0.38271 | -0.41276 | -0.44548 | -0.47852 | -0.50746
Sorell | 41513 | 101.5096 | 97.3826 | 97.3826 | 97.3826 | 97.3826 | 97.3826 | 97.3826 | 97.3826 | 97.3826 | 97.3826 | 97.3826 | 97.3826 | 150.2341 | 154.0362 | 154.0362 | 154.0362 | 154.0362 | 154.0362 | 154.0362 | 154.0362 | 154.0362 | 154.0362 | 154.0362 | 154.0362 | 0.064052 | 0.12783 | 0.20246 | 0.28562 | 0.37076 | 0.46454 | 0.56918 | 0.79265 | 0.98322 | 1.1629 | -0.60503 | -0.74871 | -0.90434 | -1.0547 | -1.1856 | -1.3026 | -1.4115 | -1.5286 | -1.6486 | -1.7538
Sorell | 41514 | 74.1092 | 46.289 | 46.289 | 46.289 | 46.289 | 46.289 | 46.289 | 46.289 | 46.289 | 46.289 | 46.289 | 46.289 | 63.8671 | 65.7428 | 65.7428 | 65.7428 | 65.7428 | 65.7428 | 65.7428 | 65.7428 | 65.7428 | 65.7428 | 65.7428 | 65.7428 | 0.035822 | 0.073828 | 0.11888 | 0.17017 | 0.22372 | 0.28376 | 0.3516 | 0.49872 | 0.62352 | 0.74152 | -0.35548 | -0.44072 | -0.53347 | -0.62314 | -0.70122 | -0.77063 | -0.83482 | -0.89994 | -0.96822 | -1.0278
Sorell | 41515 | 89.6717 | 79.2186 | 79.2186 | 79.2186 | 79.2186 | 79.2186 | 79.2186 | 79.2186 | 79.2186 | 79.2186 | 79.2186 | 79.2186 | 126.7966 | 130.4681 | 130.4681 | 130.4681 | 130.4681 | 130.4681 | 130.4681 | 130.4681 | 130.4681 | 130.4681 | 130.4681 | 130.4681 | 0.11607 | 0.22624 | 0.35913 | 0.5153 | 0.68307 | 0.87632 | 1.0987 | 1.5925 | 2.0081 | 2.4032 | -0.96905 | -1.2114 | -1.4753 | -1.7287 | -1.9471 | -2.1373 | -2.3093 | -2.4589 | -2.627 | -2.7689
Sorell | 41516 | 152.6188 | 80.2733 | 81.3906 | 81.3906 | 81.3906 | 81.3906 | 81.3906 | 81.3906 | 81.3906 | 81.3906 | 81.3906 | 81.3906 | 124.3357 | 129.7075 | 130.5825 | 130.5825 | 130.5825 | 130.5825 | 130.5825 | 130.5825 | 130.5825 | 130.5825 | 130.5825 | 130.5825 | 0.081337 | 0.16157 | 0.25841 | 0.37345 | 0.49854 | 0.64471 | 0.81477 | 1.1981 | 1.5198 | 1.8274 | -0.75453 | -0.92555 | -1.1091 | -1.2815 | -1.4258 | -1.5466 | -1.6507 | -1.7197 | -1.8051 | -1.873
Sorell | 41517 | 80.1996 | 73.5172 | 73.5172 | 73.5172 | 73.5172 | 73.5172 | 73.5172 | 73.5172 | 73.5172 | 73.5172 | 73.5172 | 73.5172 | 121.8776 | 126.0728 | 126.0728 | 126.0728 | 126.0728 | 126.0728 | 126.0728 | 126.0728 | 126.0728 | 126.0728 | 126.0728 | 126.0728 | 0.092548 | 0.18861 | 0.2997 | 0.42015 | 0.53998 | 0.66787 | 0.8071 | 1.0975 | 1.3476 | 1.5807 | -0.8823 | -1.1037 | -1.3446 | -1.5802 | -1.7886 | -1.9791 | -2.161 | -2.3785 | -2.5941 | -2.7864
Sorell | 41518 | 93.3939 | 77.4235 | 77.4235 | 77.4235 | 77.4235 | 77.4235 | 77.4235 | 77.4235 | 77.4235 | 77.4235 | 77.4235 | 77.4235 | 139.8467 | 144.6642 | 144.6642 | 144.6642 | 144.6642 | 144.6642 | 144.6642 | 144.6642 | 144.6642 | 144.6642 | 144.6642 | 144.6642 | 0.097933 | 0.19903 | 0.31603 | 0.44307 | 0.56965 | 0.70498 | 0.85252 | 1.1605 | 1.4258 | 1.6732 | -0.93085 | -1.1636 | -1.4168 | -1.6643 | -1.883 | -2.0828 | -2.2733 | -2.5 | -2.7251 | -2.9257
St Leonards | 66101 | 69.7833 | 29.1 | 29.1552 | 29.1552 | 29.1552 | 29.1552 | 29.1552 | 29.1552 | 29.1552 | 29.1552 | 29.1552 | 29.1552 | 56.9 | 56.9214 | 56.9214 | 56.9214 | 56.9214 | 56.9214 | 56.9214 | 56.9214 | 56.9214 | 56.9214 | 56.9214 | 56.9214 | 0.027116 | 0.052079 | 0.081358 | 0.11391 | 0.14706 | 0.1832 | 0.22311 | 0.30862 | 0.38012 | 0.44633 | -0.25842 | -0.31543 | -0.37763 | -0.43823 | -0.49163 | -0.53999 | -0.5856 | -0.63739 | -0.68851 | -0.73323
St Leonards | 66102 | 82.985 | 70.4 | 71.2726 | 71.2726 | 71.2726 | 71.2726 | 71.2726 | 71.2726 | 71.2726 | 71.2726 | 71.2726 | 71.2726 | 181.1 | 181.1835 | 181.1835 | 181.1835 | 181.1835 | 181.1835 | 181.1835 | 181.1835 | 181.1835 | 181.1835 | 181.1835 | 181.1835 | 0.075664 | 0.14536 | 0.22708 | 0.31789 | 0.41028 | 0.51095 | 0.6221 | 0.85999 | 1.059 | 1.2431 | -0.72217 | -0.88145 | -1.0553 | -1.2247 | -1.374 | -1.5094 | -1.6372 | -1.7827 | -1.9262 | -2.0518
St Leonards | 66103 | 103.1333 | 79.1 | 80.0222 | 80.0222 | 80.0222 | 80.0222 | 80.0222 | 80.0222 | 80.0222 | 80.0222 | 80.0222 | 80.0222 | 197.8 | 197.898 | 197.898 | 197.898 | 197.898 | 197.898 | 197.898 | 197.898 | 197.898 | 197.898 | 197.898 | 197.898 | 0.063744 | 0.12291 | 0.19246 | 0.26996 | 0.34899 | 0.43526 | 0.53092 | 0.73542 | 0.90644 | 1.0647 | -0.6277 | -0.76321 | -0.91145 | -1.0564 | -1.1846 | -1.3011 | -1.4115 | -1.5378 | -1.6623 | -1.7719
St Leonards | 66104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
St Leonards | 66105 | 49.1817 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 104.8 | 107.0744 | 107.0744 | 107.0744 | 107.0744 | 107.0744 | 107.0744 | 107.0744 | 107.0744 | 107.0744 | 107.0744 | 107.0744 | 0.051841 | 0.099584 | 0.15557 | 0.21777 | 0.28105 | 0.35001 | 0.42614 | 0.58908 | 0.72535 | 0.85146 | -0.49454 | -0.60365 | -0.72271 | -0.83876 | -0.94107 | -1.0338 | -1.1213 | -1.2209 | -1.3192 | -1.4052
St Leonards | 66106 | 80.14 | 157.7 | 158.1003 | 158.1003 | 158.1003 | 158.1003 | 158.1003 | 158.1003 | 158.1003 | 158.1003 | 158.1003 | 158.1003 | 160.5 | 160.5713 | 160.5713 | 160.5713 | 160.5713 | 160.5713 | 160.5713 | 160.5713 | 160.5713 | 160.5713 | 160.5713 | 160.5713 | 0.060195 | 0.11666 | 0.18324 | 0.25771 | 0.33389 | 0.41724 | 0.51019 | 0.70859 | 0.87449 | 1.0281 | -0.61772 | -0.74741 | -0.88974 | -1.0294 | -1.1535 | -1.2668 | -1.3747 | -1.4987 | -1.621 | -1.7293
St Leonards | 66107 | 48.695 | 44.5 | 44.7893 | 44.7893 | 44.7893 | 44.7893 | 44.7893 | 44.7893 | 44.7893 | 44.7893 | 44.7893 | 44.7893 | 97.8 | 99.5743 | 99.5743 | 99.5743 | 99.5743 | 99.5743 | 99.5743 | 99.5743 | 99.5743 | 99.5743 | 99.5743 | 99.5743 | 0.023347 | 0.044848 | 0.07006 | 0.098074 | 0.12657 | 0.15763 | 0.19191 | 0.26529 | 0.32666 | 0.38346 | -0.22272 | -0.27185 | -0.32547 | -0.37774 | -0.42381 | -0.46556 | -0.50497 | -0.54985 | -0.5941 | -0.63285
St Leonards | 66108 | 2.2567 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.6 | 3.6827 | 3.6827 | 3.6827 | 3.6827 | 3.6827 | 3.6827 | 3.6827 | 3.6827 | 3.6827 | 3.6827 | 3.6827 | 8.1065e-05 | 0.00015572 | 0.00024327 | 0.00034053 | 0.00043949 | 0.00054732 | 0.00066637 | 0.00092115 | 0.0011342 | 0.0013314 | -0.00077332 | -0.00094393 | -0.0011301 | -0.0013116 | -0.0014716 | -0.0016165 | -0.0017534 | -0.0019092 | -0.0020629 | -0.0021974
St Leonards | 66109 | 30.9 | 26.9 | 26.9479 | 26.9479 | 26.9479 | 26.9479 | 26.9479 | 26.9479 | 26.9479 | 26.9479 | 26.9479 | 26.9479 | 57.3 | 57.3 | 57.3 | 57.3 | 57.3 | 57.3 | 57.3 | 57.3 | 57.3 | 57.3 | 57.3 | 57.3 | 0.025738 | 0.049442 | 0.077237 | 0.10812 | 0.13954 | 0.17377 | 0.21157 | 0.29247 | 0.36012 | 0.42274 | -0.24553 | -0.2997 | -0.35881 | -0.41643 | -0.46722 | -0.51324 | -0.55669 | -0.60617 | -0.65496 | -0.69767
St Leonards | 66110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
St Marys | 57003 | 90.3711 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 35 | 35.3797 | 35.3797 | 35.3797 | 35.3797 | 35.3797 | 35.3797 | 35.3797 | 35.3797 | 35.3797 | 35.3797 | 35.3797 | 0.02466 | 0.049441 | 0.079589 | 0.11593 | 0.15594 | 0.20322 | 0.25861 | 0.38459 | 0.4898 | 0.59053 | -0.21612 | -0.26843 | -0.32445 | -0.37651 | -0.4195 | -0.45455 | -0.48371 | -0.49789 | -0.51811 | -0.53265
St Marys | 57004 | 134.4289 | 127 | 127 | 127 | 127 | 127 | 127 | 127 | 127 | 127 | 127 | 127 | 163 | 168.4184 | 168.4184 | 168.4184 | 168.4184 | 168.4184 | 168.4184 | 168.4184 | 168.4184 | 168.4184 | 168.4184 | 168.4184 | 0.094146 | 0.1887 | 0.30376 | 0.44251 | 0.59533 | 0.77594 | 0.98757 | 1.4691 | 1.8712 | 2.2562 | -0.82452 | -1.0241 | -1.2378 | -1.4364 | -1.6004 | -1.7341 | -1.8453 | -1.8991 | -1.976 | -2.0313
St Marys | 57005 | 31.8244 | 58 | 58.0021 | 58.0021 | 58.0021 | 58.0021 | 58.0021 | 58.0021 | 58.0021 | 58.0021 | 58.0021 | 58.0021 | 60 | 60.4225 | 60.4225 | 60.4225 | 60.4225 | 60.4225 | 60.4225 | 60.4225 | 60.4225 | 60.4225 | 60.4225 | 60.4225 | 0.012056 | 0.024197 | 0.038981 | 0.056836 | 0.076529 | 0.099831 | 0.12716 | 0.1894 | 0.24136 | 0.29113 | -0.1052 | -0.13079 | -0.15817 | -0.1836 | -0.20457 | -0.22161 | -0.23574 | -0.24231 | -0.25191 | -0.25872
St Marys | 57006 | 132.7133 | 131 | 131 | 131 | 131 | 131 | 131 | 131 | 131 | 131 | 131 | 131 | 194 | 194.7492 | 194.7492 | 194.7492 | 194.7492 | 194.7492 | 194.7492 | 194.7492 | 194.7492 | 194.7492 | 194.7492 | 194.7492 | 0.14392 | 0.29403 | 0.47077 | 0.67068 | 0.87845 | 1.1108 | 1.3728 | 1.9406 | 2.42 | 2.8721 | -1.5983 | -1.9306 | -2.2883 | -2.6287 | -2.9198 | -3.173 | -3.4014 | -3.6189 | -3.8463 | -4.0374
Summerleas Zone | 32374 | 266.6667 | 103.3333 | 103.6504 | 103.6504 | 103.6504 | 103.6504 | 103.6504 | 103.6504 | 103.6504 | 103.6504 | 103.6504 | 103.6504 | 238 | 247.3439 | 247.3439 | 247.3439 | 247.3439 | 247.3439 | 247.3439 | 247.3439 | 247.3439 | 247.3439 | 247.3439 | 247.3439 | 0.0488 | 0.096863 | 0.1533 | 0.21622 | 0.28051 | 0.35101 | 0.42933 | 0.59685 | 0.7396 | 0.87343 | -0.45729 | -0.5673 | -0.68757 | -0.80524 | -0.90928 | -1.0039 | -1.0936 | -1.1953 | -1.298 | -1.389
Summerleas Zone | 32377 | 125.0111 | 123.3333 | 123.3333 | 123.3333 | 123.3333 | 123.3333 | 123.3333 | 123.3333 | 123.3333 | 123.3333 | 123.3333 | 123.3333 | 159 | 160.1844 | 160.1844 | 160.1844 | 160.1844 | 160.1844 | 160.1844 | 160.1844 | 160.1844 | 160.1844 | 160.1844 | 160.1844 | 0.015577 | 0.030919 | 0.048935 | 0.069017 | 0.089539 | 0.11204 | 0.13704 | 0.19052 | 0.23608 | 0.2788 | -0.14597 | -0.18108 | -0.21947 | -0.25704 | -0.29025 | -0.32044 | -0.34908 | -0.38154 | -0.41433 | -0.44336
Summerleas Zone | 32379 | 148.8167 | 132.3333 | 132.7569 | 132.7569 | 132.7569 | 132.7569 | 132.7569 | 132.7569 | 132.7569 | 132.7569 | 132.7569 | 132.7569 | 266.3333 | 278.6 | 278.6 | 278.6 | 278.6 | 278.6 | 278.6 | 278.6 | 278.6 | 278.6 | 278.6 | 278.6 | 0.063507 | 0.1261 | 0.19954 | 0.28131 | 0.36477 | 0.4562 | 0.55769 | 0.77467 | 0.95949 | 1.1327 | -0.59364 | -0.73689 | -0.89342 | -1.0465 | -1.1819 | -1.3049 | -1.4216 | -1.5542 | -1.688 | -1.8064
Trevallyn | 61021 | 73.4944 | 73.3333 | 73.4555 | 73.4555 | 73.4555 | 73.4555 | 73.4555 | 73.4555 | 73.4555 | 73.4555 | 73.4555 | 73.4555 | 152 | 152.0531 | 152.0531 | 152.0531 | 152.0531 | 152.0531 | 152.0531 | 152.0531 | 152.0531 | 152.0531 | 152.0531 | 152.0531 | 0.09926 | 0.17682 | 0.26634 | 0.36452 | 0.46368 | 0.57162 | 0.69081 | 0.94311 | 1.1554 | 1.3532 | -0.87905 | -1.0491 | -1.2302 | -1.4015 | -1.5477 | -1.6755 | -1.7918 | -1.9147 | -2.0364 | -2.1403
Trevallyn | 61022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Trevallyn | 61023 | 71.0333 | 77.3333 | 77.4793 | 77.4793 | 77.4793 | 77.4793 | 77.4793 | 77.4793 | 77.4793 | 77.4793 | 77.4793 | 77.4793 | 134.3333 | 135.991 | 135.991 | 135.991 | 135.991 | 135.991 | 135.991 | 135.991 | 135.991 | 135.991 | 135.991 | 135.991 | 0.11482 | 0.21081 | 0.3216 | 0.44368 | 0.56782 | 0.70419 | 0.85602 | 1.1811 | 1.4553 | 1.7127 | -1.0474 | -1.2553 | -1.4751 | -1.6804 | -1.8528 | -2.0003 | -2.1311 | -2.2575 | -2.3862 | -2.4929
Trevallyn | 61024 | 142.2272 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 160 | 162.0917 | 162.0917 | 162.0917 | 162.0917 | 162.0917 | 162.0917 | 162.0917 | 162.0917 | 162.0917 | 162.0917 | 162.0917 | 0.013862 | 0.026629 | 0.041598 | 0.058231 | 0.075153 | 0.093592 | 0.11395 | 0.15752 | 0.19396 | 0.22768 | -0.13224 | -0.16141 | -0.19325 | -0.22428 | -0.25164 | -0.27642 | -0.29982 | -0.32647 | -0.35275 | -0.37575
Trevallyn | 61025 | 73.9722 | 71.6667 | 71.2568 | 71.2568 | 71.2568 | 71.2568 | 71.2568 | 71.2568 | 71.2568 | 71.2568 | 71.2568 | 71.2568 | 160 | 160.0595 | 160.0595 | 160.0595 | 160.0595 | 160.0595 | 160.0595 | 160.0595 | 160.0595 | 160.0595 | 160.0595 | 160.0595 | 0.068739 | 0.13217 | 0.20659 | 0.28933 | 0.37356 | 0.46538 | 0.56686 | 0.78399 | 0.96559 | 1.1337 | -0.66087 | -0.8059 | -0.96425 | -1.1187 | -1.255 | -1.3786 | -1.4953 | -1.6285 | -1.7597 | -1.8748
Trevallyn | 61026 | 105.7722 | 118.3333 | 118.3333 | 118.3333 | 118.3333 | 118.3333 | 118.3333 | 118.3333 | 118.3333 | 118.3333 | 118.3333 | 118.3333 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 0.0087478 | 0.016805 | 0.026254 | 0.036753 | 0.047435 | 0.059075 | 0.071927 | 0.099432 | 0.12244 | 0.14373 | -0.083503 | -0.10192 | -0.12201 | -0.1416 | -0.15887 | -0.17452 | -0.1893 | -0.20612 | -0.22271 | -0.23724
Trevallyn | 61027 | 93.55 | 84 | 83.632 | 83.632 | 83.632 | 83.632 | 83.632 | 83.632 | 83.632 | 83.632 | 83.632 | 83.632 | 239 | 239 | 239 | 239 | 239 | 239 | 239 | 239 | 239 | 239 | 239 | 239 | 0.093281 | 0.17926 | 0.2801 | 0.39217 | 0.50622 | 0.63052 | 0.7678 | 1.0616 | 1.3073 | 1.5347 | -0.89274 | -1.0893 | -1.3038 | -1.5129 | -1.6974 | -1.8645 | -2.0224 | -2.2023 | -2.3796 | -2.535
Trevallyn | 61028 | 100.9278 | 99.3333 | 99.3333 | 99.3333 | 99.3333 | 99.3333 | 99.3333 | 99.3333 | 99.3333 | 99.3333 | 99.3333 | 99.3333 | 193.6667 | 193.6667 | 193.6667 | 193.6667 | 193.6667 | 193.6667 | 193.6667 | 193.6667 | 193.6667 | 193.6667 | 193.6667 | 193.6667 | 0.15497 | 0.27836 | 0.41899 | 0.57 | 0.71953 | 0.87925 | 1.0532 | 1.4149 | 1.721 | 2.0053 | -1.4087 | -1.6789 | -1.9647 | -2.2336 | -2.462 | -2.6615 | -2.8427 | -3.0418 | -3.2358 | -3.4013
Trevallyn | 61029 | 42.5278 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 97 | 98.3626 | 98.3626 | 98.3626 | 98.3626 | 98.3626 | 98.3626 | 98.3626 | 98.3626 | 98.3626 | 98.3626 | 98.3626 | 0.030568 | 0.061897 | 0.099079 | 0.14102 | 0.18425 | 0.23186 | 0.28514 | 0.3994 | 0.49538 | 0.58465 | -0.3273 | -0.39953 | -0.47926 | -0.55799 | -0.62835 | -0.69297 | -0.75482 | -0.82584 | -0.89684 | -0.96027
Trevallyn | 61030 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Trevallyn | 61037 | 105.2056 | 50.3333 | 50.3333 | 50.3333 | 50.3333 | 50.3333 | 50.3333 | 50.3333 | 50.3333 | 50.3333 | 50.3333 | 50.3333 | 95.6667 | 95.7018 | 95.7018 | 95.7018 | 95.7018 | 95.7018 | 95.7018 | 95.7018 | 95.7018 | 95.7018 | 95.7018 | 95.7018 | 0.036439 | 0.069997 | 0.10935 | 0.15307 | 0.19755 | 0.24602 | 0.29953 | 0.41406 | 0.50984 | 0.59849 | -0.34761 | -0.4243 | -0.50799 | -0.58956 | -0.66147 | -0.72663 | -0.78813 | -0.85818 | -0.92725 | -0.98772
Trevallyn | 61039 | 142.0072 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 148 | 148.0539 | 148.0539 | 148.0539 | 148.0539 | 148.0539 | 148.0539 | 148.0539 | 148.0539 | 148.0539 | 148.0539 | 148.0539 | 0.026062 | 0.050065 | 0.07821 | 0.10948 | 0.1413 | 0.17596 | 0.21424 | 0.29615 | 0.36466 | 0.42806 | -0.24862 | -0.30347 | -0.36333 | -0.42167 | -0.47311 | -0.51971 | -0.5637 | -0.6138 | -0.66321 | -0.70646
Trevallyn | 61040 | 117.0389 | 115.6667 | 115.6667 | 115.6667 | 115.6667 | 115.6667 | 115.6667 | 115.6667 | 115.6667 | 115.6667 | 115.6667 | 115.6667 | 161 | 168.5095 | 168.5095 | 168.5095 | 168.5095 | 168.5095 | 168.5095 | 168.5095 | 168.5095 | 168.5095 | 168.5095 | 168.5095 | 0.04655 | 0.089425 | 0.1397 | 0.19556 | 0.2524 | 0.31433 | 0.38271 | 0.52905 | 0.65144 | 0.76471 | -0.44423 | -0.54221 | -0.64913 | -0.75336 | -0.84524 | -0.9285 | -1.0071 | -1.0966 | -1.1849 | -1.2622
Trevallyn | 61041 | 76.3667 | 69.6667 | 70.1037 | 70.1037 | 70.1037 | 70.1037 | 70.1037 | 70.1037 | 70.1037 | 70.1037 | 70.1037 | 70.1037 | 158 | 160.7499 | 160.7499 | 160.7499 | 160.7499 | 160.7499 | 160.7499 | 160.7499 | 160.7499 | 160.7499 | 160.7499 | 160.7499 | 0.069776 | 0.13432 | 0.2101 | 0.29444 | 0.38035 | 0.47406 | 0.57776 | 0.79958 | 0.98509 | 1.1568 | -0.67749 | -0.82516 | -0.98653 | -1.1441 | -1.2832 | -1.4095 | -1.529 | -1.6654 | -1.7999 | -1.918
Trevallyn | 61043 | 133.9056 | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 298.3333 | 298.4291 | 298.4291 | 298.4291 | 298.4291 | 298.4291 | 298.4291 | 298.4291 | 298.4291 | 298.4291 | 298.4291 | 298.4291 | 0.14013 | 0.25832 | 0.39654 | 0.5513 | 0.71061 | 0.88713 | 1.0846 | 1.5092 | 1.8655 | 2.199 | -1.2734 | -1.5336 | -1.8127 | -2.0779 | -2.3049 | -2.503 | -2.6828 | -2.8633 | -3.0463 | -3.2015
Triabunna | 43505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012076 | 0.023776 | 0.038117 | 0.055604 | 0.075039 | 0.098194 | 0.1255 | 0.18802 | 0.24046 | 0.29092 | -0.10964 | -0.13436 | -0.16096 | -0.1859 | -0.20666 | -0.22375 | -0.23817 | -0.24535 | -0.25578 | -0.26374
Triabunna | 43506 | 79.0309 | 68.6206 | 68.6206 | 68.6206 | 68.6206 | 68.6206 | 68.6206 | 68.6206 | 68.6206 | 68.6206 | 68.6206 | 68.6206 | 91.2857 | 94.8244 | 94.8244 | 94.8244 | 94.8244 | 94.8244 | 94.8244 | 94.8244 | 94.8244 | 94.8244 | 94.8244 | 94.8244 | 0.06503 | 0.12803 | 0.20526 | 0.29942 | 0.40408 | 0.52876 | 0.67582 | 1.0125 | 1.2948 | 1.5666 | -0.59039 | -0.72349 | -0.86677 | -1.0011 | -1.1128 | -1.2049 | -1.2825 | -1.3212 | -1.3774 | -1.4202
Triabunna | 43507 | 108.4903 | 83.3138 | 83.3138 | 83.3138 | 83.3138 | 83.3138 | 83.3138 | 83.3138 | 83.3138 | 83.3138 | 83.3138 | 83.3138 | 117.9367 | 118.3747 | 118.3747 | 118.3747 | 118.3747 | 118.3747 | 118.3747 | 118.3747 | 118.3747 | 118.3747 | 118.3747 | 118.3747 | 0.064906 | 0.12779 | 0.20486 | 0.29885 | 0.4033 | 0.52775 | 0.67453 | 1.0105 | 1.2924 | 1.5636 | -0.58926 | -0.7221 | -0.86511 | -0.99915 | -1.1107 | -1.2025 | -1.2801 | -1.3187 | -1.3747 | -1.4175
Trial Harbour Zone | 99981 | 36.0167 | 30.6667 | 31.1818 | 31.1818 | 31.1818 | 31.1818 | 31.1818 | 31.1818 | 31.1818 | 31.1818 | 31.1818 | 31.1818 | 42.6667 | 44.543 | 44.543 | 44.543 | 44.543 | 44.543 | 44.543 | 44.543 | 44.543 | 44.543 | 44.543 | 44.543 | 0.061011 | 0.1021 | 0.17688 | 0.32628 | 0.5477 | 0.87131 | 1.3001 | 2.4108 | 3.3154 | 4.2165 | -0.059888 | -0.069869 | -0.064775 | -0.016832 | 0.021276 | 0.02696 | 0.033489 | 0.04714 | 0.059035 | 0.070387
Trial Harbour Zone | 99982 | 10 | 23.6667 | 23.6667 | 23.6667 | 23.6667 | 23.6667 | 23.6667 | 23.6667 | 23.6667 | 23.6667 | 23.6667 | 23.6667 | 27.6667 | 28.7912 | 28.7912 | 28.7912 | 28.7912 | 28.7912 | 28.7912 | 28.7912 | 28.7912 | 28.7912 | 28.7912 | 28.7912 | 9.4419e-05 | 0.00015798 | 0.00027371 | 0.00050508 | 0.00084804 | 0.0013493 | 0.0020136 | 0.0037344 | 0.0051358 | 0.0065318 | -9.1318e-05 | -0.00010645 | -9.8186e-05 | -2.3535e-05 | 3.2727e-05 | 4.1484e-05 | 5.1548e-05 | 7.26e-05 | 9.0941e-05 | 0.00010845
Trial Harbour Zone | 99983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00018884 | 0.00031595 | 0.00054742 | 0.0010102 | 0.0016961 | 0.0026987 | 0.0040271 | 0.0074689 | 0.010272 | 0.013064 | -0.00018264 | -0.0002129 | -0.00019637 | -4.707e-05 | 6.5453e-05 | 8.2968e-05 | 0.0001031 | 0.0001452 | 0.00018188 | 0.00021689
Tungatinah | 49302 | 1.1689 | 11 | 11.0667 | 11.0667 | 11.0667 | 11.0667 | 11.0667 | 11.0667 | 11.0667 | 11.0667 | 11.0667 | 11.0667 | 11 | 11.0774 | 11.0774 | 11.0774 | 11.0774 | 11.0774 | 11.0774 | 11.0774 | 11.0774 | 11.0774 | 11.0774 | 11.0774 | 3.7539e-05 | 7.4867e-05 | 0.00012259 | 0.00018502 | 0.00025832 | 0.00034971 | 0.00046066 | 0.00072308 | 0.00094143 | 0.0011534 | -0.0003157 | -0.00038994 | -0.00046959 | -0.00054225 | -0.00060003 | -0.00064324 | -0.00067487 | -0.0006594 | -0.00066255 | -0.00065806
Tungatinah | 49303 | 13.0533 | 22 | 22.6651 | 22.6651 | 22.6651 | 22.6651 | 22.6651 | 22.6651 | 22.6651 | 22.6651 | 22.6651 | 22.6651 | 23 | 23.1627 | 23.1627 | 23.1627 | 23.1627 | 23.1627 | 23.1627 | 23.1627 | 23.1627 | 23.1627 | 23.1627 | 23.1627 | 0.010548 | 0.021038 | 0.034448 | 0.05199 | 0.072587 | 0.098269 | 0.12944 | 0.20319 | 0.26454 | 0.32412 | -0.088712 | -0.10957 | -0.13196 | -0.15237 | -0.16861 | -0.18075 | -0.18964 | -0.18529 | -0.18618 | -0.18491
Tungatinah | 49304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7539e-05 | 7.4867e-05 | 0.00012259 | 0.00018502 | 0.00025832 | 0.00034971 | 0.00046066 | 0.00072308 | 0.00094143 | 0.0011534 | -0.0003157 | -0.00038994 | -0.00046959 | -0.00054225 | -0.00060003 | -0.00064324 | -0.00067487 | -0.0006594 | -0.00066255 | -0.00065806
Tungatinah | 49307 | 2.3444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.000488 | 0.00097327 | 0.0015937 | 0.0024052 | 0.0033581 | 0.0045463 | 0.0059885 | 0.0094 | 0.012239 | 0.014995 | -0.0041041 | -0.0050692 | -0.0061047 | -0.0070493 | -0.0078004 | -0.0083621 | -0.0087733 | -0.0085722 | -0.0086132 | -0.0085548
Ulverstone | 82001 | 109.0799 | 106.3 | 106.7451 | 107.192 | 107.6408 | 108.0914 | 108.544 | 108.9985 | 109.4548 | 109.9131 | 110.3733 | 110.8354 | 68.1 | 68.3875 | 68.4772 | 68.5671 | 68.6571 | 68.7472 | 68.8374 | 68.9278 | 69.0182 | 69.1088 | 69.1995 | 69.2904 | 0.018071 | 0.03737 | 0.060201 | 0.085821 | 0.11211 | 0.14096 | 0.17293 | 0.24143 | 0.29934 | 0.35332 | -0.18642 | -0.23098 | -0.28008 | -0.32846 | -0.37161 | -0.41113 | -0.44887 | -0.49208 | -0.53554 | -0.5743
Ulverstone | 82002 | 155.1763 | 84.4 | 85.4201 | 85.7778 | 86.1369 | 86.4975 | 86.8597 | 87.2234 | 87.5885 | 87.9553 | 88.3235 | 88.6933 | 165.1 | 170.7264 | 170.9505 | 171.1748 | 171.3995 | 171.6244 | 171.8497 | 172.0752 | 172.3011 | 172.5272 | 172.7536 | 172.9804 | 0.090344 | 0.18231 | 0.29005 | 0.40932 | 0.5303 | 0.66174 | 0.80648 | 1.1119 | 1.3718 | 1.6137 | -0.94812 | -1.1594 | -1.3904 | -1.6159 | -1.815 | -1.9958 | -2.1668 | -2.3617 | -2.5554 | -2.7274
Ulverstone | 82003 | 108.0108 | 101.4 | 102.4817 | 102.9107 | 103.3416 | 103.7743 | 104.2088 | 104.6451 | 105.0832 | 105.5231 | 105.965 | 106.4086 | 177.8 | 180.9301 | 181.1676 | 181.4054 | 181.6434 | 181.8818 | 182.1206 | 182.3596 | 182.5989 | 182.8386 | 183.0785 | 183.3188 | 0.10638 | 0.20399 | 0.31817 | 0.44492 | 0.57404 | 0.71522 | 0.87151 | 1.2021 | 1.4821 | 1.7438 | -1.0031 | -1.2244 | -1.4646 | -1.6967 | -1.8992 | -2.0805 | -2.2493 | -2.4336 | -2.6183 | -2.7799
Ulverstone | 82004 | 68.5632 | 53.7 | 53.9248 | 54.1506 | 54.3773 | 54.605 | 54.8336 | 55.0632 | 55.2937 | 55.5252 | 55.7577 | 55.9912 | 51.3 | 53.8031 | 53.8737 | 53.9444 | 54.0152 | 54.0861 | 54.1571 | 54.2282 | 54.2993 | 54.3706 | 54.442 | 54.5134 | 0.034309 | 0.069294 | 0.11028 | 0.15564 | 0.20166 | 0.25165 | 0.30669 | 0.42283 | 0.52169 | 0.61367 | -0.36067 | -0.44107 | -0.52894 | -0.61476 | -0.69056 | -0.75939 | -0.82449 | -0.89877 | -0.97254 | -1.0381
Ulverstone | 82005 | 190.3283 | 87.1 | 87.836 | 88.2037 | 88.573 | 88.9438 | 89.3162 | 89.6902 | 90.0657 | 90.4428 | 90.8215 | 91.2017 | 162 | 164.9558 | 165.1723 | 165.3891 | 165.6061 | 165.8235 | 166.0411 | 166.259 | 166.4772 | 166.6957 | 166.9145 | 167.1336 | 0.075084 | 0.15165 | 0.24133 | 0.34061 | 0.44132 | 0.55072 | 0.67118 | 0.92533 | 1.1417 | 1.343 | -0.78931 | -0.96525 | -1.1576 | -1.3454 | -1.5113 | -1.6619 | -1.8044 | -1.9669 | -2.1283 | -2.2718
Ulverstone | 82006 | 173.1444 | 94.9 | 96.5115 | 96.9156 | 97.3214 | 97.7288 | 98.138 | 98.5489 | 98.9615 | 99.3758 | 99.7919 | 100.2097 | 107.5 | 107.6411 | 107.7824 | 107.9238 | 108.0655 | 108.2073 | 108.3493 | 108.4915 | 108.6339 | 108.7765 | 108.9193 | 109.0622 | 0.0086467 | 0.017464 | 0.027792 | 0.039226 | 0.050822 | 0.063422 | 0.077294 | 0.10656 | 0.13148 | 0.15466 | -0.090898 | -0.11116 | -0.13331 | -0.15493 | -0.17404 | -0.19138 | -0.20779 | -0.22651 | -0.2451 | -0.26163
Ulverstone | 82007 | 50.95 | 43 | 43.18 | 43.3608 | 43.5424 | 43.7247 | 43.9077 | 44.0916 | 44.2762 | 44.4615 | 44.6477 | 44.8346 | 23.5 | 24.0901 | 24.1218 | 24.1534 | 24.1851 | 24.2169 | 24.2486 | 24.2805 | 24.3123 | 24.3442 | 24.3762 | 24.4082 | 0.020454 | 0.04146 | 0.066105 | 0.093447 | 0.12123 | 0.15147 | 0.18479 | 0.25528 | 0.31522 | 0.37101 | -0.21441 | -0.26272 | -0.31559 | -0.36729 | -0.41304 | -0.45463 | -0.49404 | -0.53902 | -0.58378 | -0.62359
Ulverstone | 82008 | 98.6817 | 153 | 158.272 | 158.9347 | 159.6001 | 160.2683 | 160.9393 | 161.6131 | 162.2898 | 162.9693 | 163.6516 | 164.3367 | 168 | 172.8608 | 173.7736 | 174.0017 | 174.2301 | 174.4588 | 174.6877 | 174.917 | 175.1466 | 175.3764 | 175.6066 | 175.8371 | 0.075362 | 0.15221 | 0.24222 | 0.34187 | 0.44295 | 0.55276 | 0.67366 | 0.92876 | 1.1459 | 1.348 | -0.79223 | -0.96882 | -1.1618 | -1.3503 | -1.5168 | -1.668 | -1.811 | -1.9742 | -2.1362 | -2.2802
Waddamana | 49202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.4535 | 19.4535 | 19.4535 | 19.4535 | 19.4535 | 19.4535 | 19.4535 | 19.4535 | 19.4535 | 19.4535 | 19.4535 | 19.4535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wayatinah | 49411 | 26.8238 | 8 | 7.9901 | 7.9901 | 7.9901 | 7.9901 | 7.9901 | 7.9901 | 7.9901 | 7.9901 | 7.9901 | 7.9901 | 12 | 12.3661 | 12.3661 | 12.3661 | 12.3661 | 12.3661 | 12.3661 | 12.3661 | 12.3661 | 12.3661 | 12.3661 | 12.3661 | 0.0023649 | 0.0047166 | 0.0077232 | 0.011656 | 0.016274 | 0.022032 | 0.029021 | 0.045554 | 0.05931 | 0.072667 | -0.019889 | -0.024566 | -0.029584 | -0.034162 | -0.037802 | -0.040524 | -0.042517 | -0.041542 | -0.041741 | -0.041458
Wayatinah | 49412 | 25.1362 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 0.00097601 | 0.0019465 | 0.0031873 | 0.0048105 | 0.0067162 | 0.0090925 | 0.011977 | 0.0188 | 0.024477 | 0.029989 | -0.0082082 | -0.010138 | -0.012209 | -0.014099 | -0.015601 | -0.016724 | -0.017547 | -0.017144 | -0.017226 | -0.01711
Wesley Vale | 81001 | 32.2507 | 32 | 32.1937 | 32.3886 | 32.5847 | 32.782 | 32.9804 | 33.1801 | 33.3809 | 33.583 | 33.7863 | 33.9908 | 42 | 42.8395 | 43.0834 | 43.3288 | 43.5755 | 43.8236 | 44.0732 | 44.3241 | 44.5765 | 44.8304 | 45.0856 | 45.3424 | 0.016094 | 0.033468 | 0.054053 | 0.07721 | 0.10102 | 0.12721 | 0.15627 | 0.21868 | 0.27139 | 0.32054 | -0.16608 | -0.20619 | -0.25042 | -0.29405 | -0.33298 | -0.36867 | -0.40276 | -0.44172 | -0.48099 | -0.51601
Wesley Vale | 81002 | 52.6293 | 55.2 | 55.5342 | 55.8704 | 56.2086 | 56.5489 | 56.8912 | 57.2356 | 57.5821 | 57.9307 | 58.2814 | 58.6342 | 56 | 57.21 | 57.5358 | 57.8634 | 58.1929 | 58.5242 | 58.8575 | 59.1926 | 59.5297 | 59.8687 | 60.2096 | 60.5524 | 0.032284 | 0.067555 | 0.10886 | 0.15491 | 0.20205 | 0.25388 | 0.31152 | 0.43426 | 0.53799 | 0.63507 | -0.36735 | -0.44676 | -0.53271 | -0.61538 | -0.68711 | -0.75081 | -0.80964 | -0.87193 | -0.9347 | -0.98901
Wesley Vale | 81003 | 7.1013 | 99.6 | 100.203 | 100.8096 | 101.4198 | 102.0338 | 102.6515 | 103.2729 | 103.8981 | 104.5271 | 105.1599 | 105.7965 | 175.2 | 179.4088 | 180.4304 | 181.4578 | 182.4911 | 183.5303 | 184.5753 | 185.6264 | 186.6834 | 187.7464 | 188.8155 | 189.8906 | 0.097217 | 0.20343 | 0.32781 | 0.46647 | 0.6084 | 0.76447 | 0.93802 | 1.3076 | 1.6199 | 1.9123 | -1.1065 | -1.3456 | -1.6044 | -1.8533 | -2.0692 | -2.261 | -2.438 | -2.6255 | -2.8143 | -2.9777
West Hobart Zone | 13043 | 78.4611 | 38 | 38.2004 | 38.3439 | 38.4879 | 38.6325 | 38.7777 | 38.9234 | 39.0696 | 39.2164 | 39.3638 | 39.5116 | 88.3333 | 91.6365 | 92.0173 | 92.3996 | 92.7836 | 93.1692 | 93.5563 | 93.9451 | 94.3355 | 94.7275 | 95.1211 | 95.5164 | 0.012229 | 0.024807 | 0.039716 | 0.056722 | 0.07446 | 0.094601 | 0.11739 | 0.1675 | 0.20894 | 0.24734 | -0.10947 | -0.1376 | -0.16824 | -0.19802 | -0.22414 | -0.24763 | -0.26967 | -0.29385 | -0.3177 | -0.33764
West Hobart Zone | 13044 | 126.1222 | 118.3333 | 118.7779 | 119.2242 | 119.6721 | 120.1218 | 120.5731 | 121.0261 | 121.4808 | 121.9372 | 122.3953 | 122.8552 | 179.3333 | 188.515 | 189.2983 | 190.0849 | 190.8748 | 191.668 | 192.4644 | 193.2642 | 194.0673 | 194.8737 | 195.6835 | 196.4967 | 0.0092304 | 0.018118 | 0.028814 | 0.041331 | 0.054686 | 0.070192 | 0.087943 | 0.12773 | 0.16037 | 0.19071 | -0.095016 | -0.11474 | -0.13631 | -0.15731 | -0.17573 | -0.19221 | -0.20758 | -0.22338 | -0.2392 | -0.25231
West Hobart Zone | 13045 | 142.0444 | 159 | 160.9404 | 161.5451 | 162.1521 | 162.7613 | 163.3728 | 163.9866 | 164.6027 | 165.2212 | 165.8419 | 166.465 | 245 | 248.2074 | 249.2388 | 250.2745 | 251.3144 | 252.3588 | 253.4074 | 254.4604 | 255.5178 | 256.5796 | 257.6458 | 258.7164 | 0.040597 | 0.082379 | 0.13204 | 0.18897 | 0.24862 | 0.31669 | 0.39391 | 0.56443 | 0.70515 | 0.83558 | -0.37959 | -0.47282 | -0.57433 | -0.67296 | -0.75938 | -0.83697 | -0.90958 | -0.98793 | -1.0656 | -1.1303
West Hobart Zone | 13046 | 60.3778 | 55.3333 | 55.5412 | 55.7499 | 55.9594 | 56.1696 | 56.3806 | 56.5925 | 56.8051 | 57.0185 | 57.2327 | 57.4478 | 69.6667 | 71.9391 | 72.238 | 72.5382 | 72.8396 | 73.1423 | 73.4463 | 73.7515 | 74.0579 | 74.3657 | 74.6747 | 74.985 | 0.00020925 | 0.00041074 | 0.00065322 | 0.00093698 | 0.0012397 | 0.0015913 | 0.0019937 | 0.0028956 | 0.0036355 | 0.0043233 | -0.002154 | -0.0026012 | -0.0030902 | -0.0035663 | -0.0039838 | -0.0043574 | -0.0047059 | -0.005064 | -0.0054226 | -0.0057199
West Hobart Zone | 13047 | 44.6611 | 48 | 48.1803 | 48.3614 | 48.5431 | 48.7254 | 48.9085 | 49.0923 | 49.2767 | 49.4618 | 49.6477 | 49.8342 | 89.6667 | 94.0042 | 94.3948 | 94.7871 | 95.181 | 95.5765 | 95.9736 | 96.3725 | 96.7729 | 97.1751 | 97.5789 | 97.9843 | 0.0041646 | 0.0084724 | 0.013588 | 0.019443 | 0.02557 | 0.032552 | 0.040466 | 0.057922 | 0.072335 | 0.085691 | -0.038631 | -0.048247 | -0.058714 | -0.068882 | -0.077791 | -0.085791 | -0.09328 | -0.10139 | -0.10942 | -0.11611
West Hobart Zone | 13048 | 98.3944 | 87.3333 | 87.6615 | 87.9908 | 88.3214 | 88.6532 | 88.9863 | 89.3206 | 89.6562 | 89.9931 | 90.3312 | 90.6706 | 140.3333 | 143.9514 | 144.5496 | 145.1502 | 145.7534 | 146.3591 | 146.9672 | 147.5779 | 148.1912 | 148.807 | 149.4253 | 150.0463 | 0.0091374 | 0.017936 | 0.028524 | 0.040915 | 0.054135 | 0.069485 | 0.087057 | 0.12644 | 0.15875 | 0.18878 | -0.094059 | -0.11359 | -0.13494 | -0.15573 | -0.17396 | -0.19027 | -0.20549 | -0.22113 | -0.23679 | -0.24977
West Hobart Zone | 13049 | 100.95 | 77.6667 | 78.8052 | 79.1013 | 79.3984 | 79.6968 | 79.9962 | 80.2967 | 80.5984 | 80.9012 | 81.2052 | 81.5103 | 169.6667 | 176.0193 | 176.7507 | 177.4852 | 178.2227 | 178.9633 | 179.707 | 180.4537 | 181.2036 | 181.9565 | 182.7127 | 183.4719 | 0.023367 | 0.045866 | 0.072943 | 0.10463 | 0.13844 | 0.17769 | 0.22263 | 0.32335 | 0.40597 | 0.48277 | -0.24053 | -0.29047 | -0.34507 | -0.39824 | -0.44485 | -0.48658 | -0.52549 | -0.56548 | -0.60552 | -0.63872
West Hobart Zone | 13050 | 48.4556 | 43.3333 | 43.4961 | 43.6596 | 43.8236 | 43.9882 | 44.1535 | 44.3194 | 44.4859 | 44.6531 | 44.8208 | 44.9892 | 81 | 83.5874 | 83.9348 | 84.2835 | 84.6338 | 84.9855 | 85.3386 | 85.6932 | 86.0493 | 86.4069 | 86.7659 | 87.1265 | 0.010047 | 0.018988 | 0.029675 | 0.041988 | 0.054938 | 0.069735 | 0.086552 | 0.12365 | 0.15438 | 0.18294 | -0.084725 | -0.10488 | -0.12698 | -0.14865 | -0.16782 | -0.1852 | -0.20164 | -0.21964 | -0.23767 | -0.25293
West Hobart Zone | 13052 | 124.5444 | 141 | 141.5298 | 142.0615 | 142.5952 | 143.131 | 143.6687 | 144.2085 | 144.7503 | 145.2942 | 145.8401 | 146.388 | 240.3333 | 249.168 | 250.2033 | 251.243 | 252.2871 | 253.3354 | 254.3881 | 255.4452 | 256.5067 | 257.5726 | 258.6429 | 259.7177 | 0.021263 | 0.043392 | 0.069574 | 0.099349 | 0.13032 | 0.1654 | 0.20503 | 0.29195 | 0.36391 | 0.43054 | -0.18755 | -0.23708 | -0.29097 | -0.34334 | -0.38926 | -0.43058 | -0.46935 | -0.51218 | -0.5543 | -0.58956
West Hobart Zone | 13053 | 98.3944 | 79.3333 | 79.6684 | 79.9677 | 80.2681 | 80.5697 | 80.8724 | 81.1763 | 81.4813 | 81.7874 | 82.0947 | 82.4031 | 144.6667 | 151.5842 | 152.2141 | 152.8467 | 153.4818 | 154.1196 | 154.76 | 155.4031 | 156.0489 | 156.6973 | 157.3485 | 158.0023 | 0.022628 | 0.046619 | 0.074981 | 0.1072 | 0.1407 | 0.1786 | 0.22142 | 0.31529 | 0.39299 | 0.46491 | -0.20157 | -0.25523 | -0.31354 | -0.37015 | -0.41974 | -0.46431 | -0.50609 | -0.55221 | -0.59751 | -0.63535
West Hobart Zone | 13054 | 100.95 | 84.3333 | 84.6502 | 84.9682 | 85.2875 | 85.6079 | 85.9295 | 86.2524 | 86.5764 | 86.9017 | 87.2282 | 87.5559 | 111.3333 | 112.7022 | 113.1705 | 113.6407 | 114.113 | 114.5872 | 115.0633 | 115.5414 | 116.0216 | 116.5037 | 116.9878 | 117.4739 | 0.0052897 | 0.010594 | 0.016929 | 0.024249 | 0.031974 | 0.040851 | 0.050956 | 0.073407 | 0.091889 | 0.10904 | -0.051448 | -0.063259 | -0.076141 | -0.088668 | -0.099647 | -0.10949 | -0.11869 | -0.12843 | -0.13814 | -0.1462
West Hobart Zone | 13055 | 48.4556 | 107.6667 | 110.075 | 110.4886 | 110.9037 | 111.3204 | 111.7386 | 112.1584 | 112.5798 | 113.0028 | 113.4274 | 113.8535 | 195 | 206.7556 | 207.6147 | 208.4774 | 209.3437 | 210.2137 | 211.0872 | 211.9643 | 212.8451 | 213.7296 | 214.6177 | 215.5096 | 0.028011 | 0.057751 | 0.0929 | 0.13281 | 0.17428 | 0.22119 | 0.27417 | 0.39028 | 0.48639 | 0.57535 | -0.2488 | -0.31532 | -0.38761 | -0.45779 | -0.51926 | -0.57452 | -0.62632 | -0.68358 | -0.73978 | -0.78675
West Hobart Zone | 13056 | 124.5444 | 43.6667 | 43.9845 | 44.1498 | 44.3157 | 44.4822 | 44.6493 | 44.817 | 44.9854 | 45.1544 | 45.3241 | 45.4944 | 92 | 95.3489 | 95.7451 | 96.143 | 96.5425 | 96.9437 | 97.3465 | 97.751 | 98.1572 | 98.5651 | 98.9747 | 99.386 | 0.020135 | 0.038564 | 0.06055 | 0.085823 | 0.11235 | 0.14262 | 0.17699 | 0.25273 | 0.31546 | 0.37371 | -0.17132 | -0.2128 | -0.25822 | -0.30268 | -0.34195 | -0.37749 | -0.41106 | -0.44787 | -0.4846 | -0.51564
West Hobart Zone | 13057 | 179.9611 | 94.6667 | 97.9579 | 98.326 | 98.6954 | 99.0662 | 99.4384 | 99.812 | 100.187 | 100.5634 | 100.9412 | 101.3205 | 172 | 176.1402 | 176.8721 | 177.6071 | 178.3451 | 179.0862 | 179.8304 | 180.5777 | 181.328 | 182.0815 | 182.8382 | 183.5979 | 0.04845 | 0.097909 | 0.15544 | 0.21899 | 0.28344 | 0.35374 | 0.43159 | 0.59931 | 0.73985 | 0.87064 | -0.47562 | -0.58667 | -0.70666 | -0.82263 | -0.92388 | -1.0149 | -1.1003 | -1.197 | -1.2928 | -1.3757
West Hobart Zone | 13058 | 62.2222 | 65 | 65.2442 | 65.4893 | 65.7354 | 65.9824 | 66.2303 | 66.4791 | 66.7289 | 66.9796 | 67.2312 | 67.4838 | 89.6667 | 91.2806 | 91.6599 | 92.0408 | 92.4233 | 92.8074 | 93.193 | 93.5803 | 93.9691 | 94.3596 | 94.7517 | 95.1454 | 0.00062776 | 0.0012322 | 0.0019597 | 0.0028109 | 0.0037192 | 0.0047738 | 0.005981 | 0.0086869 | 0.010907 | 0.01297 | -0.0064621 | -0.0078036 | -0.0092706 | -0.010699 | -0.011951 | -0.013072 | -0.014118 | -0.015192 | -0.016268 | -0.01716

## ForecastData (hidden)
Ref. Embedded Generation NMIs 230621.xlsx in 2021 APR Chapter 4 folder, http://collaborationzone.tnad.tasnetworks.com.au/business-functions/network-planning/APR15/Annual%20Planning%20Report%20Creation/Chapter%204%20-%20Area%20planning
|  |  | Summer (MVA) | [13 empty] | Winter (MVA) | [14 empty] | Embedded generation
|  | Non-peaking season | 2021 (Actual) | 2022 (Actuals) | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | PF | Regional DF | 2021 (Actuals) | 2022 (Actuals) | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | PF | Regional DF |  | less than 100 kVA | Over 100 kVA
AL | Arthurs Lake (DL) | Summer | 0.37223 | 0.52501 | 0.51701 | 0.50991 | 0.50418 | 0.50611 | 0.51376 | 0.51934 | 0.5259 | 0.53195 | 0.53762 | 0.5434 | 0.99922 | 0.80435 | 0.020643 | 0.022543 | 0.022667 | 0.022247 | 0.022039 | 0.022008 | 0.022309 | 0.022516 | 0.022751 | 0.022888 | 0.023313 | 0.023519 | 0.99922 | 0.5974 | TR | 20.6073 | 2
AV | Avoca | Summer | 10.3262 | 13.2985 | 13.3437 | 13.1804 | 13.0778 | 13.1427 | 13.4131 | 13.6283 | 13.9001 | 14.1524 | 14.4064 | 14.7176 | 0.98539 | 0.43165 | 7.3639 | 8.2335 | 8.4584 | 8.359 | 8.3461 | 8.3759 | 8.5672 | 8.7244 | 8.9231 | 9.0819 | 9.3631 | 9.5878 | 0.98539 | 0.73008 | GT | 7.5015 | 0.30292
BEZ | Zs-Bellerive | Summer | 9.6417 | 7.558 | 7.3066 | 7.1006 | 6.9294 | 6.8764 | 6.9203 | 6.963 | 7.036 | 7.1379 | 7.2637 | 7.3924 |  |  | 10.4442 | 10.3203 | 10.4279 | 10.2694 | 10.1792 | 10.1931 | 10.3633 | 10.5157 | 10.7032 | 10.8832 | 11.2093 | 11.4546
BU | Burnie | Summer | 44.3842 | 41.8144 | 40.8413 | 40.1811 | 39.6538 | 39.9128 | 40.479 | 40.9682 | 41.6218 | 42.3717 | 43.2467 | 44.1577 | 0.99868 | 0.93437 | 57.5142 | 58.1268 | 57.902 | 56.7461 | 56.15 | 56.2288 | 56.965 | 57.5576 | 58.4054 | 59.1245 | 60.7562 | 61.8463 | 0.99863 | 0.92899 | TU | 0.0657 | 0
BW | Bridgewater | Summer | 21.0321 | 19.096 | 18.489 | 18.9051 | 18.9796 | 19.0765 | 19.3234 | 19.506 | 19.7753 | 20.1706 | 20.6411 | 21.1634 | 0.9999 | 0.86038 | 36.4906 | 34.895 | 35.1625 | 35.497 | 35.7037 | 35.9336 | 36.6117 | 37.1373 | 37.7814 | 38.3962 | 39.5356 | 40.3752 | 0.99946 | 0.93665 | DP | 11.2123 | 0.95333
CAZ | Cambridge-Total | Summer | 11.5972 | 12.5347 | 12.2623 | 11.9919 | 11.7976 | 11.8209 | 11.9891 | 12.1207 | 12.2792 | 12.4435 | 12.5918 | 12.7962 |  |  | 17.4502 | 16.9885 | 17.0118 | 16.6128 | 16.4143 | 16.3909 | 16.6224 | 16.7917 | 16.9888 | 17.1201 | 17.4447 | 17.6761 |  |  | WA | 0 | 0
CLZ | Zs-Claremont | Summer | 14.3675 | 12.6915 | 12.3336 | 11.9896 | 11.7432 | 11.7204 | 11.8959 | 12.0854 | 12.345 | 12.7175 | 13.1502 | 13.5975 |  |  | 22.3649 | 22.118 | 22.3641 | 21.9673 | 21.8083 | 21.8308 | 22.2188 | 22.5457 | 22.9666 | 23.3675 | 24.0959 | 24.6231
CR | Creek Road | Summer | 56.3751 | 51.9611 | 51.0448 | 50.7017 | 50.1533 | 50.279 | 51.0143 | 51.7271 | 52.6457 | 53.87 | 55.2141 | 56.6653 | 0.99836 | 0.8873 | 87.5113 | 89.0875 | 89.9332 | 89.0702 | 88.6317 | 88.8768 | 90.5321 | 92.0611 | 94.0411 | 96.0477 | 99.3545 | 101.9634 | 0.98957 | 0.9452 | AL | 0.36324 | 1.6
CS | Chapel Street | Summer | 21.6881 | 20.2013 | 19.8779 | 19.4818 | 19.3476 | 19.5381 | 20.01 | 20.505 | 21.1028 | 21.9167 | 22.8124 | 23.7825 | 1 | 0.92902 | 39.343 | 38.759 | 39.268 | 38.7192 | 38.6818 | 38.9351 | 39.8349 | 40.6535 | 41.6554 | 42.6403 | 44.1976 | 45.4115 | 0.99976 | 0.90185
DB | Derwent Bridge | Summer | 0.31856 | 0.28717 | 0.28375 | 0.28011 | 0.27733 | 0.27854 | 0.28337 | 0.28712 | 0.29168 | 0.29607 | 0.30049 | 0.30542 | 0.98995 | 0.76923 | 0.31143 | 0.33494 | 0.34036 | 0.33598 | 0.33456 | 0.33559 | 0.34211 | 0.3472 | 0.35297 | 0.35737 | 0.36635 | 0.37262 | 0.99451 | 0.71875 | DB | 0 | 0
DE | Derby | Winter | 7.9449 | 7.8275 | 7.6469 | 7.4737 | 7.3389 | 7.4145 | 7.4909 | 7.542 | 7.6274 | 7.7051 | 7.7963 | 7.908 | 0.99802 | 0.71111 | 6.0029 | 7.0036 | 6.9744 | 6.8194 | 6.7424 | 6.7791 | 6.8636 | 6.9236 | 7.0138 | 7.0676 | 7.2318 | 7.3299 | 1 | 0.32805 | KR | 6.9122 | 0.1992
DP | Devonport | Summer | 39.4649 | 36.0101 | 35.9928 | 36.1406 | 35.8579 | 35.8464 | 36.1993 | 36.4508 | 36.8187 | 37.1803 | 37.6438 | 38.0799 | 0.99161 | 0.86328 | 56.3522 | 52.515 | 53.6751 | 53.666 | 53.5888 | 53.6442 | 54.4392 | 55.0365 | 55.7631 | 56.2256 | 57.5066 | 58.2075 | 0.9978 | 0.95374 | HR | 0.01525 | 0
DPZ | Zs-Derwent Park | Summer | 14.472 | 12.9504 | 12.751 | 12.5131 | 12.3045 | 12.3101 | 12.4769 | 12.6229 | 12.8048 | 13.0048 | 13.2059 | 13.4335 |  |  | 19.6301 | 19.1852 | 19.4164 | 19.058 | 18.852 | 18.8312 | 19.1122 | 19.3447 | 19.6213 | 19.8379 | 20.2967 | 20.6115
EB | Emu Bay (RT) | Summer | 7.7309 | 7.8282 | 7.678 | 7.709 | 7.6779 | 7.6603 | 7.7312 | 7.7719 | 7.8427 | 7.8681 | 7.9185 | 7.9017 | 0.95637 | 0.76111 | 9.4861 | 9.0691 | 9.0724 | 9.06 | 9.0473 | 8.9932 | 9.0792 | 9.1274 | 9.2052 | 9.1975 | 9.3391 | 9.3116 | 0.9601 | 0.8838 | UL | 10.809 | 8.805
EHZ | Zs-East Hobart | Summer | 23.8871 | 23.8662 | 23.4563 | 25.8637 | 27.0012 | 27.5933 | 28.1669 | 28.5239 | 28.9528 | 29.2924 | 29.6187 | 29.9456 |  |  | 28.5788 | 29.2574 | 29.6632 | 31.8147 | 32.94 | 33.4795 | 34.1831 | 34.6615 | 35.1923 | 35.5262 | 36.2663 | 36.7728
EL | Electrona | Summer | 9.8412 | 10.0694 | 9.7878 | 9.679 | 9.5433 | 9.5355 | 9.645 | 9.7441 | 9.8831 | 10.0839 | 10.3227 | 10.5671 | 0.99855 | 0.78257 | 16.1153 | 16.2935 | 16.2331 | 15.9397 | 15.7373 | 15.6491 | 15.8016 | 15.9185 | 16.1023 | 16.2988 | 16.7348 | 17.0325 | 0.99827 | 0.88141 | NT | 0 | 0
GBZ | Zs-Geilston Bay | Summer | 11.0712 | 10.354 | 9.9818 | 9.6686 | 9.4018 | 9.3182 | 9.362 | 9.411 | 9.5001 | 9.6705 | 9.885 | 10.1046 |  |  | 19.1596 | 19.0827 | 19.1263 | 18.7793 | 18.5522 | 18.4896 | 18.6986 | 18.863 | 19.0743 | 19.2745 | 19.751 | 20.0212
GRZ | Zs-Gretna | Winter | 1.0285 | 1.9864 | 1.9416 | 1.918 | 1.9007 | 1.9054 | 1.9353 | 1.9578 | 1.9863 | 2.0091 | 2.0342 | 2.0542 |  |  | 0.032832 | 0.31302 | 0.31721 | 0.31313 | 0.31199 | 0.31317 | 0.31973 | 0.32525 | 0.33194 | 0.33786 | 0.34866 | 0.35711
GT | George Town | Summer | 13.5516 | 12.9473 | 13.5827 | 16.3103 | 17.5396 | 18.3206 | 18.6793 | 18.859 | 19.1004 | 19.3219 | 19.5741 | 19.8116 | 0.99078 | 0.91086 | 20.701 | 19.5416 | 20.2239 | 22.5526 | 23.5964 | 24.2622 | 24.5581 | 24.6602 | 24.8518 | 24.9389 | 25.4046 | 25.6188 | 0.99989 | 0.77669 | NW | 7.5109 | 0.58708
HA | Hadspen | Summer | 38.3217 | 40.4237 | 39.6969 | 37.8152 | 37.6279 | 37.599 | 37.8427 | 37.9462 | 38.1938 | 38.5556 | 39.0114 | 39.5861 | 1 | 0.93747 | 55.8628 | 54.9768 | 55.75 | 53.8261 | 54.2863 | 54.6654 | 55.6507 | 56.3492 | 57.1776 | 57.7639 | 59.1172 | 59.979 | 0.99997 | 0.93765 | PM | 1.026 | 0
HOZ | Zs-Howrah | Summer | 11.3546 | 12.0396 | 11.5871 | 11.2266 | 10.9494 | 10.8814 | 10.9733 | 11.0704 | 11.2184 | 11.4326 | 11.6903 | 11.9613 |  |  | 21.6344 | 21.2816 | 21.5126 | 21.2046 | 21.057 | 21.1297 | 21.5141 | 21.8508 | 22.2417 | 22.604 | 23.2603 | 23.7391
HR | Huon River | Winter | 1.7871 | 0.55446 | 0.53171 | 0.5234 | 0.51743 | 0.51561 | 0.52083 | 0.52409 | 0.52919 | 0.53096 | 0.53416 | 0.53275 |  | 0.83333 | 0.81762 | 0.92276 | 0.9037 | 0.88566 | 0.87757 | 0.87019 | 0.87801 | 0.88234 | 0.88926 | 0.8876 | 0.90014 | 0.89621 |  | 0.81818 | NH | 5.5279 | 0
KE | Kermandie | Summer | 6.3951 | 6.2488 | 6.1025 | 5.9686 | 5.8676 | 5.8449 | 5.9088 | 5.9508 | 6.0149 | 6.077 | 6.1516 | 6.2323 | 0.99336 | 0.86854 | 8.4451 | 8.6874 | 8.7826 | 8.6219 | 8.5544 | 8.5429 | 8.6822 | 8.7829 | 8.911 | 9.0092 | 9.2319 | 9.3955 | 0.99325 | 0.91347 | MY | 6.4748 | 2.2
KI11 | Kingston 11kV | Summer | 15.4883 | 16.2318 | 15.7276 | 15.2113 | 14.7267 | 14.5198 | 14.5161 | 14.5192 | 14.588 | 14.7564 | 14.981 | 15.2218 | 0.99986 | 0.7452 | 27.7733 | 27.5402 | 27.7016 | 27.1939 | 26.8776 | 26.8273 | 27.2102 | 27.5601 | 28.0309 | 28.52 | 29.4314 | 30.1039 | 1 | 0.9059 | BU | 13.9754 | 4.1353
KI33 | Kingston 33kV | Summer | 5.9545 | 5.6704 | 5.6147 | 5.7403 | 5.8116 | 5.9635 | 6.19 | 6.434 | 6.7158 | 7.0977 | 7.524 | 7.9881 | 0.99991 | 0.85913 | 11.1944 | 11.1262 | 11.242 | 11.2802 | 11.3657 | 11.5549 | 11.9422 | 12.3427 | 12.8532 | 13.4427 | 14.2447 | 14.9736 | 0.99555 | 0.94338 | CS | 7.4504 | 1.69
KR | Knights Road | Summer | 15.7919 | 15.0454 | 14.4547 | 14.4482 | 14.4122 | 14.4818 | 14.7009 | 14.841 | 15.0221 | 15.1817 | 15.3444 | 15.5351 | 0.9869 | 0.90798 | 19.2064 | 20.0543 | 19.7929 | 19.472 | 19.3043 | 19.2216 | 19.425 | 19.524 | 19.6715 | 19.7543 | 20.0832 | 20.3273 | 0.99261 | 0.96199 | NN | 4.4486 | 0.56
LF | Lindisfarne | Summer | 22.4525 | 20.1035 | 19.5646 | 18.984 | 18.5013 | 18.3947 | 18.5224 | 18.6338 | 18.8042 | 19.0804 | 19.3822 | 19.7586 | 0.9999 | 0.81658 | 36.5452 | 35.7593 | 36.0053 | 35.3337 | 34.9522 | 34.9271 | 35.4186 | 35.8099 | 36.2759 | 36.6808 | 37.5481 | 38.14 | 0.99913 | 0.92622
MB | Meadowbank | Winter | 7.7135 | 8.3046 | 8.1507 | 8.0559 | 7.9858 | 8.0197 | 8.1568 | 8.2646 | 8.3974 | 8.5172 | 8.6459 | 8.7678 | 0.99203 | 0.71486 | 4.6448 | 4.6221 | 4.6198 | 4.5333 | 4.494 | 4.4849 | 4.5541 | 4.6091 | 4.6811 | 4.7376 | 4.8655 | 4.9479 | 0.99999 | 0.69937 | EL | 8.7161 | 0.1298
MT | Mornington | Summer | 22.9744 | 22.6309 | 21.8563 | 21.1222 | 20.5324 | 20.3735 | 20.4973 | 20.6313 | 20.8511 | 21.2223 | 21.6557 | 22.1616 | 0.99878 | 0.82309 | 38.1091 | 38.7639 | 38.9706 | 38.2617 | 37.8579 | 37.8616 | 38.4444 | 38.9525 | 39.5777 | 40.1773 | 41.3154 | 42.1482 | 0.99762 | 0.94757
MY | Mowbray | Summer | 23.1322 | 22.4062 | 21.9251 | 21.8649 | 21.5785 | 21.4923 | 21.6206 | 21.6962 | 21.838 | 21.9937 | 22.1786 | 22.3617 | 0.99792 | 0.73585 | 39.6803 | 38.721 | 38.7052 | 38.3203 | 38.0022 | 37.8392 | 38.2111 | 38.4689 | 38.8195 | 39.0224 | 39.7663 | 40.1188 | 0.99874 | 0.93917 | PL | 2.3477 | 0.45
NH | North Hobart | Summer | 19.8857 | 19.9398 | 19.8138 | 19.8027 | 19.7113 | 19.9225 | 20.3542 | 20.7669 | 21.2348 | 21.7547 | 22.262 | 22.8658 | 0.99976 | 0.82122 | 37.0368 | 35.6257 | 36.1383 | 35.8848 | 35.8487 | 36.1706 | 37.0646 | 37.923 | 38.9446 | 39.9142 | 41.3574 | 42.5949 | 0.99887 | 0.94864 | AV | 1.2114 | 5
NN | New Norfolk | Winter | 17.7032 | 14.95 | 12.3411 | 12.7529 | 12.8706 | 12.9608 | 13.18 | 13.366 | 13.603 | 13.7756 | 13.9929 | 14.1289 | 0.98984 | 0.89365 | 18.04 | 20.854 | 19.4809 | 19.5114 | 19.6647 | 19.6593 | 19.9361 | 20.155 | 20.457 | 20.599 | 21.0808 | 21.2289 | 0.99505 | 0.85865 | EB | 0.70338 | 0
NT | Newton (Henty Goldmine) | Summer | 4.2094 | 4.0472 | 4.0044 | 3.9579 | 3.9301 | 3.9368 | 3.9962 | 4.0354 | 4.0888 | 4.1305 | 4.1778 | 4.2247 | 0.99637 | 0.89037 | 3.7798 | 3.8815 | 3.9247 | 3.8608 | 3.8416 | 3.8285 | 3.8812 | 3.9133 | 3.9569 | 3.9762 | 4.0537 | 4.0929 | 0.9964 | 0.875 | RK | 7.1907 | 0
NTZ | Zs-New Town | Summer | 13.7969 | 17.1169 | 17.0384 | 17.0891 | 17.691 | 18.1609 | 18.5833 | 18.8829 | 19.2011 | 19.5502 | 19.9064 | 20.2937 |  |  | 22.3948 | 22.067 | 22.5275 | 22.4988 | 23.1802 | 23.6793 | 24.2949 | 24.7818 | 25.3366 | 25.8535 | 26.6954 | 27.3562
NW | Norwood | Summer | 16.3714 | 16.7155 | 16.1 | 15.7161 | 15.3734 | 15.2735 | 15.3807 | 15.4712 | 15.6219 | 15.8118 | 16.0447 | 16.2834 | 0.99989 | 0.87602 | 29.5689 | 29.396 | 29.2112 | 28.6691 | 28.3761 | 28.2697 | 28.6037 | 28.8504 | 29.1696 | 29.3664 | 29.9722 | 30.2636 | 0.99971 | 0.90014 | QT | 0.88118 | 0
PL | Port Latta (RT) | Winter | 22.0321 | 22.6255 | 23.2909 | 23.1324 | 23.0263 | 23.011 | 23.1473 | 23.2525 | 23.406 | 23.5057 | 26.1236 | 26.1849 |  | 0.6205 | 20.7189 | 21.4055 | 22.3483 | 22.1556 | 22.0766 | 22.0139 | 22.1241 | 22.2087 | 22.3388 | 22.3994 | 25.1789 | 25.2418 |  | 0.86096 | MB | 0.91829 | 0.2
PM | Palmerston | Winter | 11.5081 | 15.0674 | 15.9442 | 16.2273 | 16.2842 | 16.4179 | 16.7443 | 16.9963 | 17.3093 | 17.5643 | 17.8161 | 18.0998 | 0.95333 | 0.69309 | 6.0975 | 7.1856 | 8.1779 | 8.492 | 8.5979 | 8.6247 | 8.7679 | 8.8755 | 9.018 | 9.1023 | 9.3151 | 9.44 | 0.98298 | 0.56731 | GO | 0 | 0
QT | Queenstown | Summer | 5.1861 | 3.7277 | 3.6754 | 3.605 | 3.5666 | 3.5616 | 3.6063 | 3.6349 | 3.6832 | 3.7358 | 3.8046 | 3.8923 | 0.94921 | 0.84143 | 5.7855 | 6.1594 | 6.2504 | 6.1516 | 6.1243 | 6.1075 | 6.1968 | 6.2572 | 6.3434 | 6.4025 | 6.5627 | 6.6739 | 0.99961 | 0.88151 | RB22 | 0 | 0
RA | Railton | Summer | 47.0341 | 50.3439 | 49.5961 | 48.7 | 48.0307 | 49.6116 | 51.0189 | 52.2134 | 52.7354 | 52.2858 | 52.7854 | 51.9716 | 0.99614 | 0.76883 | 47.3585 | 49.2087 | 49.2097 | 48.0484 | 47.4464 | 48.4428 | 49.5747 | 50.4923 | 50.8584 | 50.2149 | 51.0435 | 50.212 | 0.99394 | 0.95984 | KE | 3.2869 | 0
RB22 | Rosebery 22kV | Winter | 1.9221 | 2.2636 | 2.4016 | 2.3532 | 2.3257 | 2.3194 | 2.344 | 2.3602 | 2.3895 | 2.4241 | 2.4705 | 2.5297 | 0.99891 | 0.64286 | 0.77159 | 5.6267 | 5.7453 | 5.6459 | 5.6116 | 5.587 | 5.6597 | 5.7084 | 5.7817 | 5.8284 | 5.9683 | 6.0552 | 0.99834 |  | SR | 0.19812 | 0
RB44 | Rosebery 44kV | Summer | 40.0117 | 42.0001 | 40.1039 | 39.5664 | 39.2252 | 39.1698 | 39.3604 | 39.494 | 39.6985 | 39.7745 | 40.6762 | 40.6294 |  | 0.88287 | 42.7625 | 42.8784 | 41.3864 | 40.7444 | 40.4416 | 40.2791 | 40.4455 | 40.549 | 40.7129 | 40.6756 | 41.7647 | 41.6739 |  | 0.86062 | RB44 | 0.57149 | 0
RI | Risdon 33kV | Summer | 44.4865 | 45.7255 | 45.3484 | 47.5347 | 49.0766 | 50.1338 | 51.2035 | 51.95 | 52.7972 | 53.6439 | 54.4696 | 55.4058 | 0.99614 | 0.79104 | 70.5844 | 67.9417 | 69.0181 | 70.7898 | 72.3912 | 73.3803 | 74.8971 | 76.0066 | 77.2545 | 78.1984 | 80.0729 | 81.4051 | 0.97749 | 0.90684 | BW | 10.2075 | 0.32
RIZ | Zs-Richmond | Winter | 3.2633 | 2.3693 | 2.234 | 2.1185 | 2.0288 | 1.9743 | 1.9521 | 1.9283 | 1.9158 | 1.912 | 1.9179 | 1.9272 |  |  | 2.957 | 3.8639 | 3.8858 | 3.8119 | 3.7767 | 3.7757 | 3.8355 | 3.8823 | 3.9407 | 3.9928 | 4.0991 | 4.1762
RK | Rokeby | Summer | 14.3626 | 13.4039 | 12.6989 | 12.123 | 11.6872 | 11.5105 | 11.5141 | 11.5284 | 11.6013 | 11.7894 | 12.0346 | 12.3035 | 0.99998 | 0.81879 | 21.6782 | 22.8645 | 23.0691 | 22.744 | 22.6181 | 22.753 | 23.2288 | 23.6482 | 24.1313 | 24.6359 | 25.4703 | 26.1 | 0.99941 | 0.8624 | CR | 15.6436 | 1.065
RPZ | Zs-Rosny Park | Summer | 8.4629 | 9.8715 | 9.5571 | 9.29 | 9.067 | 9.0111 | 9.0741 | 9.1337 | 9.2278 | 9.3684 | 9.5351 | 9.7121 |  |  | 15.8764 | 15.1503 | 15.2175 | 14.9433 | 14.778 | 14.7572 | 14.9595 | 15.1315 | 15.3475 | 15.5485 | 15.963 | 16.2412
SBZ | Zs-Sandy Bay | Summer | 20.8534 | 18.7989 | 18.2036 | 17.9705 | 17.6707 | 17.6398 | 17.8429 | 18.0825 | 18.416 | 18.947 | 19.5684 | 20.2212 |  |  | 37.5846 | 39.248 | 39.2574 | 38.7716 | 38.4295 | 38.3492 | 38.8584 | 39.3168 | 39.9507 | 40.5843 | 41.8064 | 42.6291
SD | Scottsdale | Summer | 12.717 | 12.5948 | 12.2591 | 11.9601 | 11.7217 | 11.8224 | 11.9304 | 12.0076 | 12.1465 | 12.2877 | 12.464 | 12.6745 | 0.98231 | 0.76872 | 11.889 | 11.7572 | 11.714 | 11.4179 | 11.255 | 11.339 | 11.4754 | 11.5805 | 11.7524 | 11.8908 | 12.2264 | 12.4833 | 1 | 1 | LF | 5.6014 | 0
SL | St Leonards | Summer | 19.1789 | 36.3243 | 34.8125 | 34.0968 | 33.5185 | 33.3122 | 33.5555 | 33.7078 | 33.9819 | 34.1479 | 34.4003 | 34.4663 | 0.99983 | 0.65982 | 23.7605 | 31.1972 | 30.9234 | 30.2811 | 29.9252 | 29.7612 | 30.0508 | 30.2528 | 30.5219 | 30.6479 | 31.1965 | 31.3996 | 0.99893 | 0.9316 | RI | 5.8486 | 0.59998
SM | St Marys | Summer | 10.7653 | 11.1371 | 10.7577 | 10.4579 | 10.1914 | 10.0538 | 10.0561 | 10.0398 | 10.0671 | 10.1119 | 10.1924 | 10.2725 | 0.99571 | 0.63105 | 15.1112 | 17.1811 | 17.2928 | 16.9775 | 16.7947 | 16.7159 | 16.9037 | 17.0323 | 17.2134 | 17.3474 | 17.7252 | 17.9586 | 0.99912 | 0.75654 | TB | 2.9445 | 0
SO | Sorell | Summer | 23.1344 | 23.7 | 23.4583 | 24.4314 | 24.743 | 24.9164 | 25.24 | 25.4448 | 25.7455 | 26.0873 | 26.5161 | 26.9075 | 0.99992 | 0.77083 | 34.9534 | 37.4986 | 38.08 | 38.8545 | 39.1976 | 39.364 | 39.9664 | 40.3812 | 40.9167 | 41.3749 | 42.4236 | 43.0855 | 0.99998 | 0.92281 | SM | 6.2124 | 0
SR | Savage River DL | Summer | 22.9611 | 23.1001 | 25.2805 | 25.2588 | 25.2428 | 25.2341 | 25.2373 | 25.2391 | 25.2449 | 25.2482 | 30.1519 | 30.1534 |  | 0.79167 | 24.3329 | 23.3432 | 25.5383 | 25.5158 | 25.5064 | 25.4986 | 25.5108 | 25.5195 | 25.533 | 25.5376 | 30.444 | 30.448 |  | -0.17391 | SD | 4.8918 | 1.89
ST | Smithton | Summer | 24.355 | 25.3099 | 26.2251 | 26.4874 | 26.4087 | 26.4217 | 26.7404 | 26.9425 | 27.2489 | 27.4768 | 27.7451 | 28.0015 | 0.95925 | 0.87291 | 20.062 | 21.8625 | 23.2722 | 23.4744 | 23.4989 | 23.4256 | 23.7103 | 23.8891 | 24.1527 | 24.2765 | 24.7651 | 25.0154 | 0.97926 | 0.79216 | MT | 11.4925 | 0
SUZ | Zs-Summerleas | Summer | 6.0811 | 5.7946 | 5.5758 | 5.519 | 5.416 | 5.3729 | 5.3878 | 5.3999 | 5.4379 | 5.5173 | 5.6174 | 5.7323 |  |  | 11.8138 | 12.055 | 12.1258 | 12.0599 | 12.014 | 12.031 | 12.2151 | 12.3675 | 12.5587 | 12.7346 | 13.0894 | 13.3299
TB | Triabunna (RT) | Summer | 6.1136 | 5.8378 | 5.8111 | 5.9046 | 5.917 | 5.9452 | 6.036 | 6.1116 | 6.2137 | 6.3307 | 6.475 | 6.611 | 0.99304 | 0.662 | 7.8426 | 9.0762 | 9.1933 | 9.2029 | 9.1935 | 9.1834 | 9.3127 | 9.4109 | 9.5514 | 9.6738 | 9.9467 | 10.1283 | 1 | 0.82309 | HA | 15.1834 | 1.0487
THZ | Zs-Trial Harbour | Summer | 1.9425 | 2.2437 | 2.2965 | 1.9216 | 1.7276 | 1.6645 | 1.6666 | 1.6788 | 1.6992 | 1.7213 | 1.7495 | 1.7864 |  |  | 2.6591 | 3.1466 | 3.1968 | 2.8121 | 2.6243 | 2.555 | 2.5728 | 2.5956 | 2.629 | 2.6513 | 2.7148 | 2.7584
TR | Trevallyn | Summer | 38.8026 | 38.6613 | 37.1623 | 36.7065 | 36.0912 | 35.8842 | 36.0529 | 36.1513 | 36.3832 | 36.7016 | 37.103 | 37.5277 |  | 0.88594 | 68.7532 | 71.3244 | 70.6397 | 69.5726 | 68.9059 | 68.601 | 69.2376 | 69.6539 | 70.2397 | 70.5701 | 71.8702 | 72.4654 | 0.99992 | 0.92367 | RA | 11.638 | 3.2592
TU | Tungatinah | Summer | 0.70458 | 0.74973 | 0.73167 | 0.71642 | 0.70512 | 0.70393 | 0.71297 | 0.72017 | 0.73047 | 0.7416 | 0.75488 | 0.76953 | 0.99832 | 0.61017 | 1.1565 | 1.0265 | 1.0362 | 1.0216 | 1.0169 | 1.0189 | 1.0385 | 1.0546 | 1.0742 | 1.0903 | 1.1222 | 1.1453 | 0.98466 | 0.83333 | ST | 3.3141 | 1.1333
UL | Ulverstone | Summer | 23.2102 | 19.0966 | 18.3364 | 17.7131 | 17.1317 | 16.7992 | 16.7065 | 16.5977 | 16.5712 | 16.6017 | 16.7049 | 16.8159 | 0.99583 | 0.67998 | 32.1449 | 31.413 | 31.4189 | 30.875 | 30.5323 | 30.3636 | 30.6814 | 30.9119 | 31.2463 | 31.4904 | 32.2099 | 32.605 | 1 | 0.84857 | KI11 | 9.0801 | 0.30004
WA | Waddamana | Summer | 0.1453 | 0.14344 | 0.13461 | 0.1317 | 0.13212 | 0.13654 | 0.14628 | 0.15938 | 0.17588 | 0.19996 | 0.23012 | 0.2621 | 0.95 |  | 0.55831 | 0.90555 | 0.9111 | 0.89823 | 0.89602 | 0.90382 | 0.92812 | 0.95182 | 0.98179 | 1.0141 | 1.0627 | 1.1053 | 0.99995 |  | DE | 1.3562 | 2.02
WHZ | Zs-West Hobart | Summer | 23.1266 | 26.2904 | 27.1819 | 27.3333 | 27.2628 | 27.4879 | 27.9795 | 28.4224 | 28.9438 | 29.527 | 30.1052 | 30.7868 |  |  | 37.525 | 37.7186 | 38.7146 | 38.6083 | 38.5951 | 38.8252 | 39.6229 | 40.3429 | 41.2148 | 42.0053 | 43.3042 | 44.3479
WV | Wesley Vale | Summer | 7.9193 | 8.8731 | 8.4105 | 8.1959 | 8.0304 | 7.9395 | 7.9713 | 7.9837 | 8.0338 | 8.0532 | 8.1104 | 8.1003 |  | 0.77692 | 12.614 | 11.4381 | 11.1202 | 10.8327 | 10.6808 | 10.5453 | 10.6117 | 10.6468 | 10.733 | 10.7357 | 10.9305 | 10.9317 |  | 0.8574 | KI33 | 2.8651 | 0
WYZ | Wayatinah | Winter | 0.58305 | 1.2223 | 1.3054 | 1.3072 | 1.3076 | 1.3151 | 1.3209 | 1.3263 | 1.3302 | 1.3398 | 1.3457 | 1.3624 |  | 0.7972 | 1.2994 | 1.1687 | 1.3102 | 1.3173 | 1.321 | 1.3362 | 1.3486 | 1.3601 | 1.3692 | 1.3875 | 1.3996 | 1.4293 |  | 0.10569 | SL | 5.9534 | 0
| Zs-CambridgeMT | Winter | [14 empty] | #N/A
| Zs-CambridgeLF | Summer | [14 empty] | #N/A
GO | Gordon | Summer | 0.33193 | 0.3265 | 0.31328 | 0.30856 | 0.30519 | 0.30428 | 0.30753 | 0.30966 | 0.31289 | 0.31425 | 0.31655 | 0.3162 |  | 0.63415 | 0.2693 | 0.2627 | 0.25731 | 0.2522 | 0.24992 | 0.24787 | 0.25013 | 0.25143 | 0.25348 | 0.25311 | 0.25683 | 0.25588 |  | 0.73585 | SO | 12.6619 | 1.067
[31 empty] | WV | 4.0988 | 0.265
[31 empty] | WY | 0.00304 | 0.9

## Substation DER
|  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26
[8 empty] | NET DER AVERAGE DAY MAX DEMAND IMPACT (kW) | [10 empty] | NET DER AVERAGE DAY MIN DEMAND IMPACT (kW)
Substation | Abbreviation | [6 empty] | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 |  | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
0 | [7 empty] | 1.8576 | 3.1313 | 4.6455 | 6.3838 | 8.213 | 10.2811 | 12.6303 | 17.7702 | 22.0962 | 26.184 |  | -13.8169 | -16.6384 | -19.6983 | -22.6399 | -25.1841 | -27.4244 | -29.4758 | -31.4685 | -33.5737 | -35.3764
Arthurs Lake | AL | Embedded generation forecast capacity (MVA) | ALEmbedded generation forecast capacity (MVA) |  |  |  |  | 0.64963 | 0.72359 | 0.78166 | 0.83891 | 0.89536 | 0.94917 | 1.0008 | 1.0507 | 1.0986 | 1.1448 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Avoca | AV | Embedded generation forecast capacity (MVA) | AVEmbedded generation forecast capacity (MVA) |  |  |  |  | 229.8202 | 263.3029 | 294.3801 | 325.0065 | 354.8484 | 383.1086 | 410.0514 | 435.8071 | 460.3999 | 483.9619 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgewater | BW | Embedded generation forecast capacity (MVA) | BWEmbedded generation forecast capacity (MVA) |  |  |  |  | 2974.4873 | 3300.0833 | 3556.1955 | 3808.7784 | 4057.986 | 4295.6773 | 4524.1312 | 4744.4679 | 4956.5053 | 5161.3921 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Burnie | BU | Embedded generation forecast capacity (MVA) | BUEmbedded generation forecast capacity (MVA) |  |  |  |  | 1682.5056 | 1862.9759 | 2003.7295 | 2136.33 | 2262.8173 | 2378.9627 | 2486.3559 | 2586.1192 | 2676.9508 | 2759.8075 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chapel Street | CS | Embedded generation forecast capacity (MVA) | CSEmbedded generation forecast capacity (MVA) |  |  |  |  | 1991.1388 | 2268.9419 | 2505.3563 | 2733.8643 | 2956.5449 | 3166.2394 | 3365.1137 | 3554.5277 | 3734.4091 | 3905.9659 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Creek Road | CR | Embedded generation forecast capacity (MVA) | CREmbedded generation forecast capacity (MVA) |  |  |  |  | 4567.3771 | 5158.4752 | 5631.5337 | 6090.7118 | 6538.4676 | 6960.3251 | 7360.6932 | 7742.2333 | 8104.8567 | 8450.9187 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Derby | DE | Embedded generation forecast capacity (MVA) | DEEmbedded generation forecast capacity (MVA) |  |  |  |  | 570.2145 | 639.9426 | 705.3971 | 770.9849 | 835.2516 | 898.1035 | 959.9018 | 1020.7374 | 1080.847 | 1139.8649 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Derwent Bridge | DB | Embedded generation forecast capacity (MVA) | DBEmbedded generation forecast capacity (MVA) |  |  |  |  | 10.0513 | 11.2637 | 12.2484 | 13.23 | 14.2054 | 15.1664 | 16.1173 | 17.0633 | 18.005 | 18.9376 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Devonport | DP | Embedded generation forecast capacity (MVA) | DPEmbedded generation forecast capacity (MVA) |  |  |  |  | 3441.8621 | 3817.4032 | 4126.0268 | 4419.5824 | 4700.0363 | 4958.9612 | 5199.635 | 5424.0693 | 5629.4072 | 5817.586 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Electrona | EL | Embedded generation forecast capacity (MVA) | ELEmbedded generation forecast capacity (MVA) |  |  |  |  | 468.0364 | 521.047 | 564.3236 | 605.6753 | 645.4209 | 682.387 | 716.9719 | 749.463 | 779.3929 | 807.0167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emu Bay | EB | Embedded generation forecast capacity (MVA) | EBEmbedded generation forecast capacity (MVA) |  |  |  |  | 265.5134 | 293.6355 | 314.422 | 334.3744 | 353.8118 | 371.8791 | 388.8847 | 404.9452 | 420.0605 | 434.3536 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Fisher |  | Embedded generation forecast capacity (MVA) | Embedded generation forecast capacity (MVA) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
George Town | GT | Embedded generation forecast capacity (MVA) | GTEmbedded generation forecast capacity (MVA) |  |  |  |  | 136.5015 | 151.5159 | 165.7462 | 179.1831 | 192.1189 | 204.0912 | 215.2525 | 225.706 | 235.2999 | 244.125 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gordon |  | Embedded generation forecast capacity (MVA) | Embedded generation forecast capacity (MVA) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gretna | GRZ | Embedded generation forecast capacity (MVA) | GRZEmbedded generation forecast capacity (MVA) |  |  |  |  | 12.6656 | 14.1833 | 15.416 | 16.6448 | 17.866 | 19.069 | 20.2593 | 21.4435 | 22.6225 | 23.7899 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hadspen | HA | Embedded generation forecast capacity (MVA) | HAEmbedded generation forecast capacity (MVA) |  |  |  |  | 5593.967 | 6376.1529 | 7113.4569 | 7818.8826 | 8491.8215 | 9115.4758 | 9696.3055 | 10239.2168 | 10737.2588 | 11194.7564 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Huon River | HR | Embedded generation forecast capacity (MVA) | HREmbedded generation forecast capacity (MVA) |  |  |  |  | 1.407 | 1.5801 | 1.7183 | 1.8512 | 1.9797 | 2.0995 | 2.2121 | 2.3183 | 2.4165 | 2.5074 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kermandie | KE | Embedded generation forecast capacity (MVA) | KEEmbedded generation forecast capacity (MVA) |  |  |  |  | 383.0144 | 431.113 | 470.8754 | 510.0173 | 548.559 | 585.2413 | 620.4212 | 654.2594 | 686.7421 | 718.0464 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kingston | KI11 | Embedded generation forecast capacity (MVA) | KI11Embedded generation forecast capacity (MVA) |  |  |  |  | 3197.5977 | 3612.887 | 3977.4075 | 4342.1369 | 4705.5296 | 5064.7637 | 5421.604 | 5777.8997 | 6133.8497 | 6487.6286 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kingston (33 kV) | KI33 | Embedded generation forecast capacity (MVA) | KI33Embedded generation forecast capacity (MVA) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Knights Road | KR | Embedded generation forecast capacity (MVA) | KREmbedded generation forecast capacity (MVA) |  |  |  |  | 106.283 | 119.1528 | 129.4229 | 139.2966 | 148.8434 | 157.7501 | 166.1198 | 174.0091 | 181.3041 | 188.0626 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lindisfarne | LF | Embedded generation forecast capacity (MVA) | LFEmbedded generation forecast capacity (MVA) |  |  |  |  | 2512.8723 | 2866.0671 | 3139.8628 | 3408.7188 | 3672.159 | 3922.715 | 4162.3225 | 4392.3221 | 4612.6714 | 4824.5536 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Meadowbank | MB | Embedded generation forecast capacity (MVA) | MBEmbedded generation forecast capacity (MVA) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mornington | MT | Embedded generation forecast capacity (MVA) | MTEmbedded generation forecast capacity (MVA) |  |  |  |  | 3597.132 | 4123.1508 | 4530.6172 | 4930.625 | 5322.4274 | 5694.9681 | 6051.1176 | 6392.8766 | 6720.1961 | 7034.8374 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mowbray | MY | Embedded generation forecast capacity (MVA) | MYEmbedded generation forecast capacity (MVA) |  |  |  |  | 1787.6644 | 1979.4335 | 2166.4847 | 2351.8779 | 2535.0288 | 2714.0391 | 2890.0886 | 3064.112 | 3236.2179 | 3405.5324 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
New Norfolk Terminal | NN | Embedded generation forecast capacity (MVA) | NNEmbedded generation forecast capacity (MVA) |  |  |  |  | 252.5741 | 282.1063 | 305.2396 | 327.7966 | 349.8276 | 370.6672 | 390.4942 | 409.4423 | 427.5048 | 444.7906 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Newton | NT | Embedded generation forecast capacity (MVA) | NTEmbedded generation forecast capacity (MVA) |  |  |  |  | 0.14998 | 0.1679 | 0.1777 | 0.18725 | 0.19655 | 0.20533 | 0.21367 | 0.22162 | 0.22919 | 0.23641 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
North Hobart | NH | Embedded generation forecast capacity (MVA) | NHEmbedded generation forecast capacity (MVA) |  |  |  |  | 800.8598 | 905.6161 | 988.9926 | 1071.7342 | 1153.7735 | 1234.1302 | 1313.3419 | 1391.8128 | 1469.5996 | 1546.3023 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Norwood | NW | Embedded generation forecast capacity (MVA) | NWEmbedded generation forecast capacity (MVA) |  |  |  |  | 1631.8478 | 1810.9378 | 1975.5555 | 2131.9918 | 2281.2469 | 2418.8879 | 2546.6736 | 2665.787 | 2774.6763 | 2874.3881 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Palmerston | PM | Embedded generation forecast capacity (MVA) | PMEmbedded generation forecast capacity (MVA) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Latta | PL | Embedded generation forecast capacity (MVA) | PLEmbedded generation forecast capacity (MVA) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Queenstown | QT | Embedded generation forecast capacity (MVA) | QTEmbedded generation forecast capacity (MVA) |  |  |  |  | 253.2898 | 283.563 | 300.1179 | 316.2359 | 331.9441 | 346.7759 | 360.8598 | 374.2889 | 387.0642 | 399.2639 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Railton | RA | Embedded generation forecast capacity (MVA) | RAEmbedded generation forecast capacity (MVA) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Richmond | RIZ | Embedded generation forecast capacity (MVA) | RIZEmbedded generation forecast capacity (MVA) |  |  |  |  | 578.9777 | 657.0494 | 717.9344 | 776.2682 | 832.4996 | 884.8076 | 933.8064 | 979.8838 | 1022.3787 | 1061.6487 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Risdon | RI | Embedded generation forecast capacity (MVA) | RIEmbedded generation forecast capacity (MVA) |  |  |  |  | 1634.3882 | 1846.1445 | 2014.7367 | 2174.1912 | 2326.8722 | 2467.8637 | 2598.9549 | 2721.3655 | 2833.419 | 2936.1986 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rokeby | RK | Embedded generation forecast capacity (MVA) | RKEmbedded generation forecast capacity (MVA) |  |  |  |  | 3154.2152 | 3620.9045 | 3982.4067 | 4337.283 | 4684.8696 | 5015.3617 | 5331.3046 | 5634.4744 | 5924.8281 | 6203.9285 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rosebery | RB22 | Embedded generation forecast capacity (MVA) | RB22Embedded generation forecast capacity (MVA) |  |  |  |  | 38.3669 | 63.9523 | 79.5141 | 94.6533 | 109.3705 | 123.2394 | 136.3824 | 148.8869 | 160.7587 | 172.072 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Savage River | SR | Embedded generation forecast capacity (MVA) | SREmbedded generation forecast capacity (MVA) |  |  |  |  | 85.3539 | 95.5332 | 104.3439 | 113.0892 | 121.6936 | 130.0988 | 138.3456 | 146.4726 | 154.494 | 162.365 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Scottsdale | SD | Embedded generation forecast capacity (MVA) | SDEmbedded generation forecast capacity (MVA) |  |  |  |  | 1144.9025 | 1271.8 | 1385.6446 | 1494.3068 | 1597.2659 | 1692.0602 | 1779.9103 | 1861.393 | 1935.6886 | 2003.4982 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Smithton | ST | Embedded generation forecast capacity (MVA) | STEmbedded generation forecast capacity (MVA) |  |  |  |  | 213.0668 | 247.4094 | 281.6624 | 314.7564 | 345.5951 | 374.1009 | 400.3736 | 424.6187 | 446.6622 | 466.6846 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sorell | SO | Embedded generation forecast capacity (MVA) | SOEmbedded generation forecast capacity (MVA) |  |  |  |  | 1475.689 | 1670.7518 | 1817.4261 | 1958.011 | 2093.729 | 2220.4639 | 2339.4214 | 2451.6002 | 2555.3157 | 2651.3958 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
St Leonards | SL | Embedded generation forecast capacity (MVA) | SLEmbedded generation forecast capacity (MVA) |  |  |  |  | 2445.2478 | 2691.4474 | 2924.5604 | 3150.4488 | 3369.6634 | 3575.3479 | 3769.7605 | 3954.305 | 4128.9861 | 4295.0076 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
St Marys | SM | Embedded generation forecast capacity (MVA) | SMEmbedded generation forecast capacity (MVA) |  |  |  |  | 1898.6453 | 2086.4955 | 2246.545 | 2406.5867 | 2565.6267 | 2721.0932 | 2874.592 | 3026.7091 | 3177.5624 | 3326.4117 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Trevallyn | TR | Embedded generation forecast capacity (MVA) | TREmbedded generation forecast capacity (MVA) |  |  |  |  | 3452.6345 | 3870.7926 | 4261.5278 | 4632.6151 | 4987.3204 | 5315.3177 | 5620.2699 | 5905.1422 | 6166.0336 | 6405.3899 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Triabunna | TB | Embedded generation forecast capacity (MVA) | TBEmbedded generation forecast capacity (MVA) |  |  |  |  | 314.5736 | 349.7207 | 376.9904 | 403.7344 | 429.9495 | 454.7816 | 478.4858 | 501.1987 | 522.9075 | 543.7407 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Trial Harbour Road | THZ | Embedded generation forecast capacity (MVA) | THZEmbedded generation forecast capacity (MVA) |  |  |  |  | 23.0469 | 37.7745 | 46.3308 | 54.8547 | 63.3041 | 71.6151 | 79.8235 | 87.9717 | 96.0683 | 104.0691 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tungatinah | TU | Embedded generation forecast capacity (MVA) | TUEmbedded generation forecast capacity (MVA) |  |  |  |  | 71.5148 | 79.8894 | 86.4482 | 92.8402 | 99.0801 | 104.9803 | 110.5911 | 115.9508 | 121.0576 | 125.9425 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ulverstone | UL | Embedded generation forecast capacity (MVA) | ULEmbedded generation forecast capacity (MVA) |  |  |  |  | 4122.7459 | 4602.4241 | 5015.6745 | 5425.9173 | 5831.1119 | 6227.4053 | 6616.9844 | 7001.8209 | 7382.3667 | 7756.573 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wayatinah | WA | Embedded generation forecast capacity (MVA) | WAEmbedded generation forecast capacity (MVA) |  |  |  |  | 2.9686 | 5.667 | 7.7019 | 9.6394 | 11.4969 | 13.2188 | 14.8235 | 16.3259 | 17.7051 | 18.9735 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wesley Vale | WV | Embedded generation forecast capacity (MVA) | WVEmbedded generation forecast capacity (MVA) |  |  |  |  | 735.0057 | 831.1439 | 921.5004 | 1010.4842 | 1097.8487 | 1181.2098 | 1261.1601 | 1338.1141 | 1412.0384 | 1483.3205 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
#N/A | [7 empty] | 115.0778 | 209.4838 | 321.9403 | 451.4632 | 588.1434 | 743.0459 | 919.2364 | 1305.4575 | 1629.8736 | 1936.2611 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## DERdataMAX (hidden)
[20 empty] | MW | [32 empty] | kW
Index | constraint | planning_region | final_ss_code | final_name | scenario | max_min | series | coincidence | Type | season | category | subcategory | units | Transmission Customer | LoadType_MI_or_RT | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
48 | PMA | George Town | TC01 | Comalco | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Camalco | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | George Town | TSW1 | Starwood | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Starwood | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | George Town | TTE1 | Temco | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Temco | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | North | TAL2 | Ax-Arthurs Lake 6.6 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | Ax | 0.00034908 | 0.00039755 | 0.00047542 | 0.00056389 | 0.00064963 | 0.00072359 | 0.00078166 | 0.00083891 | 0.00089536 | 0.00094917 | 0.0010008 | 0.0010507 | 0.0010986 | 0.0011448 | 0.0011898 | 0.0012349 | 0.0012813 | 0.0013284 | 0.001375 | 0.0014207 | 0.0014654 | 0.0015086 | 0.0015512 | 0.001593 | 0.0016338 | 0.0016742 | 0.0017142 | 0.0017534 | 0.0017923 | 0.001831 | 0.0018694 | 0.0019075 | 0.0019453 | 0.0019829 | 0.0020203 | 0.0020575 | 0.0020945 | 0.64963 | 0.72359 | 0.78166 | 0.83891 | 0.89536 | 0.94917 | 1.0008 | 1.0507 | 1.0986 | 1.1448
48 | PMA | North | TAV2 | Avoca 22 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0.11792 | 0.14942 | 0.17489 | 0.19931 | 0.22982 | 0.2633 | 0.29438 | 0.32501 | 0.35485 | 0.38311 | 0.41005 | 0.43581 | 0.4604 | 0.48396 | 0.5067 | 0.52929 | 0.55239 | 0.57566 | 0.59846 | 0.62066 | 0.64218 | 0.66286 | 0.68304 | 0.70269 | 0.72168 | 0.74039 | 0.75869 | 0.7765 | 0.79404 | 0.81132 | 0.82831 | 0.84503 | 0.86149 | 0.87771 | 0.89369 | 0.90944 | 0.92497 | 229.8202 | 263.3029 | 294.3801 | 325.0065 | 354.8484 | 383.1086 | 410.0514 | 435.8071 | 460.3999 | 483.9619
48 | PMA | North | TDE2 | Derby 22 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0.33085 | 0.3803 | 0.44369 | 0.5035 | 0.56972 | 0.63738 | 0.69887 | 0.75911 | 0.8171 | 0.87153 | 0.92297 | 0.9716 | 1.0176 | 1.0612 | 1.1028 | 1.1438 | 1.1853 | 1.2267 | 1.2668 | 1.3055 | 1.3427 | 1.378 | 1.4122 | 1.4451 | 1.4766 | 1.5074 | 1.5372 | 1.5659 | 1.5939 | 1.6213 | 1.6479 | 1.6739 | 1.6992 | 1.7239 | 1.7481 | 1.7716 | 1.7947 | 569.7175 | 637.3842 | 698.8694 | 759.1078 | 817.1015 | 871.5325 | 922.973 | 971.5971 | 1017.576 | 1061.1874
48 | PMA | North | THA3 | Hadspen 22 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 2.9419 | 3.5359 | 4.1462 | 4.8132 | 5.6001 | 6.4082 | 7.1944 | 7.9642 | 8.7121 | 9.419 | 10.0908 | 10.7316 | 11.3416 | 11.9245 | 12.4855 | 13.0413 | 13.6083 | 14.1777 | 14.7341 | 15.2744 | 15.7968 | 16.2976 | 16.7847 | 17.2579 | 17.7139 | 18.1618 | 18.5991 | 19.0231 | 19.4399 | 19.8492 | 20.2507 | 20.6446 | 21.0313 | 21.4114 | 21.785 | 22.1521 | 22.5129 | 5600.0615 | 6408.155 | 7194.3764 | 7964.2157 | 8712.0619 | 9419.0044 | 10090.8278 | 10731.5548 | 11341.6024 | 11924.4879
48 | PMA | North | TMY2 | Mowbray 22 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0.9257 | 1.1315 | 1.351 | 1.5707 | 1.7863 | 1.9721 | 2.1478 | 2.3181 | 2.4834 | 2.6384 | 2.785 | 2.924 | 3.0557 | 3.1808 | 3.3006 | 3.4185 | 3.5382 | 3.6578 | 3.7739 | 3.8861 | 3.994 | 4.0968 | 4.1962 | 4.2923 | 4.3844 | 4.4743 | 4.5615 | 4.6457 | 4.7279 | 4.8082 | 4.8866 | 4.963 | 5.0375 | 5.1104 | 5.1816 | 5.2512 | 5.3192 | 1786.2562 | 1972.0528 | 2147.8151 | 2318.1095 | 2483.3738 | 2638.418 | 2784.9554 | 2924.0452 | 3055.6902 | 3180.7997
48 | PMA | North | TPM3 | Palmerston 22 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | North | TSD2 | Scottsdale 22 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0.68795 | 0.77766 | 0.89744 | 1.0187 | 1.1459 | 1.2768 | 1.3982 | 1.5168 | 1.6312 | 1.7386 | 1.8403 | 1.9364 | 2.0274 | 2.1138 | 2.1964 | 2.2777 | 2.3601 | 2.4423 | 2.5222 | 2.5993 | 2.6733 | 2.7439 | 2.8121 | 2.8779 | 2.941 | 3.0026 | 3.0623 | 3.12 | 3.1762 | 3.2312 | 3.2848 | 3.3371 | 3.3881 | 3.438 | 3.4867 | 3.5344 | 3.5809 | 1145.8772 | 1276.7922 | 1398.1869 | 1516.7855 | 1631.1942 | 1738.6447 | 1840.2506 | 1936.4079 | 2027.402 | 2113.7906
48 | PMA | North | TSL2 | St Leonards 22 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 1.3143 | 1.5404 | 1.8154 | 2.142 | 2.4452 | 2.6914 | 2.9246 | 3.1504 | 3.3697 | 3.5753 | 3.7698 | 3.9543 | 4.129 | 4.295 | 4.4539 | 4.6105 | 4.7694 | 4.9281 | 5.0823 | 5.2312 | 5.3744 | 5.5109 | 5.643 | 5.7706 | 5.8929 | 6.0123 | 6.1282 | 6.24 | 6.3493 | 6.456 | 6.5601 | 6.6616 | 6.7607 | 6.8576 | 6.9522 | 7.0447 | 7.1351 | 2445.2478 | 2691.4474 | 2924.5604 | 3150.4488 | 3369.6634 | 3575.3479 | 3769.7605 | 3954.305 | 4128.9861 | 4295.0076
48 | PMA | North | TSL3 | St Leonards 22 kV (scheduled load) | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Firmus Grid | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | North | TSM2 | St Marys 22 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0.94174 | 1.1809 | 1.4436 | 1.6677 | 1.8974 | 2.0801 | 2.2304 | 2.3774 | 2.5209 | 2.6556 | 2.7833 | 2.9049 | 3.0203 | 3.1303 | 3.2359 | 3.3402 | 3.4463 | 3.5526 | 3.6562 | 3.7565 | 3.8532 | 3.9457 | 4.0355 | 4.1224 | 4.206 | 4.2879 | 4.3676 | 4.4447 | 4.5203 | 4.5943 | 4.6667 | 4.7376 | 4.807 | 4.8751 | 4.9418 | 5.0072 | 5.0712 | 1897.3817 | 2080.0645 | 2230.4409 | 2377.4267 | 2520.9398 | 2655.5784 | 2783.3421 | 2904.9175 | 3020.3027 | 3130.2847
48 | PMA | Northwest | TDP2 | Devonport 22 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 1.8825 | 2.1757 | 2.5355 | 2.9784 | 3.4445 | 3.831 | 4.1601 | 4.4805 | 4.7922 | 5.0856 | 5.364 | 5.6289 | 5.8804 | 6.1201 | 6.3503 | 6.5778 | 6.8092 | 7.0411 | 7.2672 | 7.4861 | 7.6973 | 7.8993 | 8.0952 | 8.2851 | 8.4676 | 8.6465 | 8.8207 | 8.9892 | 9.1544 | 9.3163 | 9.4746 | 9.6296 | 9.7814 | 9.9303 | 10.0762 | 10.2193 | 10.3596 | 3444.509 | 3831.0399 | 4160.0934 | 4480.4894 | 4792.1505 | 5085.647 | 5364.0209 | 5628.8832 | 5880.3892 | 6120.1366
48 | PMA | Northwest | TEB2 | Emu Bay 11 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Emu Bay | MI | 0.13673 | 0.16675 | 0.19871 | 0.23161 | 0.26551 | 0.29364 | 0.31442 | 0.33437 | 0.35381 | 0.37188 | 0.38888 | 0.40495 | 0.42006 | 0.43435 | 0.44796 | 0.4613 | 0.47475 | 0.48812 | 0.50105 | 0.51347 | 0.52534 | 0.53661 | 0.54744 | 0.55785 | 0.56778 | 0.57742 | 0.58673 | 0.59566 | 0.60435 | 0.61278 | 0.62096 | 0.6289 | 0.63661 | 0.64411 | 0.65139 | 0.65847 | 0.66535 | 265.5134 | 293.6355 | 314.422 | 334.3744 | 353.8118 | 371.8791 | 388.8847 | 404.9452 | 420.0605 | 434.3536
48 | PMA | Northwest | THM2 | Hampshire | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Hampshire | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Northwest | TPL2 | Port Latta | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | Port Latta | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Northwest | TRA2 | Railton 22 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Northwest | TSH3 | Sheffield | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Northwest | TST2 | Smithton 22 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0.11298 | 0.13907 | 0.1642 | 0.18346 | 0.21334 | 0.24885 | 0.2854 | 0.32151 | 0.35578 | 0.38809 | 0.41848 | 0.44709 | 0.47409 | 0.49959 | 0.52388 | 0.54769 | 0.57171 | 0.59557 | 0.61865 | 0.64082 | 0.66203 | 0.68213 | 0.70148 | 0.72008 | 0.7378 | 0.75502 | 0.77165 | 0.7876 | 0.80311 | 0.81818 | 0.83279 | 0.84698 | 0.86075 | 0.87414 | 0.88715 | 0.89981 | 0.9121 | 213.3376 | 248.8493 | 285.4014 | 321.5137 | 355.7832 | 388.0945 | 418.4788 | 447.0898 | 474.0852 | 499.5924
48 | PMA | Northwest | TUL2 | Ulverstone 22 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 2.3973 | 2.7385 | 3.152 | 3.6105 | 4.1197 | 4.5862 | 4.9744 | 5.3512 | 5.7168 | 6.0601 | 6.3844 | 6.6919 | 6.983 | 7.2595 | 7.5241 | 7.7847 | 8.0489 | 8.3127 | 8.5689 | 8.8163 | 9.0541 | 9.2806 | 9.4996 | 9.7112 | 9.9138 | 10.1116 | 10.3035 | 10.4886 | 10.6693 | 10.8458 | 11.0178 | 11.1855 | 11.3492 | 11.509 | 11.6652 | 11.8178 | 11.9668 | 4119.6579 | 4586.1667 | 4974.4162 | 5351.2219 | 5716.8459 | 6060.0787 | 6384.3523 | 6691.9362 | 6983.0196 | 7259.5299
48 | PMA | Northwest | TWV2 | Wesley Vale 11 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | Wesley Vale | MI | 0.36594 | 0.43045 | 0.52262 | 0.62956 | 0.73501 | 0.83114 | 0.9215 | 1.0105 | 1.0978 | 1.1812 | 1.2612 | 1.3381 | 1.412 | 1.4833 | 1.5526 | 1.6218 | 1.693 | 1.7652 | 1.8364 | 1.9062 | 1.9742 | 2.04 | 2.1046 | 2.168 | 2.2296 | 2.2906 | 2.3507 | 2.4095 | 2.4679 | 2.5257 | 2.5829 | 2.6396 | 2.6957 | 2.7513 | 2.8065 | 2.8612 | 2.9155 | 735.0057 | 831.1439 | 921.5004 | 1010.4842 | 1097.8487 | 1181.2098 | 1261.1601 | 1338.1141 | 1412.0384 | 1483.3205
48 | PMA | Southern | TBW2 | Bridgewater 11 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 1.6264 | 1.8376 | 2.1832 | 2.5897 | 2.9745 | 3.3001 | 3.5562 | 3.8088 | 4.058 | 4.2957 | 4.5241 | 4.7445 | 4.9565 | 5.1614 | 5.3608 | 5.5606 | 5.7667 | 5.976 | 6.1828 | 6.386 | 6.5847 | 6.7773 | 6.9669 | 7.1532 | 7.3349 | 7.5154 | 7.6936 | 7.8686 | 8.0426 | 8.2155 | 8.3871 | 8.5575 | 8.7268 | 8.8952 | 9.0627 | 9.2294 | 9.3951 | 2974.4873 | 3300.0833 | 3556.1955 | 3808.7784 | 4057.986 | 4295.6773 | 4524.1312 | 4744.4679 | 4956.5053 | 5161.3921
48 | PMA | Southern | TBYA | Boyer SWA | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Boyer | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Southern | TBYB | Boyer SWB | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Boyer | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Southern | TCR2 | Creek Rd 33 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 2.5047 | 2.8775 | 3.3595 | 3.9287 | 4.5674 | 5.1585 | 5.6315 | 6.0907 | 6.5385 | 6.9603 | 7.3607 | 7.7422 | 8.1049 | 8.4509 | 8.7836 | 9.1126 | 9.4479 | 9.7841 | 10.1122 | 10.4304 | 10.7376 | 11.0317 | 11.3174 | 11.5946 | 11.8614 | 12.123 | 12.378 | 12.625 | 12.8675 | 13.1053 | 13.3383 | 13.5665 | 13.7902 | 14.0098 | 14.2254 | 14.4369 | 14.6446 | 4567.3771 | 5158.4752 | 5631.5337 | 6090.7118 | 6538.4676 | 6960.3251 | 7360.6932 | 7742.2333 | 8104.8567 | 8450.9187
48 | PMA | Southern | TCS3 | Chapel St 11 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 1.0991 | 1.249 | 1.4605 | 1.7133 | 1.9911 | 2.2689 | 2.5054 | 2.7339 | 2.9565 | 3.1662 | 3.3651 | 3.5545 | 3.7344 | 3.906 | 4.0708 | 4.2337 | 4.3995 | 4.5657 | 4.7278 | 4.8849 | 5.0364 | 5.1814 | 5.3221 | 5.4585 | 5.5896 | 5.7181 | 5.8434 | 5.9645 | 6.0833 | 6.1998 | 6.3137 | 6.4253 | 6.5346 | 6.6417 | 6.7468 | 6.8498 | 6.9508 | 1991.1388 | 2268.9419 | 2505.3563 | 2733.8643 | 2956.5449 | 3166.2394 | 3365.1137 | 3554.5277 | 3734.4091 | 3905.9659
48 | PMA | Southern | TDB2 | Derwent Bridge 22 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0.0058532 | 0.0066611 | 0.0076296 | 0.0087712 | 0.010044 | 0.011225 | 0.01215 | 0.013052 | 0.013932 | 0.014764 | 0.015556 | 0.016312 | 0.017032 | 0.017721 | 0.018385 | 0.019043 | 0.019716 | 0.020392 | 0.021053 | 0.021696 | 0.022318 | 0.022915 | 0.023496 | 0.024061 | 0.024607 | 0.025143 | 0.025667 | 0.026176 | 0.026676 | 0.027168 | 0.027651 | 0.028126 | 0.028592 | 0.029051 | 0.029503 | 0.029947 | 0.030384 | 10.0441 | 11.2253 | 12.1505 | 13.052 | 13.9322 | 14.7644 | 15.5558 | 16.3118 | 17.0321 | 17.7211
48 | PMA | Southern | TEL2 | Electrona 11 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0.27974 | 0.31639 | 0.3626 | 0.41424 | 0.4684 | 0.52294 | 0.56908 | 0.61421 | 0.65839 | 0.70029 | 0.74029 | 0.77864 | 0.8153 | 0.8505 | 0.88453 | 0.9184 | 0.9531 | 0.98812 | 1.0225 | 1.056 | 1.0886 | 1.1199 | 1.1505 | 1.1804 | 1.2094 | 1.2379 | 1.2659 | 1.2931 | 1.32 | 1.3466 | 1.3727 | 1.3985 | 1.4239 | 1.449 | 1.4737 | 1.4982 | 1.5223 | 468.3989 | 522.9404 | 569.0825 | 614.2135 | 658.3853 | 700.2891 | 740.2938 | 778.64 | 815.3037 | 850.4996
48 | PMA | Southern | THR2 | Huon River | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Huon River | MI | 0.00077139 | 0.00089743 | 0.0010512 | 0.0012212 | 0.0014081 | 0.0015862 | 0.0017336 | 0.0018786 | 0.0020214 | 0.0021572 | 0.0022875 | 0.0024128 | 0.0025331 | 0.002649 | 0.0027614 | 0.0028738 | 0.0029893 | 0.0031063 | 0.0032216 | 0.0033344 | 0.0034444 | 0.0035507 | 0.003655 | 0.0037571 | 0.0038563 | 0.0039545 | 0.0040511 | 0.0041456 | 0.0042393 | 0.0043319 | 0.0044236 | 0.0045142 | 0.0046039 | 0.0046928 | 0.0047809 | 0.0048681 | 0.0049545 | 1.4081 | 1.5862 | 1.7336 | 1.8786 | 2.0214 | 2.1572 | 2.2875 | 2.4128 | 2.5331 | 2.649
48 | PMA | Southern | TK12 | Kingston 11 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 1.7336 | 1.9837 | 2.3406 | 2.7539 | 3.1949 | 3.5987 | 3.9412 | 4.2761 | 4.604 | 4.9151 | 5.2121 | 5.4968 | 5.7691 | 6.0304 | 6.2832 | 6.5347 | 6.7925 | 7.0526 | 7.3079 | 7.5569 | 7.7989 | 8.0318 | 8.2594 | 8.4815 | 8.6965 | 8.9086 | 9.1167 | 9.3193 | 9.5193 | 9.7167 | 9.9111 | 10.1027 | 10.2916 | 10.4781 | 10.6622 | 10.8439 | 11.0233 | 3194.9084 | 3598.6732 | 3941.1535 | 4276.1486 | 4604.0193 | 4915.0952 | 5212.0948 | 5496.8078 | 5769.0512 | 6030.418
48 | PMA | Southern | TK13 | Kingston 33 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Southern | TKE2 | Kermandie 11 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0.20696 | 0.24483 | 0.28985 | 0.33256 | 0.38301 | 0.43111 | 0.47088 | 0.51002 | 0.54856 | 0.58524 | 0.62042 | 0.65426 | 0.68674 | 0.71805 | 0.74843 | 0.77878 | 0.81001 | 0.84163 | 0.87278 | 0.90329 | 0.93303 | 0.96177 | 0.98997 | 1.0176 | 1.0444 | 1.071 | 1.0971 | 1.1227 | 1.148 | 1.1731 | 1.198 | 1.2225 | 1.2468 | 1.2709 | 1.2947 | 1.3183 | 1.3417 | 383.0144 | 431.113 | 470.8754 | 510.0173 | 548.559 | 585.2413 | 620.4212 | 654.2594 | 686.7421 | 718.0464
48 | PMA | Southern | TLF2 | Lindisfarne 33 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 1.3376 | 1.5206 | 1.7944 | 2.1302 | 2.5129 | 2.8661 | 3.1399 | 3.4087 | 3.6722 | 3.9227 | 4.1623 | 4.3923 | 4.6127 | 4.8246 | 5.0298 | 5.2344 | 5.4444 | 5.6566 | 5.8653 | 6.0692 | 6.2676 | 6.459 | 6.6462 | 6.8293 | 7.0068 | 7.1822 | 7.3545 | 7.5227 | 7.6889 | 7.8532 | 8.0154 | 8.1754 | 8.3335 | 8.4898 | 8.6444 | 8.7972 | 8.9483 | 2512.8723 | 2866.0671 | 3139.8628 | 3408.7188 | 3672.159 | 3922.715 | 4162.3225 | 4392.3221 | 4612.6714 | 4824.5536
48 | PMA | Southern | TMB2 | Meadowbank 22 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Southern | TMT2 | Mornington 33 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 1.8847 | 2.1391 | 2.5251 | 3.0197 | 3.5971 | 4.1232 | 4.5306 | 4.9306 | 5.3224 | 5.695 | 6.0511 | 6.3929 | 6.7202 | 7.0348 | 7.3395 | 7.6431 | 7.9547 | 8.2694 | 8.5788 | 8.8811 | 9.175 | 9.4584 | 9.7357 | 10.0066 | 10.2692 | 10.5287 | 10.7834 | 11.0319 | 11.2776 | 11.5202 | 11.7596 | 11.9958 | 12.229 | 12.4595 | 12.6873 | 12.9125 | 13.1351 | 3597.132 | 4123.1508 | 4530.6172 | 4930.625 | 5322.4274 | 5694.9681 | 6051.1176 | 6392.8766 | 6720.1961 | 7034.8374
48 | PMA | Southern | TNH2 | North Hobart 11 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0.45368 | 0.51946 | 0.59562 | 0.68753 | 0.80024 | 0.90234 | 0.98068 | 1.0567 | 1.1307 | 1.2003 | 1.2662 | 1.3289 | 1.3884 | 1.4451 | 1.4995 | 1.5532 | 1.6078 | 1.6624 | 1.7157 | 1.7672 | 1.8168 | 1.8643 | 1.9102 | 1.9548 | 1.9975 | 2.0394 | 2.0801 | 2.1195 | 2.158 | 2.1958 | 2.2326 | 2.2687 | 2.304 | 2.3385 | 2.3724 | 2.4055 | 2.438 | 800.2384 | 902.3378 | 980.6819 | 1056.6788 | 1130.7059 | 1200.3009 | 1266.2329 | 1328.9487 | 1388.4472 | 1445.1221
48 | PMA | Southern | TNN2 | New Norfolk 22 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | Brynn Estyn | MI | 0.14705 | 0.1672 | 0.19176 | 0.22064 | 0.25257 | 0.28211 | 0.30524 | 0.3278 | 0.34983 | 0.37067 | 0.39049 | 0.40944 | 0.4275 | 0.44479 | 0.46145 | 0.47799 | 0.49488 | 0.51187 | 0.5285 | 0.54467 | 0.56033 | 0.57537 | 0.59002 | 0.60427 | 0.61803 | 0.63157 | 0.6448 | 0.65766 | 0.67032 | 0.68277 | 0.695 | 0.70702 | 0.71885 | 0.73049 | 0.74195 | 0.75323 | 0.76434 | 252.5741 | 282.1063 | 305.2396 | 327.7966 | 349.8276 | 370.6672 | 390.4942 | 409.4423 | 427.5048 | 444.7906
48 | PMA | Southern | TR13 | Risdon 11 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Risdon | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Southern | TR14 | Risdon 33 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0.91939 | 1.0443 | 1.201 | 1.4 | 1.6358 | 1.8536 | 2.0333 | 2.2073 | 2.377 | 2.5368 | 2.6884 | 2.8329 | 2.9702 | 3.1011 | 3.2269 | 3.3514 | 3.4781 | 3.6052 | 3.7292 | 3.8494 | 3.9654 | 4.0764 | 4.1842 | 4.2888 | 4.3894 | 4.4881 | 4.5843 | 4.6774 | 4.7687 | 4.8583 | 4.946 | 5.032 | 5.1162 | 5.1988 | 5.2799 | 5.3595 | 5.4376 | 1635.8153 | 1853.5789 | 2033.2975 | 2207.3248 | 2376.9981 | 2536.8123 | 2688.4399 | 2832.9011 | 2970.1504 | 3101.0968
48 | PMA | Southern | TRK2 | Rokeby 11 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 1.607 | 1.8442 | 2.1931 | 2.634 | 3.1542 | 3.6209 | 3.9824 | 4.3373 | 4.6849 | 5.0154 | 5.3313 | 5.6345 | 5.9248 | 6.2039 | 6.4742 | 6.7435 | 7.0198 | 7.299 | 7.5734 | 7.8415 | 8.1021 | 8.3535 | 8.5994 | 8.8397 | 9.0726 | 9.3026 | 9.5285 | 9.7489 | 9.9667 | 10.1818 | 10.3941 | 10.6034 | 10.8102 | 11.0146 | 11.2166 | 11.4162 | 11.6135 | 3154.2152 | 3620.9045 | 3982.4067 | 4337.283 | 4684.8696 | 5015.3617 | 5331.3046 | 5634.4744 | 5924.8281 | 6203.9285
48 | PMA | Southern | TS02 | Sorell | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0.7646 | 0.89123 | 1.0632 | 1.2586 | 1.4769 | 1.6772 | 1.8336 | 1.987 | 2.1378 | 2.2815 | 2.4191 | 2.5515 | 2.6786 | 2.801 | 2.9198 | 3.0385 | 3.1606 | 3.2843 | 3.4061 | 3.5254 | 3.6418 | 3.7542 | 3.8646 | 3.9727 | 4.0778 | 4.1819 | 4.2844 | 4.3846 | 4.484 | 4.5825 | 4.68 | 4.7764 | 4.8719 | 4.9666 | 5.0605 | 5.1535 | 5.2458 | 1476.906 | 1677.1502 | 1833.5518 | 1986.9946 | 2137.8332 | 2281.5013 | 2419.1064 | 2551.5051 | 2678.5637 | 2800.9859
48 | PMA | Southern | TTB2 | Triabunna 22 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0.15761 | 0.19624 | 0.23445 | 0.27077 | 0.31457 | 0.34972 | 0.37699 | 0.40373 | 0.42995 | 0.45478 | 0.47849 | 0.5012 | 0.52291 | 0.54374 | 0.56388 | 0.58391 | 0.60444 | 0.62514 | 0.64545 | 0.66526 | 0.6845 | 0.70302 | 0.72111 | 0.73877 | 0.75585 | 0.7727 | 0.78922 | 0.80532 | 0.82121 | 0.83688 | 0.85231 | 0.86752 | 0.88252 | 0.89733 | 0.91195 | 0.92638 | 0.94062 | 314.5736 | 349.7207 | 376.9904 | 403.7344 | 429.9495 | 454.7816 | 478.4858 | 501.1987 | 522.9075 | 543.7407
48 | PMA | Southern | TTU2 | Tungatinah 22 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0.041793 | 0.047521 | 0.054392 | 0.06249 | 0.071515 | 0.079889 | 0.086448 | 0.09284 | 0.09908 | 0.10498 | 0.11059 | 0.11595 | 0.12106 | 0.12594 | 0.13065 | 0.13532 | 0.14008 | 0.14488 | 0.14956 | 0.15412 | 0.15853 | 0.16276 | 0.16688 | 0.17089 | 0.17476 | 0.17856 | 0.18227 | 0.18588 | 0.18943 | 0.19292 | 0.19634 | 0.19971 | 0.20301 | 0.20627 | 0.20947 | 0.21262 | 0.21572 | 71.5148 | 79.8894 | 86.4482 | 92.8402 | 99.0801 | 104.9803 | 110.5911 | 115.9508 | 121.0576 | 125.9425
48 | PMA | Southern | TWA2 | Waddamana 22 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0.017701 | 0.02016 | 0.02411 | 0.028596 | 0.032949 | 0.036708 | 0.039661 | 0.042572 | 0.045442 | 0.048177 | 0.050804 | 0.053336 | 0.055771 | 0.058122 | 0.060408 | 0.062698 | 0.065058 | 0.067453 | 0.069819 | 0.072141 | 0.074411 | 0.07661 | 0.078772 | 0.080897 | 0.082966 | 0.085022 | 0.087051 | 0.089041 | 0.091019 | 0.092984 | 0.094933 | 0.096867 | 0.098788 | 0.1007 | 0.1026 | 0.10448 | 0.10636 | 32.9494 | 36.7083 | 39.6613 | 42.572 | 45.4421 | 48.1772 | 50.8042 | 53.3361 | 55.7709 | 58.1219
48 | PMA | Western | TGO2 | Gordon | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Western | TNT2 | Newton 22 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 7.924e-05 | 8.809e-05 | 9.9043e-05 | 0.00012121 | 0.00014998 | 0.0001679 | 0.0001777 | 0.00018725 | 0.00019655 | 0.00020533 | 0.00021367 | 0.00022162 | 0.00022919 | 0.00023641 | 0.00024336 | 0.00025024 | 0.00025725 | 0.00026429 | 0.00027116 | 0.00027783 | 0.00028428 | 0.00029045 | 0.00029646 | 0.00030228 | 0.00030789 | 0.0003134 | 0.00031878 | 0.00032398 | 0.0003291 | 0.00033412 | 0.00033904 | 0.00034387 | 0.0003486 | 0.00035325 | 0.00035781 | 0.0003623 | 0.0003667 | 0.14998 | 0.1679 | 0.1777 | 0.18725 | 0.19655 | 0.20533 | 0.21367 | 0.22162 | 0.22919 | 0.23641
48 | PMA | Western | TNT3 | Ax-Newton 11 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | Ax | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Western | TQT2 | Queenstown 22 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0.13383 | 0.14877 | 0.16727 | 0.2047 | 0.25329 | 0.28356 | 0.30012 | 0.31624 | 0.33194 | 0.34678 | 0.36086 | 0.37429 | 0.38706 | 0.39926 | 0.411 | 0.42262 | 0.43446 | 0.44635 | 0.45796 | 0.46922 | 0.48011 | 0.49054 | 0.50067 | 0.51052 | 0.51999 | 0.5293 | 0.53837 | 0.54717 | 0.55581 | 0.56428 | 0.5726 | 0.58074 | 0.58874 | 0.59659 | 0.6043 | 0.61187 | 0.61931 | 253.2898 | 283.563 | 300.1179 | 316.2359 | 331.9441 | 346.7759 | 360.8598 | 374.2889 | 387.0642 | 399.2639
48 | PMA | Western | TQT3 | Queenstown 11 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Queenstown 11 kV | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Western | TQU2 | Que | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Que | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Western | TRB2 | Rosebery 44 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Rosebery | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Western | TSR2 | Savage River | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Savage River | MI | 0.048061 | 0.056142 | 0.065245 | 0.074328 | 0.085288 | 0.095187 | 0.10346 | 0.1115 | 0.11926 | 0.12654 | 0.13341 | 0.1399 | 0.14604 | 0.15185 | 0.15741 | 0.16287 | 0.16839 | 0.17389 | 0.17923 | 0.18437 | 0.1893 | 0.19399 | 0.19851 | 0.20287 | 0.20704 | 0.2111 | 0.21504 | 0.21882 | 0.22251 | 0.22611 | 0.22961 | 0.23301 | 0.23633 | 0.23956 | 0.24271 | 0.24579 | 0.24878 | 85.2882 | 95.1874 | 103.4647 | 111.4974 | 119.2616 | 126.5416 | 133.4061 | 139.9019 | 146.0377 | 151.854
48 | PMA | Southern | BEZ | Bellerive | base | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.5472 | 0.6176 | 0.72902 | 0.87404 | 1.0428 | 1.1957 | 1.3141 | 1.4303 | 1.5442 | 1.6524 | 1.7559 | 1.8552 | 1.9503 | 2.0417 | 2.1302 | 2.2185 | 2.309 | 2.4004 | 2.4903 | 2.5781 | 2.6635 | 2.7458 | 2.8263 | 2.905 | 2.9813 | 3.0567 | 3.1307 | 3.2028 | 3.2742 | 3.3446 | 3.4142 | 3.4827 | 3.5505 | 3.6174 | 3.6836 | 3.7489 | 3.8136 | 1042.8348 | 1195.6916 | 1314.0961 | 1430.3304 | 1544.1772 | 1652.425 | 1755.9076 | 1855.2065 | 1950.3078 | 2041.7233
48 | PMA | Southern | CLZ | Claremont | base | maximum | PV | non-coincident | POE50 | summer | zone | zone plus embedded | MW | 0 | Zs | 0.83836 | 0.95383 | 1.1451 | 1.3743 | 1.612 | 1.8302 | 2.0161 | 2.196 | 2.3715 | 2.5369 | 2.694 | 2.8437 | 2.9861 | 3.1221 | 3.2528 | 3.3822 | 3.5141 | 3.6464 | 3.7757 | 3.901 | 4.0221 | 4.1381 | 4.2509 | 4.3603 | 4.4657 | 4.5691 | 4.6699 | 4.7677 | 4.8637 | 4.9579 | 5.0502 | 5.1408 | 5.2296 | 5.3168 | 5.4024 | 5.4866 | 5.5692 | 1612.0006 | 1830.1552 | 2016.0695 | 2195.9771 | 2371.4661 | 2536.9033 | 2693.9782 | 2843.7426 | 2986.1296 | 3122.0818
48 | PMA | Southern | DPZ | Derwent Park | base | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.30994 | 0.35038 | 0.4067 | 0.4768 | 0.55339 | 0.62646 | 0.68835 | 0.74836 | 0.80696 | 0.86227 | 0.91485 | 0.96505 | 1.0128 | 1.0585 | 1.1025 | 1.1461 | 1.1906 | 1.2353 | 1.2791 | 1.3215 | 1.3626 | 1.4021 | 1.4404 | 1.4777 | 1.5137 | 1.5491 | 1.5836 | 1.6171 | 1.6501 | 1.6825 | 1.7143 | 1.7456 | 1.7763 | 1.8065 | 1.8362 | 1.8655 | 1.8942 | 553.3881 | 626.4567 | 688.3531 | 748.357 | 806.9558 | 862.2674 | 914.8512 | 965.05 | 1012.8387 | 1058.5277
48 | PMA | Southern | EHZ | East Hobart | base | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.1669 | 0.19393 | 0.22298 | 0.25522 | 0.29633 | 0.33485 | 0.36441 | 0.39309 | 0.42102 | 0.44728 | 0.47216 | 0.49582 | 0.51827 | 0.53966 | 0.56017 | 0.58043 | 0.60103 | 0.62165 | 0.64173 | 0.66118 | 0.67991 | 0.69781 | 0.71516 | 0.73196 | 0.7481 | 0.76389 | 0.77926 | 0.79411 | 0.80866 | 0.8229 | 0.83682 | 0.85043 | 0.86374 | 0.87678 | 0.88955 | 0.90206 | 0.91431 | 296.3315 | 334.8535 | 364.4136 | 393.0883 | 421.0199 | 447.2793 | 472.1567 | 495.8207 | 518.2709 | 539.6557
48 | PMA | Southern | GBZ | Geilston Bay | base | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.85515 | 0.96363 | 1.1408 | 1.3486 | 1.569 | 1.7764 | 1.937 | 2.0948 | 2.2495 | 2.3967 | 2.5375 | 2.6727 | 2.8022 | 2.9268 | 3.0475 | 3.1679 | 3.2915 | 3.4165 | 3.5394 | 3.6595 | 3.7765 | 3.8893 | 3.9997 | 4.1077 | 4.2125 | 4.316 | 4.4178 | 4.5171 | 4.6154 | 4.7125 | 4.8084 | 4.9031 | 4.9966 | 5.0891 | 5.1807 | 5.2712 | 5.3608 | 1569.0201 | 1776.3658 | 1937.0253 | 2094.8438 | 2249.538 | 2396.7012 | 2537.4793 | 2672.6522 | 2802.192 | 2926.7926
48 | PMA | Southern | GRZ | Gretna | base | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.0074076 | 0.0084189 | 0.0096327 | 0.011063 | 0.012657 | 0.014135 | 0.015293 | 0.016422 | 0.017524 | 0.018566 | 0.019556 | 0.020503 | 0.021405 | 0.022267 | 0.023098 | 0.023922 | 0.024764 | 0.02561 | 0.026438 | 0.027242 | 0.028021 | 0.028769 | 0.029496 | 0.030204 | 0.030887 | 0.031558 | 0.032214 | 0.03285 | 0.033477 | 0.034093 | 0.034698 | 0.035292 | 0.035876 | 0.03645 | 0.037015 | 0.037571 | 0.038118 | 12.6566 | 14.1353 | 15.2934 | 16.4221 | 17.5239 | 18.5657 | 19.5564 | 20.5028 | 21.4045 | 22.2671
48 | PMA | Southern | HOZ | Howrah | base | maximum | PV | non-coincident | POE50 | summer | zone | zone plus embedded | MW | 0 | Zs | 0.89544 | 1.0103 | 1.1989 | 1.446 | 1.7309 | 1.9869 | 2.1853 | 2.38 | 2.5707 | 2.7521 | 2.9254 | 3.0918 | 3.2511 | 3.4042 | 3.5525 | 3.7003 | 3.8519 | 4.0051 | 4.1557 | 4.3027 | 4.4458 | 4.5837 | 4.7186 | 4.8504 | 4.9782 | 5.1045 | 5.2284 | 5.3493 | 5.4688 | 5.5869 | 5.7033 | 5.8182 | 5.9316 | 6.0438 | 6.1546 | 6.2641 | 6.3724 | 1730.8706 | 1986.9391 | 2185.2947 | 2380.0143 | 2570.734 | 2752.0737 | 2925.4302 | 3091.778 | 3251.0935 | 3404.2342
48 | PMA | Southern | NTZ | New Town | base | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.45273 | 0.51284 | 0.58701 | 0.68503 | 0.80441 | 0.91251 | 1.0019 | 1.0883 | 1.1725 | 1.2518 | 1.3269 | 1.3985 | 1.4664 | 1.5311 | 1.5933 | 1.6547 | 1.7172 | 1.7799 | 1.8409 | 1.9 | 1.9571 | 2.0116 | 2.0645 | 2.1158 | 2.165 | 2.2133 | 2.2603 | 2.3058 | 2.3503 | 2.394 | 2.4367 | 2.4785 | 2.5194 | 2.5595 | 2.5988 | 2.6373 | 2.675 | 804.413 | 912.5136 | 1001.8638 | 1088.3025 | 1172.5211 | 1251.7861 | 1326.9327 | 1398.4742 | 1466.3907 | 1531.1369
48 | PMA | Southern | RIZ | Richmond | base | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.31002 | 0.35457 | 0.41891 | 0.49458 | 0.57949 | 0.65973 | 0.72465 | 0.78832 | 0.85081 | 0.91011 | 0.96678 | 1.0212 | 1.0732 | 1.1233 | 1.1717 | 1.22 | 1.2695 | 1.3196 | 1.3688 | 1.4169 | 1.4637 | 1.5088 | 1.553 | 1.5962 | 1.6381 | 1.6796 | 1.7203 | 1.7601 | 1.7995 | 1.8384 | 1.8768 | 1.9148 | 1.9524 | 1.9896 | 2.0264 | 2.0628 | 2.0989 | 579.4926 | 659.7259 | 724.6472 | 788.3178 | 850.8105 | 910.1062 | 966.7845 | 1021.1656 | 1073.2224 | 1123.2577
48 | PMA | Southern | RPZ | Rosny Park | base | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.62925 | 0.70515 | 0.83117 | 0.99073 | 1.1682 | 1.3327 | 1.46 | 1.5851 | 1.7076 | 1.824 | 1.9354 | 2.0422 | 2.1446 | 2.243 | 2.3382 | 2.4332 | 2.5306 | 2.6291 | 2.7259 | 2.8204 | 2.9124 | 3.001 | 3.0878 | 3.1726 | 3.2547 | 3.3359 | 3.4157 | 3.4934 | 3.5703 | 3.6463 | 3.7212 | 3.7951 | 3.8682 | 3.9403 | 4.0117 | 4.0822 | 4.1519 | 1168.2491 | 1332.667 | 1460.0315 | 1585.0722 | 1707.5563 | 1824.0244 | 1935.3747 | 2042.2321 | 2144.5805 | 2242.9704
48 | PMA | Southern | SBZ | Sandy Bay | base | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 1.3655 | 1.5686 | 1.8187 | 2.1206 | 2.4663 | 2.78 | 3.026 | 3.2651 | 3.4982 | 3.7179 | 3.9263 | 4.1249 | 4.3136 | 4.4937 | 4.6668 | 4.838 | 5.0125 | 5.1874 | 5.3581 | 5.5236 | 5.6834 | 5.8363 | 5.9849 | 6.129 | 6.2677 | 6.4037 | 6.5363 | 6.6646 | 6.7906 | 6.9142 | 7.0352 | 7.1537 | 7.2699 | 7.384 | 7.4959 | 7.6057 | 7.7135 | 2466.3089 | 2779.9909 | 3026.0225 | 3265.1114 | 3498.2364 | 3717.8521 | 3926.2664 | 4124.8598 | 4313.5998 | 4493.7025
48 | PMA | Southern | SUZ | Summerleas Road | base | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.65883 | 0.75889 | 0.90746 | 1.0783 | 1.2596 | 1.4236 | 1.5629 | 1.6991 | 1.8323 | 1.9587 | 2.0794 | 2.195 | 2.3056 | 2.4117 | 2.5143 | 2.6164 | 2.721 | 2.8265 | 2.9301 | 3.0311 | 3.1292 | 3.2236 | 3.3158 | 3.4058 | 3.4929 | 3.5789 | 3.6631 | 3.7451 | 3.8261 | 3.9059 | 3.9846 | 4.0621 | 4.1385 | 4.2139 | 4.2883 | 4.3617 | 4.4342 | 1259.6358 | 1423.58 | 1562.8686 | 1699.0663 | 1832.3232 | 1958.7338 | 2079.3951 | 2195.0441 | 2305.6048 | 2411.7264
48 | PMA | Southern | TWY2 | Wayatinah | base | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | RT | 0.013722 | 0.015617 | 0.017888 | 0.020565 | 0.0029855 | 0.0057559 | 0.0079257 | 0.01004 | 0.012104 | 0.014056 | 0.015912 | 0.017686 | 0.019375 | 0.020991 | 0.022548 | 0.024092 | 0.025669 | 0.027254 | 0.028805 | 0.030313 | 0.031772 | 0.033172 | 0.034535 | 0.035861 | 0.03714 | 0.038398 | 0.039627 | 0.04082 | 0.041994 | 0.043148 | 0.044281 | 0.045394 | 0.046488 | 0.047564 | 0.048623 | 0.049665 | 0.05069 | 2.9855 | 5.7559 | 7.9257 | 10.0402 | 12.1045 | 14.0563 | 15.9125 | 17.6855 | 19.375 | 20.991
48 | PMA | Southern | WHZ | West Hobart Zone | base | maximum | PV | non-coincident | POE50 | summer | zone | zone plus embedded | MW | 0 | Zs | 0.60518 | 0.69967 | 0.80934 | 0.93342 | 0.14457 | 0.28273 | 0.39083 | 0.49585 | 0.59825 | 0.6947 | 0.7862 | 0.87338 | 0.95622 | 1.0353 | 1.1112 | 1.1863 | 1.2628 | 1.3395 | 1.4144 | 1.4869 | 1.5569 | 1.624 | 1.689 | 1.7522 | 1.8129 | 1.8724 | 1.9305 | 1.9867 | 2.0418 | 2.0959 | 2.1488 | 2.2006 | 2.2514 | 2.3013 | 2.3502 | 2.3982 | 2.4453 | 144.5702 | 282.7273 | 390.8252 | 495.8534 | 598.2517 | 694.6954 | 786.2039 | 873.3845 | 956.2244 | 1035.2589
48 | PMA | Western | THZ | Trial Harbour | base | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.063729 | 0.070961 | 0.07986 | 0.097555 | 0.022984 | 0.037442 | 0.045481 | 0.053311 | 0.060936 | 0.068134 | 0.074967 | 0.081479 | 0.087673 | 0.093585 | 0.09927 | 0.1049 | 0.11063 | 0.11638 | 0.122 | 0.12745 | 0.13271 | 0.13775 | 0.14265 | 0.1474 | 0.15198 | 0.15647 | 0.16085 | 0.16509 | 0.16926 | 0.17335 | 0.17735 | 0.18128 | 0.18513 | 0.18891 | 0.19262 | 0.19627 | 0.19985 | 22.9844 | 37.4419 | 45.4812 | 53.3109 | 60.9355 | 68.1337 | 74.9666 | 81.4791 | 87.6726 | 93.585
48 | PMA | Western | RBZ | Rosebery 22 kV | base | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.1152 | 0.12955 | 0.14681 | 0.17669 | 0.038367 | 0.063952 | 0.079514 | 0.094653 | 0.10937 | 0.12324 | 0.13638 | 0.14889 | 0.16076 | 0.17207 | 0.18293 | 0.19366 | 0.20458 | 0.21551 | 0.22617 | 0.23649 | 0.24644 | 0.25595 | 0.26519 | 0.27413 | 0.28273 | 0.29115 | 0.29935 | 0.30728 | 0.31506 | 0.32268 | 0.33013 | 0.33742 | 0.34456 | 0.35156 | 0.35842 | 0.36515 | 0.37175 | 38.3669 | 63.9523 | 79.5141 | 94.6533 | 109.3705 | 123.2394 | 136.3824 | 148.8869 | 160.7587 | 172.072
48 | PMA | total terminal |  | total terminal | base | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | #N/A | #N/A | 33.5903 | 38.9738 | 45.725 | 53.4868 | 61.9642 | 69.7367 | 76.3889 | 82.881 | 89.2137 | 95.1982 | 100.8906 | 106.3258 | 111.504 | 116.4565 | 121.2276 | 125.9589 | 130.7893 | 135.6456 | 140.396 | 145.0139 | 149.4834 | 153.7721 | 157.9487 | 162.011 | 165.9297 | 169.7834 | 173.5499 | 177.2071 | 180.8067 | 184.3459 | 187.8223 | 191.2369 | 194.5941 | 197.8985 | 201.1506 | 204.3515 | 207.5018 | 61964.2366 | 69736.7443 | 76388.9474 | 82880.9959 | 89213.7486 | 95198.2252 | 100890.6231 | 106325.8163 | 111503.9545 | 116456.4676
48 | PMA | total zone |  | total zone | base | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | #N/A | #N/A | 8.6354 | 9.8513 | 11.5677 | 13.6795 | 14.8543 | 17.0459 | 18.7832 | 20.4795 | 22.1378 | 23.7082 | 25.2048 | 26.6366 | 28.0034 | 29.3132 | 30.5774 | 31.8336 | 33.1185 | 34.4127 | 35.6811 | 36.9164 | 38.1141 | 39.2656 | 40.3889 | 41.4835 | 42.5413 | 43.5833 | 44.6036 | 45.596 | 46.5744 | 47.538 | 48.4861 | 49.419 | 50.3376 | 51.2433 | 52.1361 | 53.0162 | 53.8838 | 14854.3482 | 17045.941 | 18783.2292 | 20479.4719 | 22137.8271 | 23708.219 | 25204.7757 | 26636.622 | 28003.3957 | 29313.1788
48 | PMA | George Town | TGT3 | George Town 22 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0.078266 | 0.089154 | 0.10375 | 0.12051 | 0.13662 | 0.15214 | 0.16731 | 0.18198 | 0.19636 | 0.20993 | 0.22284 | 0.23517 | 0.24693 | 0.25817 | 0.269 | 0.27975 | 0.29072 | 0.30175 | 0.31254 | 0.32303 | 0.33319 | 0.34293 | 0.35241 | 0.36164 | 0.37054 | 0.37928 | 0.38783 | 0.39613 | 0.40429 | 0.41232 | 0.4202 | 0.42793 | 0.43553 | 0.44301 | 0.45037 | 0.45761 | 0.46472 | 136.6215 | 152.1445 | 167.3131 | 181.9791 | 196.3551 | 209.926 | 222.8364 | 235.1733 | 246.9252 | 258.1691
48 | PMA | North | TNW2 | Norwood 22 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0.89761 | 1.0512 | 1.2232 | 1.4231 | 1.6332 | 1.8182 | 1.9937 | 2.1644 | 2.3303 | 2.4863 | 2.6341 | 2.7747 | 2.908 | 3.0351 | 3.1569 | 3.2773 | 3.3997 | 3.5222 | 3.6415 | 3.7571 | 3.8684 | 3.9748 | 4.078 | 4.1779 | 4.2738 | 4.3678 | 4.4592 | 4.5476 | 4.6342 | 4.719 | 4.8019 | 4.883 | 4.9623 | 5.04 | 5.1162 | 5.1908 | 5.264 | 1633.2376 | 1818.1748 | 1993.6828 | 2164.4032 | 2330.2653 | 2486.2815 | 2634.083 | 2774.6516 | 2908.0213 | 3035.0574
48 | PMA | North | TTR2 | Trevallyn 22 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 1.8699 | 2.188 | 2.5558 | 2.9926 | 3.4559 | 3.8879 | 4.3045 | 4.7095 | 5.1037 | 5.4755 | 5.8282 | 6.1644 | 6.484 | 6.7889 | 7.0821 | 7.3721 | 7.6675 | 7.9639 | 8.2531 | 8.5336 | 8.8045 | 9.0637 | 9.3156 | 9.56 | 9.7952 | 10.0258 | 10.2507 | 10.4685 | 10.6824 | 10.8921 | 11.0975 | 11.2988 | 11.4961 | 11.6898 | 11.8799 | 12.0665 | 12.2496 | 3455.9106 | 3887.9385 | 4304.532 | 4709.5075 | 5103.6976 | 5475.4869 | 5828.213 | 6164.4044 | 6483.9599 | 6788.914
48 | PMA | Northwest | TBU3 | Burnie 22 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0.94235 | 1.0982 | 1.277 | 1.4722 | 1.6837 | 1.8692 | 2.0193 | 2.164 | 2.3046 | 2.4362 | 2.5604 | 2.6782 | 2.7894 | 2.895 | 2.9958 | 3.0951 | 3.1956 | 3.2958 | 3.3931 | 3.4869 | 3.5769 | 3.6626 | 3.7454 | 3.8252 | 3.9016 | 3.9761 | 4.0483 | 4.1179 | 4.1857 | 4.2519 | 4.3164 | 4.3791 | 4.4403 | 4.5001 | 4.5583 | 4.6152 | 4.6707 | 1683.7161 | 1869.2441 | 2019.2942 | 2164.0092 | 2304.5677 | 2436.2131 | 2560.4248 | 2678.1535 | 2789.3982 | 2894.9569
48 | PMA | Southern | TKR2 | Knights Rd 11 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0.059251 | 0.068351 | 0.079726 | 0.092454 | 0.10637 | 0.1196 | 0.13056 | 0.14133 | 0.15194 | 0.16204 | 0.17172 | 0.18103 | 0.18997 | 0.19858 | 0.20694 | 0.21529 | 0.22387 | 0.23256 | 0.24113 | 0.24951 | 0.25769 | 0.26559 | 0.27333 | 0.28092 | 0.28829 | 0.29558 | 0.30277 | 0.30979 | 0.31674 | 0.32363 | 0.33044 | 0.33717 | 0.34384 | 0.35044 | 0.35698 | 0.36346 | 0.36988 | 106.3701 | 119.6041 | 130.5555 | 141.3333 | 151.9433 | 162.0402 | 171.7219 | 181.0332 | 189.9701 | 198.5816
48 | PMA | Southern | CAZ | Cambridge | base | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.21308 | 0.24943 | 0.29203 | 0.34484 | 0.41248 | 0.4744 | 0.52243 | 0.56958 | 0.61577 | 0.65969 | 0.70169 | 0.74198 | 0.78058 | 0.81769 | 0.85363 | 0.88944 | 0.9262 | 0.96333 | 0.99984 | 1.0355 | 1.0702 | 1.1036 | 1.1364 | 1.1683 | 1.1994 | 1.23 | 1.2601 | 1.2894 | 1.3184 | 1.3471 | 1.3754 | 1.4033 | 1.4308 | 1.458 | 1.485 | 1.5116 | 1.5379 | 412.4758 | 474.404 | 522.4339 | 569.5839 | 615.7718 | 659.6932 | 701.6852 | 741.9845 | 780.5843 | 817.6923
51 | PMA | Southern | EHZ | East Hobart | base | maximum | Battery | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0 | 0 | 0 | 0 | 0 | 0.00024612 | 0.00054165 | 0.00088445 | 0.0010909 | 0.0013644 | 0.0017975 | 0.0024885 | 0.0030761 | 0.0043861 | 0.0058739 | 0.0075406 | 0.0094136 | 0.011503 | 0.013812 | 0.01634 | 0.019089 | 0.022063 | 0.025234 | 0.028597 | 0.032154 | 0.035906 | 0.039777 | 0.043769 | 0.047881 | 0.052115 | 0.05647 | 0.060949 | 0.065551 | 0.070278 | 0.075089 | 0.079986 | 0.084967 | 0 | 0.24612 | 0.54165 | 0.88445 | 1.0909 | 1.3644 | 1.7975 | 2.4885 | 3.0761 | 4.3861
51 | PMA | Southern | GBZ | Geilston Bay | base | maximum | Battery | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0 | 0 | 0 | 0 | 0 | 0.0017655 | 0.005559 | 0.0093564 | 0.012111 | 0.016339 | 0.02225 | 0.032367 | 0.04047 | 0.058078 | 0.07828 | 0.10113 | 0.12707 | 0.15631 | 0.18892 | 0.22499 | 0.26459 | 0.30783 | 0.35437 | 0.40418 | 0.45734 | 0.51394 | 0.57284 | 0.63409 | 0.69773 | 0.76381 | 0.83238 | 0.90349 | 0.97721 | 1.0536 | 1.132 | 1.2125 | 1.295 | 0 | 1.7655 | 5.559 | 9.3564 | 12.1106 | 16.3387 | 22.2497 | 32.3673 | 40.4698 | 58.0778
51 | PMA | Southern | GRZ | Gretna | base | maximum | Battery | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0 | 0 | 0 | 0 | 0 | 4.6565e-05 | 0.00010625 | 0.00018145 | 0.0002298 | 0.00030733 | 0.0004057 | 0.00057345 | 0.00071348 | 0.0010187 | 0.0013672 | 0.0017596 | 0.0022029 | 0.0026999 | 0.0032513 | 0.0038579 | 0.0045206 | 0.0052403 | 0.0060109 | 0.0068313 | 0.0077024 | 0.0086249 | 0.0095801 | 0.010568 | 0.01159 | 0.012646 | 0.013736 | 0.01486 | 0.01602 | 0.017216 | 0.018437 | 0.019684 | 0.020956 | 0 | 0.046565 | 0.10625 | 0.18145 | 0.2298 | 0.30733 | 0.4057 | 0.57345 | 0.71348 | 1.0187
51 | PMA | Southern | HOZ | Howrah | base | maximum | Battery | non-coincident | POE50 | summer | zone | zone plus embedded | MW | 0 | Zs | 0 | 0 | 0 | 0 | 0 | 0.0020148 | 0.0063739 | 0.010739 | 0.0139 | 0.018735 | 0.025517 | 0.037139 | 0.046434 | 0.066638 | 0.089814 | 0.11603 | 0.14578 | 0.1793 | 0.21669 | 0.25802 | 0.30341 | 0.35295 | 0.40627 | 0.46331 | 0.52418 | 0.58898 | 0.65639 | 0.72648 | 0.79929 | 0.87488 | 0.9533 | 1.0346 | 1.1189 | 1.2062 | 1.2958 | 1.3877 | 1.482 | 0 | 2.0148 | 6.3739 | 10.7395 | 13.9 | 18.7346 | 25.5171 | 37.1385 | 46.4343 | 66.6378
51 | PMA | Southern | NTZ | New Town | base | maximum | Battery | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0 | 0 | 0 | 0 | 0 | 0.0022529 | 0.0048252 | 0.0076953 | 0.0099002 | 0.012669 | 0.016815 | 0.023502 | 0.029667 | 0.043078 | 0.058365 | 0.075537 | 0.094891 | 0.11654 | 0.14049 | 0.16678 | 0.19542 | 0.22644 | 0.25957 | 0.29475 | 0.33199 | 0.37133 | 0.41196 | 0.45388 | 0.49711 | 0.54165 | 0.58752 | 0.63472 | 0.68326 | 0.73317 | 0.784 | 0.83577 | 0.88848 | 0 | 2.2529 | 4.8252 | 7.6953 | 9.9002 | 12.6687 | 16.815 | 23.5018 | 29.6674 | 43.0784
51 | PMA | Southern | RIZ | Richmond | base | maximum | Battery | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0 | 0 | 0 | 0 | 0 | 0.00049651 | 0.0013642 | 0.002303 | 0.0030612 | 0.0040928 | 0.0055333 | 0.007859 | 0.0099257 | 0.014324 | 0.019367 | 0.025064 | 0.03152 | 0.03878 | 0.046858 | 0.055769 | 0.065526 | 0.076148 | 0.087549 | 0.099712 | 0.11266 | 0.12639 | 0.14065 | 0.15543 | 0.17074 | 0.1866 | 0.20301 | 0.21998 | 0.23753 | 0.25566 | 0.27422 | 0.29322 | 0.31267 | 0 | 0.49651 | 1.3642 | 2.303 | 3.0612 | 4.0928 | 5.5333 | 7.859 | 9.9257 | 14.3241
51 | PMA | Southern | RPZ | Rosny Park | base | maximum | Battery | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0 | 0 | 0 | 0 | 0 | 0.001236 | 0.0039104 | 0.0065887 | 0.0085277 | 0.011494 | 0.015655 | 0.022785 | 0.028488 | 0.040883 | 0.055101 | 0.071182 | 0.089436 | 0.11 | 0.13294 | 0.1583 | 0.18614 | 0.21654 | 0.24925 | 0.28424 | 0.32159 | 0.36134 | 0.4027 | 0.4457 | 0.49037 | 0.53675 | 0.58486 | 0.63475 | 0.68645 | 0.74001 | 0.79498 | 0.85137 | 0.90922 | 0 | 1.236 | 3.9104 | 6.5887 | 8.5277 | 11.4938 | 15.6549 | 22.7849 | 28.4879 | 40.8828
51 | PMA | Southern | SBZ | Sandy Bay | base | maximum | Battery | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0 | 0 | 0 | 0 | 0 | 0.0043081 | 0.010311 | 0.017079 | 0.021252 | 0.026731 | 0.034948 | 0.048408 | 0.060091 | 0.085941 | 0.11538 | 0.14843 | 0.18566 | 0.22731 | 0.27342 | 0.32404 | 0.37922 | 0.43903 | 0.50297 | 0.57093 | 0.64295 | 0.71911 | 0.79785 | 0.87921 | 0.9632 | 1.0499 | 1.1392 | 1.2313 | 1.3261 | 1.4237 | 1.5232 | 1.6247 | 1.7282 | 0 | 4.3081 | 10.3108 | 17.0793 | 21.2519 | 26.7313 | 34.9475 | 48.4076 | 60.0909 | 85.9414
51 | PMA | Southern | SUZ | Summerleas Road | base | maximum | Battery | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0 | 0 | 0 | 0 | 0 | 0.0013928 | 0.0045151 | 0.007797 | 0.009941 | 0.012699 | 0.016261 | 0.022554 | 0.028322 | 0.040839 | 0.055185 | 0.071392 | 0.089767 | 0.11045 | 0.13348 | 0.15891 | 0.1868 | 0.2172 | 0.24987 | 0.28478 | 0.32198 | 0.36152 | 0.40261 | 0.44527 | 0.48953 | 0.53541 | 0.58295 | 0.63218 | 0.68313 | 0.73583 | 0.78984 | 0.84519 | 0.90188 | 0 | 1.3928 | 4.5151 | 7.797 | 9.941 | 12.6992 | 16.2606 | 22.5542 | 28.3218 | 40.8393
51 | PMA | Southern | TWY2 | Wayatinah | base | maximum | Battery | non-coincident | POE50 | summer | zone | zone | MW | 0 | RT | 0 | 0 | 0 | 0 | 4.5648e-06 | 2.7764e-05 | 6.3353e-05 | 0.00010819 | 0.00013702 | 0.00018325 | 0.00024191 | 0.00034193 | 0.00042541 | 0.00060737 | 0.00081518 | 0.0010491 | 0.0013134 | 0.0016097 | 0.0019385 | 0.0023002 | 0.0026953 | 0.0031243 | 0.0035838 | 0.0040729 | 0.0045923 | 0.0051423 | 0.0057118 | 0.0063011 | 0.0069102 | 0.0075396 | 0.0081894 | 0.0088599 | 0.0095514 | 0.010264 | 0.010992 | 0.011736 | 0.012495 | 0.0045648 | 0.027764 | 0.063353 | 0.10819 | 0.13702 | 0.18325 | 0.24191 | 0.34193 | 0.42541 | 0.60737
51 | PMA | Southern | WHZ | West Hobart Zone | base | maximum | Battery | non-coincident | POE50 | summer | zone | zone plus embedded | MW | 0 | Zs | 0 | 0 | 0 | 0 | 0 | 0.0036555 | 0.0083445 | 0.013713 | 0.016982 | 0.021293 | 0.027955 | 0.038711 | 0.047943 | 0.068454 | 0.091777 | 0.11793 | 0.14736 | 0.18022 | 0.21657 | 0.25641 | 0.2998 | 0.34676 | 0.39691 | 0.45014 | 0.50649 | 0.566 | 0.62747 | 0.6909 | 0.75631 | 0.82372 | 0.89314 | 0.96459 | 1.0381 | 1.1137 | 1.1907 | 1.2691 | 1.349 | 0 | 3.6555 | 8.3445 | 13.7133 | 16.9817 | 21.2932 | 27.955 | 38.7113 | 47.9434 | 68.4539
51 | PMA | Western | THZ | Trial Harbour | base | maximum | Battery | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0 | 0 | 0 | 0 | 0 | 7.7555e-05 | 0.00016114 | 0.00038565 | 0.00053461 | 0.00072331 | 0.0013182 | 0.0019946 | 0.0023058 | 0.0031063 | 0.004003 | 0.004997 | 0.0061037 | 0.0073293 | 0.0086756 | 0.010144 | 0.011737 | 0.013455 | 0.015286 | 0.017227 | 0.01928 | 0.021446 | 0.023684 | 0.025994 | 0.028379 | 0.030837 | 0.03337 | 0.03598 | 0.038667 | 0.041432 | 0.044252 | 0.047129 | 0.050063 | 0 | 0.077555 | 0.16114 | 0.38565 | 0.53461 | 0.72331 | 1.3182 | 1.9946 | 2.3058 | 3.1063
51 | PMA | Western | RBZ | Rosebery 22 kV | base | maximum | Battery | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0 | 0 | 0 | 0 | 8.151e-05 | 0.00024647 | 0.00053498 | 0.001128 | 0.0015649 | 0.0020659 | 0.0034959 | 0.005189 | 0.006089 | 0.0082944 | 0.010774 | 0.01353 | 0.016605 | 0.020016 | 0.023766 | 0.027858 | 0.032295 | 0.037083 | 0.042182 | 0.047582 | 0.053288 | 0.059303 | 0.06551 | 0.071911 | 0.078506 | 0.085297 | 0.092287 | 0.099476 | 0.10687 | 0.11446 | 0.1222 | 0.13008 | 0.1381 | 0.08151 | 0.24647 | 0.53498 | 1.128 | 1.5649 | 2.0659 | 3.4959 | 5.189 | 6.089 | 8.2944
51 | PMA | total terminal |  | total terminal | base | maximum | Battery | non-coincident | POE50 | summer | zone | zone | MW | #N/A | #N/A | 0 | 0 | 0 | 0 | 0.034477 | 0.13522 | 0.36171 | 0.59079 | 0.76773 | 0.9714 | 1.2718 | 1.7376 | 2.1838 | 3.1373 | 4.2291 | 5.4608 | 6.8548 | 8.4204 | 10.1601 | 12.0764 | 14.1722 | 16.4506 | 18.8928 | 21.4948 | 24.26 | 27.1912 | 30.2285 | 33.3733 | 36.6271 | 39.9914 | 43.4678 | 47.0579 | 50.7638 | 54.5872 | 58.4955 | 62.49 | 66.572 | 34.4766 | 135.2206 | 361.7143 | 590.7933 | 767.7301 | 971.3984 | 1271.8127 | 1737.6419 | 2183.7667 | 3137.2872
51 | PMA | total zone |  | total zone | base | maximum | Battery | non-coincident | POE50 | summer | zone | zone | MW | #N/A | #N/A | 0 | 0 | 0 | 0 | 8.6075e-05 | 0.02292 | 0.059521 | 0.098911 | 0.12669 | 0.16511 | 0.22128 | 0.31415 | 0.39276 | 0.56453 | 0.76087 | 0.98211 | 1.2323 | 1.5131 | 1.8251 | 2.1688 | 2.5447 | 2.9535 | 3.3919 | 3.8592 | 4.3561 | 4.8832 | 5.4298 | 5.9961 | 6.5824 | 7.1891 | 7.8165 | 8.4649 | 9.1346 | 9.8261 | 10.5334 | 11.2569 | 11.9967 | 0.086075 | 22.9196 | 59.5206 | 98.9109 | 126.6913 | 165.1057 | 221.2756 | 314.1497 | 392.7553 | 564.5317
48 | PMA | George Town | TC01 | Comalco | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Camalco | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | George Town | TSW1 | Starwood | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Starwood | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | George Town | TTE1 | Temco | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Temco | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | North | TAL2 | Ax-Arthurs Lake 6.6 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | Ax | 0.00034908 | 0.00039755 | 0.00047542 | 0.00056389 | 0.00065009 | 0.000726 | 0.00078782 | 0.00085016 | 0.00091273 | 0.00097487 | 0.001037 | 0.0010993 | 0.0011619 | 0.0012246 | 0.0012888 | 0.0013554 | 0.0014246 | 0.0014955 | 0.0015663 | 0.0016364 | 0.0017055 | 0.0017734 | 0.0018412 | 0.0019087 | 0.0019753 | 0.0020423 | 0.0021094 | 0.0021762 | 0.0022436 | 0.0023114 | 0.0023797 | 0.0024485 | 0.0025177 | 0.0025876 | 0.0026579 | 0.0027289 | 0.0028004 | 0.65009 | 0.726 | 0.78782 | 0.85016 | 0.91273 | 0.97487 | 1.037 | 1.0993 | 1.1619 | 1.2246
48 | PMA | North | TAV2 | Avoca 22 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0.11792 | 0.14942 | 0.17489 | 0.19931 | 0.23006 | 0.26458 | 0.29766 | 0.33101 | 0.36408 | 0.39672 | 0.42909 | 0.46132 | 0.49347 | 0.52536 | 0.55783 | 0.5912 | 0.62564 | 0.66066 | 0.6953 | 0.72934 | 0.76266 | 0.79511 | 0.82724 | 0.85896 | 0.89 | 0.92096 | 0.9517 | 0.98206 | 1.0124 | 1.0427 | 1.0729 | 1.1031 | 1.1332 | 1.1633 | 1.1934 | 1.2235 | 1.2535 | 230.0605 | 264.5789 | 297.6622 | 331.006 | 364.0789 | 396.7152 | 429.0859 | 461.3166 | 493.4705 | 525.3624
48 | PMA | North | TDE2 | Derby 22 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0.33085 | 0.3803 | 0.44369 | 0.5035 | 0.57021 | 0.63994 | 0.7054 | 0.77098 | 0.83525 | 0.8981 | 0.9599 | 1.0207 | 1.0808 | 1.1399 | 1.1993 | 1.2599 | 1.3217 | 1.3839 | 1.4449 | 1.5042 | 1.5618 | 1.6172 | 1.6716 | 1.7248 | 1.7763 | 1.8272 | 1.8772 | 1.9262 | 1.9746 | 2.0226 | 2.07 | 2.1168 | 2.1632 | 2.2091 | 2.2545 | 2.2995 | 2.344 | 570.2145 | 639.9426 | 705.3971 | 770.9849 | 835.2516 | 898.1035 | 959.9018 | 1020.7374 | 1080.847 | 1139.8649
48 | PMA | North | THA3 | Hadspen 22 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 2.9419 | 3.5359 | 4.1462 | 4.8132 | 5.6062 | 6.4405 | 7.2775 | 8.1156 | 8.9444 | 9.7607 | 10.5679 | 11.3697 | 12.1672 | 12.9562 | 13.7571 | 14.5783 | 15.4232 | 16.2802 | 17.1258 | 17.9542 | 18.7631 | 19.5487 | 20.3242 | 21.088 | 21.8334 | 22.5748 | 23.309 | 24.032 | 24.7525 | 25.4701 | 26.1845 | 26.8955 | 27.6036 | 28.3091 | 29.012 | 29.7123 | 30.41 | 5606.1559 | 6440.5326 | 7277.4532 | 8115.5615 | 8944.3936 | 9760.7355 | 10567.8906 | 11369.6502 | 12167.239 | 12956.1578
48 | PMA | North | TMY2 | Mowbray 22 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0.9257 | 1.1315 | 1.351 | 1.5707 | 1.7877 | 1.9794 | 2.1665 | 2.3519 | 2.535 | 2.714 | 2.8901 | 3.0641 | 3.2362 | 3.4055 | 3.5765 | 3.7508 | 3.9291 | 4.109 | 4.2856 | 4.4575 | 4.6246 | 4.7858 | 4.9441 | 5.0992 | 5.2497 | 5.3985 | 5.545 | 5.6885 | 5.8306 | 5.9714 | 6.1108 | 6.2487 | 6.3852 | 6.5205 | 6.6545 | 6.7872 | 6.9186 | 1787.6644 | 1979.4335 | 2166.4847 | 2351.8779 | 2535.0288 | 2714.0391 | 2890.0886 | 3064.112 | 3236.2179 | 3405.5324
48 | PMA | North | TPM3 | Palmerston 22 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | North | TSD2 | Scottsdale 22 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0.68795 | 0.77766 | 0.89744 | 1.0187 | 1.1469 | 1.2818 | 1.4111 | 1.5402 | 1.667 | 1.7911 | 1.9131 | 2.0334 | 2.1524 | 2.2693 | 2.3872 | 2.5073 | 2.6301 | 2.7539 | 2.8752 | 2.9934 | 3.1081 | 3.2187 | 3.3273 | 3.4336 | 3.5367 | 3.6386 | 3.7389 | 3.8371 | 3.9344 | 4.0308 | 4.1261 | 4.2205 | 4.3139 | 4.4065 | 4.4982 | 4.5891 | 4.6791 | 1146.8519 | 1281.8409 | 1411.0618 | 1540.1924 | 1666.9784 | 1791.0514 | 1913.1177 | 2033.4258 | 2152.3861 | 2269.2954
48 | PMA | North | TSL2 | St Leonards 22 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 1.3143 | 1.5404 | 1.8154 | 2.142 | 2.4471 | 2.7012 | 2.9493 | 3.1952 | 3.4382 | 3.6757 | 3.9092 | 4.1401 | 4.3685 | 4.5932 | 4.82 | 5.0514 | 5.2881 | 5.5269 | 5.7612 | 5.9896 | 6.2113 | 6.4255 | 6.6357 | 6.8416 | 7.0415 | 7.2391 | 7.4338 | 7.6244 | 7.8133 | 8.0003 | 8.1855 | 8.3687 | 8.5502 | 8.73 | 8.9081 | 9.0845 | 9.2593 | 2447.1146 | 2701.2337 | 2949.3201 | 3195.2363 | 3438.177 | 3675.6559 | 3909.2226 | 4140.1175 | 4368.4868 | 4593.1691
48 | PMA | North | TSL3 | St Leonards 22 kV (scheduled load) | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Firmus Grid | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | North | TSM2 | St Marys 22 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0.94174 | 1.1809 | 1.4436 | 1.6677 | 1.8986 | 2.0865 | 2.2465 | 2.4066 | 2.5656 | 2.7211 | 2.8746 | 3.0267 | 3.1776 | 3.3264 | 3.4771 | 3.6312 | 3.7894 | 3.9493 | 4.1067 | 4.2606 | 4.4104 | 4.5555 | 4.6984 | 4.8387 | 4.9753 | 5.1108 | 5.2446 | 5.3761 | 5.5068 | 5.6365 | 5.7654 | 5.8934 | 6.0204 | 6.1467 | 6.2722 | 6.3969 | 6.5209 | 1898.6453 | 2086.4955 | 2246.545 | 2406.5867 | 2565.6267 | 2721.0932 | 2874.592 | 3026.7091 | 3177.5624 | 3326.4117
48 | PMA | Northwest | TDP2 | Devonport 22 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 1.8825 | 2.1757 | 2.5355 | 2.9784 | 3.4472 | 3.8448 | 4.1951 | 4.5439 | 4.8893 | 5.2282 | 5.5626 | 5.8941 | 6.2229 | 6.5473 | 6.8759 | 7.212 | 7.5569 | 7.9059 | 8.2494 | 8.5851 | 8.9121 | 9.2289 | 9.5409 | 9.8474 | 10.1457 | 10.4418 | 10.7342 | 11.0215 | 11.3071 | 11.5909 | 11.8726 | 12.1524 | 12.4304 | 12.7067 | 12.9813 | 13.2542 | 13.5254 | 3447.1559 | 3844.8331 | 4195.0594 | 4543.9051 | 4889.3045 | 5228.203 | 5562.6477 | 5894.0552 | 6222.8714 | 6547.3466
48 | PMA | Northwest | TEB2 | Emu Bay 11 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Emu Bay | MI | 0.13673 | 0.16675 | 0.19871 | 0.23161 | 0.26569 | 0.29454 | 0.31665 | 0.33838 | 0.35992 | 0.38078 | 0.40121 | 0.4213 | 0.44106 | 0.4604 | 0.47982 | 0.49952 | 0.51957 | 0.53969 | 0.55934 | 0.57837 | 0.59676 | 0.61442 | 0.63167 | 0.64847 | 0.6647 | 0.68065 | 0.69629 | 0.71151 | 0.72652 | 0.7413 | 0.75586 | 0.77019 | 0.7843 | 0.79821 | 0.81192 | 0.82542 | 0.83872 | 265.6896 | 294.5358 | 316.6524 | 338.3779 | 359.9169 | 380.775 | 401.205 | 421.2965 | 441.0566 | 460.398
48 | PMA | Northwest | THM2 | Hampshire | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Hampshire | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Northwest | TPL2 | Port Latta | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | Port Latta | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Northwest | TRA2 | Railton 22 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Northwest | TSH3 | Sheffield | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Northwest | TST2 | Smithton 22 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0.11298 | 0.13907 | 0.1642 | 0.18346 | 0.21361 | 0.25031 | 0.28924 | 0.32855 | 0.36653 | 0.40384 | 0.44034 | 0.47614 | 0.51143 | 0.54594 | 0.58061 | 0.61578 | 0.65157 | 0.68749 | 0.72255 | 0.75654 | 0.78937 | 0.8209 | 0.85171 | 0.88171 | 0.91068 | 0.93918 | 0.9671 | 0.99429 | 1.0211 | 1.0475 | 1.0735 | 1.0991 | 1.1243 | 1.1492 | 1.1737 | 1.1978 | 1.2216 | 213.6084 | 250.3066 | 289.2431 | 328.5539 | 366.5325 | 403.8407 | 440.3413 | 476.1373 | 511.4276 | 545.9435
48 | PMA | Northwest | TUL2 | Ulverstone 22 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 2.3973 | 2.7385 | 3.152 | 3.6105 | 4.1227 | 4.6024 | 5.0157 | 5.4259 | 5.8311 | 6.2274 | 6.617 | 7.0018 | 7.3824 | 7.7566 | 8.1342 | 8.5192 | 8.9129 | 9.3099 | 9.6993 | 10.0785 | 10.4467 | 10.802 | 11.1507 | 11.4921 | 11.8233 | 12.1507 | 12.473 | 12.7884 | 13.1009 | 13.4102 | 13.7162 | 14.0189 | 14.3186 | 14.6153 | 14.9091 | 15.2001 | 15.4881 | 4122.7459 | 4602.4241 | 5015.6745 | 5425.9173 | 5831.1119 | 6227.4053 | 6616.9844 | 7001.8209 | 7382.3667 | 7756.573
48 | PMA | Northwest | TWV2 | Wesley Vale 11 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | Wesley Vale | MI | 0.36594 | 0.43045 | 0.52262 | 0.62956 | 0.73572 | 0.83489 | 0.93107 | 1.028 | 1.1248 | 1.2211 | 1.3171 | 1.4135 | 1.5101 | 1.6066 | 1.7055 | 1.8077 | 1.9139 | 2.0226 | 2.1308 | 2.2377 | 2.3431 | 2.4464 | 2.5493 | 2.6515 | 2.7522 | 2.8532 | 2.9542 | 3.0545 | 3.1554 | 3.2567 | 3.3586 | 3.4608 | 3.5636 | 3.6669 | 3.7707 | 3.8751 | 3.98 | 735.7172 | 834.8863 | 931.0746 | 1027.9644 | 1124.7992 | 1221.0765 | 1317.1389 | 1413.4503 | 1510.1082 | 1606.6015
48 | PMA | Southern | TBW2 | Bridgewater 11 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 1.6264 | 1.8376 | 2.1832 | 2.5897 | 2.9765 | 3.3107 | 3.5834 | 3.8584 | 4.1346 | 4.4091 | 4.6836 | 4.9594 | 5.2366 | 5.514 | 5.7987 | 6.0939 | 6.4011 | 6.7162 | 7.0305 | 7.3421 | 7.6498 | 7.952 | 8.2539 | 8.5546 | 8.8515 | 9.1503 | 9.4497 | 9.748 | 10.0488 | 10.352 | 10.6574 | 10.965 | 11.275 | 11.5877 | 11.9029 | 12.2208 | 12.5414 | 2976.5082 | 3310.7254 | 3583.3509 | 3858.3889 | 4134.6013 | 4409.1277 | 4683.6234 | 4959.3899 | 5236.6371 | 5513.9944
48 | PMA | Southern | TBYA | Boyer SWA | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Boyer | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Southern | TBYB | Boyer SWB | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Boyer | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Southern | TCR2 | Creek Rd 33 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 2.5047 | 2.8775 | 3.3595 | 3.9287 | 4.5711 | 5.1782 | 5.6817 | 6.1816 | 6.6778 | 7.165 | 7.646 | 8.1234 | 8.5975 | 9.0658 | 9.5407 | 10.0269 | 10.5265 | 11.0325 | 11.5311 | 12.019 | 12.4947 | 12.956 | 13.4109 | 13.8583 | 14.2942 | 14.7273 | 15.1555 | 15.5767 | 15.9959 | 16.4128 | 16.8272 | 17.2391 | 17.6488 | 18.0564 | 18.462 | 18.8656 | 19.267 | 4571.1244 | 5178.2437 | 5681.6821 | 6181.6139 | 6677.8458 | 7164.952 | 7645.9676 | 8123.3743 | 8597.4674 | 9065.8376
48 | PMA | Southern | TCS3 | Chapel St 11 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 1.0991 | 1.249 | 1.4605 | 1.7133 | 1.993 | 2.2788 | 2.5304 | 2.7792 | 3.026 | 3.2681 | 3.507 | 3.744 | 3.9792 | 4.2114 | 4.4467 | 4.6873 | 4.9345 | 5.1846 | 5.4309 | 5.6718 | 5.9064 | 6.1338 | 6.3578 | 6.5779 | 6.7923 | 7.0051 | 7.2153 | 7.4219 | 7.6273 | 7.8314 | 8.0342 | 8.2355 | 8.4356 | 8.6345 | 8.8322 | 9.0287 | 9.2241 | 1993.0181 | 2278.8396 | 2530.4072 | 2779.1957 | 3025.9875 | 3268.11 | 3507.0442 | 3744.0476 | 3979.2236 | 4211.4122
48 | PMA | Southern | TDB2 | Derwent Bridge 22 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0.0058532 | 0.0066611 | 0.0076296 | 0.0087712 | 0.010051 | 0.011264 | 0.012248 | 0.01323 | 0.014205 | 0.015166 | 0.016117 | 0.017063 | 0.018005 | 0.018938 | 0.019885 | 0.020858 | 0.02186 | 0.022877 | 0.023882 | 0.024868 | 0.025831 | 0.026768 | 0.027693 | 0.028606 | 0.029497 | 0.030384 | 0.031264 | 0.032132 | 0.032997 | 0.03386 | 0.034719 | 0.035576 | 0.03643 | 0.037282 | 0.038131 | 0.038979 | 0.039824 | 10.0513 | 11.2637 | 12.2484 | 13.23 | 14.2054 | 15.1664 | 16.1173 | 17.0633 | 18.005 | 18.9376
48 | PMA | Southern | TEL2 | Electrona 11 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0.27974 | 0.31639 | 0.3626 | 0.41424 | 0.46876 | 0.52486 | 0.57397 | 0.6231 | 0.67206 | 0.72045 | 0.76852 | 0.8165 | 0.86444 | 0.91208 | 0.96067 | 1.0107 | 1.0624 | 1.1151 | 1.1674 | 1.2188 | 1.2692 | 1.3183 | 1.3671 | 1.4154 | 1.4626 | 1.5099 | 1.5569 | 1.6034 | 1.6499 | 1.6964 | 1.7429 | 1.7895 | 1.836 | 1.8825 | 1.9291 | 1.9757 | 2.0223 | 468.7614 | 524.8559 | 573.9674 | 623.1045 | 672.0618 | 720.4527 | 768.5177 | 816.5048 | 864.4414 | 912.0817
48 | PMA | Southern | THR2 | Huon River | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Huon River | MI | 0.00077139 | 0.00089743 | 0.0010512 | 0.0012212 | 0.0014093 | 0.0015924 | 0.0017492 | 0.0019071 | 0.0020654 | 0.0022223 | 0.0023788 | 0.0025357 | 0.0026929 | 0.0028498 | 0.0030104 | 0.0031764 | 0.0033486 | 0.0035247 | 0.0036998 | 0.0038729 | 0.0040432 | 0.00421 | 0.004376 | 0.0045408 | 0.0047029 | 0.0048655 | 0.0050278 | 0.0051889 | 0.0053508 | 0.0055133 | 0.0056764 | 0.0058401 | 0.0060043 | 0.0061693 | 0.006335 | 0.0065014 | 0.0066685 | 1.4093 | 1.5924 | 1.7492 | 1.9071 | 2.0654 | 2.2223 | 2.3788 | 2.5357 | 2.6929 | 2.8498
48 | PMA | Southern | TK12 | Kingston 11 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 1.7336 | 1.9837 | 2.3406 | 2.7539 | 3.1976 | 3.6129 | 3.9774 | 4.3421 | 4.7055 | 5.0648 | 5.4216 | 5.7779 | 6.1338 | 6.4876 | 6.8485 | 7.2202 | 7.6044 | 7.9958 | 8.3838 | 8.7657 | 9.1403 | 9.5057 | 9.8681 | 10.2266 | 10.5781 | 10.9292 | 11.2785 | 11.624 | 11.9699 | 12.3158 | 12.6618 | 13.0076 | 13.3536 | 13.6997 | 14.0462 | 14.3928 | 14.7396 | 3197.5977 | 3612.887 | 3977.4075 | 4342.1369 | 4705.5296 | 5064.7637 | 5421.604 | 5777.8997 | 6133.8497 | 6487.6286
48 | PMA | Southern | TK13 | Kingston 33 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Southern | TKE2 | Kermandie 11 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0.20696 | 0.24483 | 0.28985 | 0.33256 | 0.38333 | 0.43277 | 0.4751 | 0.51772 | 0.56044 | 0.6028 | 0.64507 | 0.68742 | 0.72989 | 0.77227 | 0.81565 | 0.8605 | 0.90704 | 0.95463 | 1.002 | 1.0488 | 1.0948 | 1.1399 | 1.1848 | 1.2294 | 1.2732 | 1.3172 | 1.3611 | 1.4047 | 1.4486 | 1.4926 | 1.5367 | 1.581 | 1.6255 | 1.6702 | 1.715 | 1.7601 | 1.8054 | 383.3308 | 432.7709 | 475.0972 | 517.7204 | 560.438 | 602.8041 | 645.0736 | 687.4226 | 729.8944 | 772.2698
48 | PMA | Southern | TLF2 | Lindisfarne 33 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 1.3376 | 1.5206 | 1.7944 | 2.1302 | 2.515 | 2.8773 | 3.1688 | 3.4615 | 3.7535 | 4.0429 | 4.3307 | 4.6186 | 4.9067 | 5.1935 | 5.4865 | 5.7888 | 6.1018 | 6.4213 | 6.7384 | 7.0511 | 7.3583 | 7.6585 | 7.9567 | 8.2522 | 8.5424 | 8.8327 | 9.1221 | 9.4088 | 9.6962 | 9.9843 | 10.2728 | 10.5617 | 10.8511 | 11.1413 | 11.4321 | 11.7237 | 12.0159 | 2514.981 | 2877.3266 | 3168.7786 | 3461.5128 | 3753.4964 | 4042.8575 | 4330.7461 | 4618.5853 | 4906.6903 | 5193.4974
48 | PMA | Southern | TMB2 | Meadowbank 22 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Southern | TMT2 | Mornington 33 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 1.8847 | 2.1391 | 2.5251 | 3.0197 | 3.6003 | 4.1399 | 4.5736 | 5.0092 | 5.4434 | 5.8737 | 6.3016 | 6.7293 | 7.1572 | 7.5831 | 8.0181 | 8.4668 | 8.9312 | 9.4049 | 9.8751 | 10.3385 | 10.7936 | 11.2382 | 11.6797 | 12.1171 | 12.5464 | 12.9759 | 13.4036 | 13.8274 | 14.2521 | 14.6775 | 15.1034 | 15.5297 | 15.9568 | 16.3847 | 16.8134 | 17.243 | 17.6734 | 3600.2687 | 4139.9041 | 4573.6461 | 5009.1787 | 5443.4315 | 5873.6675 | 6301.5803 | 6729.2815 | 7157.2482 | 7583.1493
48 | PMA | Southern | TNH2 | North Hobart 11 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0.45368 | 0.51946 | 0.59562 | 0.68753 | 0.80086 | 0.90562 | 0.98899 | 1.0717 | 1.1538 | 1.2341 | 1.3133 | 1.3918 | 1.4696 | 1.5463 | 1.6239 | 1.7032 | 1.7846 | 1.8668 | 1.9477 | 2.0267 | 2.1036 | 2.178 | 2.2512 | 2.3231 | 2.393 | 2.4622 | 2.5306 | 2.5977 | 2.6644 | 2.7305 | 2.7961 | 2.8612 | 2.9258 | 2.99 | 3.0536 | 3.1169 | 3.1796 | 800.8598 | 905.6161 | 988.9926 | 1071.7342 | 1153.7735 | 1234.1302 | 1313.3419 | 1391.8128 | 1469.5996 | 1546.3023
48 | PMA | Southern | TNN2 | New Norfolk 22 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | Brynn Estyn | MI | 0.14705 | 0.1672 | 0.19176 | 0.22064 | 0.25275 | 0.28307 | 0.30769 | 0.33225 | 0.35667 | 0.38073 | 0.40455 | 0.42826 | 0.45188 | 0.47527 | 0.49906 | 0.52349 | 0.54867 | 0.57424 | 0.59951 | 0.6243 | 0.64856 | 0.67214 | 0.69547 | 0.71848 | 0.74097 | 0.76337 | 0.78559 | 0.80752 | 0.8294 | 0.85123 | 0.87299 | 0.8947 | 0.91634 | 0.93795 | 0.95951 | 0.98103 | 1.0025 | 252.7541 | 283.0655 | 307.6887 | 332.2479 | 356.665 | 380.7292 | 404.5507 | 428.2614 | 451.8768 | 475.2732
48 | PMA | Southern | TR13 | Risdon 11 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Risdon | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Southern | TR14 | Risdon 33 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0.91939 | 1.0443 | 1.201 | 1.4 | 1.6372 | 1.8611 | 2.0523 | 2.2418 | 2.4299 | 2.6144 | 2.7966 | 2.9773 | 3.1568 | 3.334 | 3.5136 | 3.6975 | 3.8864 | 4.0776 | 4.266 | 4.4503 | 4.6299 | 4.8041 | 4.9758 | 5.1446 | 5.309 | 5.4723 | 5.6338 | 5.7926 | 5.9505 | 6.1075 | 6.2636 | 6.4187 | 6.5729 | 6.7263 | 6.8789 | 7.0307 | 7.1817 | 1637.2424 | 1861.099 | 2052.346 | 2241.8197 | 2429.8636 | 2614.3943 | 2796.5647 | 2977.3224 | 3156.7618 | 3333.9881
48 | PMA | Southern | TRK2 | Rokeby 11 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 1.607 | 1.8442 | 2.1931 | 2.634 | 3.157 | 3.6358 | 4.0206 | 4.407 | 4.7922 | 5.1739 | 5.5535 | 5.9329 | 6.3125 | 6.6903 | 7.0762 | 7.4741 | 7.886 | 8.3062 | 8.7232 | 9.1342 | 9.5379 | 9.9321 | 10.3237 | 10.7116 | 11.0923 | 11.4731 | 11.8524 | 12.2282 | 12.6047 | 12.9819 | 13.3596 | 13.7376 | 14.1162 | 14.4955 | 14.8756 | 15.2565 | 15.638 | 3156.998 | 3635.7676 | 4020.5813 | 4406.9742 | 4792.2205 | 5173.8957 | 5553.5005 | 5932.9081 | 6312.5424 | 6690.3349
48 | PMA | Southern | TS02 | Sorell | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0.7646 | 0.89123 | 1.0632 | 1.2586 | 1.4781 | 1.6836 | 1.8501 | 2.0172 | 2.1844 | 2.3503 | 2.5156 | 2.6813 | 2.8475 | 3.0132 | 3.1828 | 3.3582 | 3.5402 | 3.7263 | 3.9115 | 4.0945 | 4.2746 | 4.4511 | 4.6268 | 4.8013 | 4.9731 | 5.1454 | 5.3175 | 5.4885 | 5.6604 | 5.833 | 6.0064 | 6.1805 | 6.3554 | 6.5311 | 6.7078 | 6.8854 | 7.0639 | 1478.1231 | 1683.6239 | 1850.1068 | 2017.1793 | 2184.367 | 2350.2871 | 2515.6231 | 2681.3225 | 2847.4537 | 3013.1728
48 | PMA | Southern | TTB2 | Triabunna 22 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0.15761 | 0.19624 | 0.23445 | 0.27077 | 0.31479 | 0.35086 | 0.37989 | 0.40901 | 0.43806 | 0.46674 | 0.49522 | 0.52364 | 0.55203 | 0.58022 | 0.60898 | 0.63858 | 0.66917 | 0.70032 | 0.73119 | 0.76157 | 0.79136 | 0.82041 | 0.84922 | 0.87771 | 0.90564 | 0.93353 | 0.96128 | 0.98872 | 1.0162 | 1.0437 | 1.0711 | 1.0986 | 1.1261 | 1.1535 | 1.181 | 1.2086 | 1.2361 | 314.7922 | 350.8629 | 379.8897 | 409.0089 | 438.0632 | 466.7396 | 495.2197 | 523.6427 | 552.026 | 580.2249
48 | PMA | Southern | TTU2 | Tungatinah 22 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0.041793 | 0.047521 | 0.054392 | 0.06249 | 0.071566 | 0.080161 | 0.087143 | 0.094102 | 0.10102 | 0.10783 | 0.11457 | 0.12128 | 0.12796 | 0.13457 | 0.14129 | 0.14818 | 0.15529 | 0.1625 | 0.16962 | 0.17661 | 0.18344 | 0.19008 | 0.19664 | 0.20311 | 0.20943 | 0.21572 | 0.22196 | 0.22811 | 0.23424 | 0.24036 | 0.24645 | 0.25253 | 0.25858 | 0.26462 | 0.27064 | 0.27665 | 0.28264 | 71.5658 | 80.1613 | 87.1425 | 94.1018 | 101.0176 | 107.8307 | 114.5718 | 121.2786 | 127.9554 | 134.5671
48 | PMA | Southern | TWA2 | Waddamana 22 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0.017701 | 0.02016 | 0.02411 | 0.028596 | 0.032973 | 0.036831 | 0.039975 | 0.043144 | 0.046325 | 0.049484 | 0.05264 | 0.055809 | 0.058993 | 0.062175 | 0.06544 | 0.068823 | 0.072341 | 0.075946 | 0.079541 | 0.083102 | 0.086617 | 0.090067 | 0.093511 | 0.096939 | 0.10032 | 0.10373 | 0.10713 | 0.11053 | 0.11395 | 0.11739 | 0.12086 | 0.12435 | 0.12787 | 0.13141 | 0.13499 | 0.13859 | 0.14222 | 32.9727 | 36.8312 | 39.9745 | 43.144 | 46.325 | 49.484 | 52.6404 | 55.8092 | 58.9927 | 62.1753
48 | PMA | Western | TGO2 | Gordon | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Western | TNT2 | Newton 22 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 7.924e-05 | 8.809e-05 | 9.9043e-05 | 0.00012121 | 0.00015005 | 0.00016831 | 0.00017874 | 0.00018913 | 0.00019944 | 0.00020958 | 0.00021959 | 0.00022954 | 0.00023943 | 0.00024921 | 0.00025912 | 0.00026929 | 0.00027974 | 0.00029033 | 0.00030077 | 0.00031099 | 0.00032097 | 0.00033066 | 0.00034021 | 0.00034961 | 0.00035879 | 0.0003679 | 0.00037692 | 0.0003858 | 0.00039464 | 0.00040344 | 0.00041219 | 0.0004209 | 0.00042956 | 0.00043819 | 0.00044678 | 0.00045533 | 0.00046384 | 0.15005 | 0.16831 | 0.17874 | 0.18913 | 0.19944 | 0.20958 | 0.21959 | 0.22954 | 0.23943 | 0.24921
48 | PMA | Western | TNT3 | Ax-Newton 11 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | Ax | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Western | TQT2 | Queenstown 22 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0.13383 | 0.14877 | 0.16727 | 0.2047 | 0.25342 | 0.28425 | 0.30187 | 0.31941 | 0.33682 | 0.35395 | 0.37087 | 0.38767 | 0.40437 | 0.42088 | 0.43763 | 0.45479 | 0.47244 | 0.49032 | 0.50796 | 0.52523 | 0.54208 | 0.55843 | 0.57457 | 0.59045 | 0.60594 | 0.62133 | 0.63657 | 0.65156 | 0.66649 | 0.68135 | 0.69614 | 0.71084 | 0.72547 | 0.74004 | 0.75455 | 0.76899 | 0.78336 | 253.4186 | 284.2483 | 301.8675 | 319.4145 | 336.8221 | 353.9467 | 370.8658 | 387.668 | 404.3687 | 420.8777
48 | PMA | Western | TQT3 | Queenstown 11 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Queenstown 11 kV | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Western | TQU2 | Que | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Que | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Western | TRB2 | Rosebery 44 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Rosebery | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Western | TSR2 | Savage River | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Savage River | MI | 0.048061 | 0.056142 | 0.065245 | 0.074328 | 0.085354 | 0.095533 | 0.10434 | 0.11309 | 0.12169 | 0.1301 | 0.13835 | 0.14647 | 0.15449 | 0.16237 | 0.17029 | 0.17836 | 0.18659 | 0.19487 | 0.20298 | 0.21086 | 0.21849 | 0.22585 | 0.23305 | 0.24009 | 0.2469 | 0.25362 | 0.26023 | 0.26668 | 0.27306 | 0.27936 | 0.28558 | 0.29173 | 0.2978 | 0.3038 | 0.30973 | 0.31559 | 0.32138 | 85.3539 | 95.5332 | 104.3439 | 113.0892 | 121.6936 | 130.0988 | 138.3456 | 146.4726 | 154.494 | 162.365
48 | PMA | Southern | BEZ | Bellerive | high | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.5472 | 0.6176 | 0.72902 | 0.87404 | 1.0437 | 1.2006 | 1.3266 | 1.4532 | 1.5793 | 1.7044 | 1.8287 | 1.953 | 2.0773 | 2.201 | 2.3274 | 2.4578 | 2.5927 | 2.7303 | 2.8669 | 3.0015 | 3.1337 | 3.2629 | 3.3911 | 3.5181 | 3.6428 | 3.7676 | 3.8918 | 4.0149 | 4.1382 | 4.2618 | 4.3855 | 4.5093 | 4.6333 | 4.7575 | 4.882 | 5.0068 | 5.1318 | 1043.7463 | 1200.5598 | 1326.5996 | 1453.1567 | 1579.3384 | 1704.3505 | 1828.6845 | 1952.9541 | 2077.298 | 2201.0388
48 | PMA | Southern | CLZ | Claremont | high | maximum | PV | non-coincident | POE50 | summer | zone | zone plus embedded | MW | 0 | Zs | 0.83836 | 0.95383 | 1.1451 | 1.3743 | 1.6135 | 1.8379 | 2.0358 | 2.2316 | 2.4261 | 2.6172 | 2.8059 | 2.9933 | 3.1794 | 3.3634 | 3.5501 | 3.7413 | 3.9378 | 4.137 | 4.3333 | 4.5256 | 4.7131 | 4.895 | 5.0745 | 5.2512 | 5.4234 | 5.5945 | 5.7639 | 5.9306 | 6.0965 | 6.2617 | 6.426 | 6.5894 | 6.752 | 6.9139 | 7.0751 | 7.2356 | 7.3953 | 1613.4777 | 1837.9342 | 2035.7678 | 2231.6445 | 2426.1368 | 2617.1621 | 2805.8784 | 2993.2745 | 3179.4324 | 3363.4367
48 | PMA | Southern | DPZ | Derwent Park | high | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.30994 | 0.35038 | 0.4067 | 0.4768 | 0.55388 | 0.62904 | 0.69491 | 0.76024 | 0.82519 | 0.88906 | 0.95223 | 1.015 | 1.0775 | 1.1394 | 1.2022 | 1.2666 | 1.3329 | 1.4002 | 1.4667 | 1.5318 | 1.5954 | 1.6573 | 1.7184 | 1.7786 | 1.8373 | 1.8959 | 1.9539 | 2.011 | 2.068 | 2.1249 | 2.1815 | 2.2379 | 2.2941 | 2.3502 | 2.4061 | 2.4619 | 2.5175 | 553.8793 | 629.0444 | 694.911 | 760.2419 | 825.1866 | 889.055 | 952.2319 | 1015.0459 | 1077.526 | 1139.3649
48 | PMA | Southern | EHZ | East Hobart | high | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.1669 | 0.19393 | 0.22298 | 0.25522 | 0.29657 | 0.33609 | 0.36755 | 0.39877 | 0.42972 | 0.46004 | 0.48993 | 0.51954 | 0.54889 | 0.57783 | 0.60712 | 0.63705 | 0.66775 | 0.69878 | 0.7293 | 0.75911 | 0.78811 | 0.81619 | 0.84381 | 0.87093 | 0.89731 | 0.92345 | 0.94925 | 0.97458 | 0.99973 | 1.0247 | 1.0495 | 1.074 | 1.0984 | 1.1226 | 1.1466 | 1.1705 | 1.1942 | 296.566 | 336.0904 | 367.5494 | 398.7689 | 429.7236 | 460.0436 | 489.9317 | 519.5404 | 548.8912 | 577.833
48 | PMA | Southern | GBZ | Geilston Bay | high | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.85515 | 0.96363 | 1.1408 | 1.3486 | 1.5703 | 1.783 | 1.954 | 2.1258 | 2.2973 | 2.4672 | 2.6364 | 2.8056 | 2.9749 | 3.1436 | 3.316 | 3.4938 | 3.6781 | 3.8662 | 4.053 | 4.2372 | 4.4182 | 4.5952 | 4.7711 | 4.9454 | 5.1167 | 5.2881 | 5.459 | 5.6283 | 5.7982 | 5.9685 | 6.1391 | 6.31 | 6.4813 | 6.6531 | 6.8253 | 6.9981 | 7.1712 | 1570.2582 | 1782.974 | 1953.9943 | 2125.8301 | 2297.2854 | 2467.2416 | 2636.387 | 2805.5535 | 2974.9263 | 3143.5884
48 | PMA | Southern | GRZ | Gretna | high | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.0074076 | 0.0084189 | 0.0096327 | 0.011063 | 0.012666 | 0.014183 | 0.015416 | 0.016645 | 0.017866 | 0.019069 | 0.020259 | 0.021444 | 0.022622 | 0.02379 | 0.024976 | 0.026194 | 0.027449 | 0.028722 | 0.02998 | 0.031214 | 0.032419 | 0.033592 | 0.03475 | 0.035893 | 0.037008 | 0.038119 | 0.039221 | 0.040307 | 0.04139 | 0.04247 | 0.043546 | 0.044618 | 0.045687 | 0.046753 | 0.047817 | 0.048877 | 0.049935 | 12.6656 | 14.1833 | 15.416 | 16.6448 | 17.866 | 19.069 | 20.2593 | 21.4435 | 22.6225 | 23.7899
48 | PMA | Southern | HOZ | Howrah | high | maximum | PV | non-coincident | POE50 | summer | zone | zone plus embedded | MW | 0 | Zs | 0.89544 | 1.0103 | 1.1989 | 1.446 | 1.7324 | 1.9951 | 2.2062 | 2.4183 | 2.6296 | 2.8391 | 3.0473 | 3.2555 | 3.4638 | 3.6711 | 3.8828 | 4.1012 | 4.3272 | 4.5577 | 4.7866 | 5.0121 | 5.2335 | 5.4499 | 5.6647 | 5.8775 | 6.0864 | 6.2954 | 6.5035 | 6.7097 | 6.9163 | 7.1233 | 7.3305 | 7.5379 | 7.7456 | 7.9538 | 8.1623 | 8.3713 | 8.5806 | 1732.3976 | 1995.0945 | 2206.2411 | 2418.2538 | 2629.6372 | 2839.0609 | 3047.3483 | 3255.5275 | 3463.8308 | 3671.1233
48 | PMA | Southern | NTZ | New Town | high | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.45273 | 0.51284 | 0.58701 | 0.68503 | 0.80512 | 0.91625 | 1.0113 | 1.1054 | 1.1988 | 1.2903 | 1.3806 | 1.4701 | 1.5589 | 1.6465 | 1.7353 | 1.826 | 1.9192 | 2.0134 | 2.1062 | 2.1969 | 2.2852 | 2.3707 | 2.4549 | 2.5377 | 2.6182 | 2.6981 | 2.777 | 2.8545 | 2.9316 | 3.0081 | 3.084 | 3.1595 | 3.2344 | 3.3088 | 3.3827 | 3.4562 | 3.5292 | 805.1229 | 916.254 | 1011.3344 | 1105.4446 | 1198.7811 | 1290.3036 | 1380.5868 | 1470.102 | 1558.8952 | 1646.5232
48 | PMA | Southern | RIZ | Richmond | high | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.31002 | 0.35457 | 0.41891 | 0.49458 | 0.58001 | 0.66243 | 0.73154 | 0.80087 | 0.87013 | 0.93861 | 1.0067 | 1.0748 | 1.1428 | 1.2106 | 1.2797 | 1.351 | 1.4249 | 1.5002 | 1.575 | 1.6488 | 1.7212 | 1.792 | 1.8624 | 1.9322 | 2.0007 | 2.0693 | 2.1377 | 2.2055 | 2.2736 | 2.3418 | 2.4102 | 2.4788 | 2.5476 | 2.6166 | 2.6859 | 2.7554 | 2.8252 | 580.0075 | 662.4337 | 731.5382 | 800.8658 | 870.1281 | 938.6057 | 1006.7044 | 1074.7594 | 1142.8228 | 1210.5504
48 | PMA | Southern | RPZ | Rosny Park | high | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.62925 | 0.70515 | 0.83117 | 0.99073 | 1.1692 | 1.3379 | 1.4735 | 1.6096 | 1.7454 | 1.8799 | 2.0137 | 2.1474 | 2.2812 | 2.4144 | 2.5504 | 2.6907 | 2.836 | 2.9842 | 3.1312 | 3.2762 | 3.4186 | 3.5577 | 3.6958 | 3.8327 | 3.967 | 4.1014 | 4.2353 | 4.3679 | 4.5008 | 4.634 | 4.7673 | 4.9008 | 5.0345 | 5.1685 | 5.3027 | 5.4373 | 5.5721 | 1169.2297 | 1337.9038 | 1473.4816 | 1609.6272 | 1745.3821 | 1879.8877 | 2013.675 | 2147.4039 | 2281.2234 | 2414.405
48 | PMA | Southern | SBZ | Sandy Bay | high | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 1.3655 | 1.5686 | 1.8187 | 2.1206 | 2.4683 | 2.7903 | 3.0521 | 3.3124 | 3.5708 | 3.8244 | 4.0748 | 4.3233 | 4.57 | 4.8138 | 5.0609 | 5.3139 | 5.5738 | 5.8371 | 6.0964 | 6.3502 | 6.5976 | 6.8375 | 7.0741 | 7.3067 | 7.5333 | 7.7584 | 7.981 | 8.1999 | 8.4177 | 8.6343 | 8.8496 | 9.0636 | 9.2764 | 9.4881 | 9.6987 | 9.9081 | 10.1165 | 2468.2555 | 2790.2666 | 3052.1082 | 3312.4162 | 3570.7788 | 3824.3628 | 4074.7582 | 4323.2504 | 4570.0082 | 4813.7634
48 | PMA | Southern | SUZ | Summerleas Road | high | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.65883 | 0.75889 | 0.90746 | 1.0783 | 1.2607 | 1.4294 | 1.5776 | 1.7259 | 1.8736 | 2.0196 | 2.1645 | 2.3093 | 2.4538 | 2.5975 | 2.744 | 2.8948 | 3.0507 | 3.2095 | 3.3669 | 3.5217 | 3.6736 | 3.8217 | 3.9686 | 4.1139 | 4.2563 | 4.3985 | 4.5399 | 4.6798 | 4.8198 | 4.9598 | 5.0997 | 5.2396 | 5.3795 | 5.5195 | 5.6595 | 5.7996 | 5.9397 | 1260.7287 | 1429.3593 | 1577.6108 | 1725.8961 | 1873.5902 | 2019.5697 | 2164.5421 | 2309.2671 | 2453.8215 | 2597.4643
48 | PMA | Southern | TWY2 | Wayatinah | high | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | RT | 0.013722 | 0.015617 | 0.017888 | 0.020565 | 0.0030024 | 0.0058459 | 0.0081553 | 0.010458 | 0.012745 | 0.014999 | 0.017229 | 0.019448 | 0.021657 | 0.023844 | 0.026067 | 0.028349 | 0.030699 | 0.033085 | 0.035441 | 0.037753 | 0.040012 | 0.042208 | 0.044379 | 0.046519 | 0.04861 | 0.050691 | 0.052755 | 0.054789 | 0.056819 | 0.058842 | 0.060858 | 0.062867 | 0.06487 | 0.066868 | 0.06886 | 0.070848 | 0.072829 | 3.0024 | 5.8459 | 8.1553 | 10.4576 | 12.7454 | 14.9993 | 17.2293 | 19.4481 | 21.6569 | 23.8441
48 | PMA | Southern | WHZ | West Hobart Zone | high | maximum | PV | non-coincident | POE50 | summer | zone | zone plus embedded | MW | 0 | Zs | 0.60518 | 0.69967 | 0.80934 | 0.93342 | 0.14543 | 0.28724 | 0.40229 | 0.51664 | 0.63012 | 0.74148 | 0.85142 | 0.96051 | 1.0688 | 1.1758 | 1.2842 | 1.3952 | 1.5092 | 1.6246 | 1.7383 | 1.8496 | 1.958 | 2.0631 | 2.1668 | 2.2686 | 2.3679 | 2.4665 | 2.5639 | 2.6597 | 2.755 | 2.8498 | 2.9439 | 3.0375 | 3.1306 | 3.2231 | 3.3151 | 3.4067 | 3.4977 | 145.4257 | 287.2431 | 402.287 | 516.6365 | 630.1199 | 741.4804 | 851.4214 | 960.5067 | 1068.811 | 1175.7777
48 | PMA | Western | THZ | Trial Harbour | high | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.063729 | 0.070961 | 0.07986 | 0.097555 | 0.023047 | 0.037774 | 0.046331 | 0.054855 | 0.063304 | 0.071615 | 0.079823 | 0.087972 | 0.096068 | 0.10407 | 0.11218 | 0.12049 | 0.12904 | 0.13769 | 0.14623 | 0.15458 | 0.16273 | 0.17063 | 0.17843 | 0.1861 | 0.19358 | 0.20101 | 0.20836 | 0.2156 | 0.2228 | 0.22996 | 0.23709 | 0.24417 | 0.25122 | 0.25824 | 0.26522 | 0.27217 | 0.27909 | 23.0469 | 37.7745 | 46.3308 | 54.8547 | 63.3041 | 71.6151 | 79.8235 | 87.9717 | 96.0683 | 104.0691
48 | PMA | Western | RBZ | Rosebery 22 kV | high | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.1152 | 0.12955 | 0.14681 | 0.17669 | 0.038489 | 0.064598 | 0.081161 | 0.097643 | 0.11395 | 0.12996 | 0.14575 | 0.1614 | 0.17692 | 0.19223 | 0.20773 | 0.22358 | 0.23984 | 0.25629 | 0.27249 | 0.28831 | 0.30371 | 0.31864 | 0.33333 | 0.34777 | 0.36181 | 0.37575 | 0.38952 | 0.40304 | 0.41648 | 0.42983 | 0.44309 | 0.45625 | 0.46932 | 0.48231 | 0.49522 | 0.50805 | 0.5208 | 38.4886 | 64.5979 | 81.1609 | 97.6427 | 113.9521 | 129.9649 | 145.7539 | 161.399 | 176.9188 | 192.2284
48 | PMA | total terminal |  | total terminal | high | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | #N/A | #N/A | 33.5903 | 38.9738 | 45.725 | 53.4868 | 62.0167 | 70.0135 | 77.0939 | 84.1622 | 91.1807 | 98.0913 | 104.9304 | 111.7316 | 118.5017 | 125.2048 | 132.0165 | 139.0065 | 146.2059 | 153.5145 | 160.7337 | 167.8139 | 174.7345 | 181.4622 | 188.1122 | 194.6686 | 201.0743 | 207.4529 | 213.7776 | 220.014 | 226.2362 | 232.4412 | 238.6259 | 244.7904 | 250.9378 | 257.0712 | 263.1906 | 269.296 | 275.3874 | 62016.6784 | 70013.4574 | 77093.8724 | 84162.1809 | 91180.7204 | 98091.2566 | 104930.3978 | 111731.6167 | 118501.6559 | 125204.8092
48 | PMA | total zone |  | total zone | high | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | #N/A | #N/A | 8.6354 | 9.8513 | 11.5677 | 13.6795 | 14.8679 | 17.118 | 18.9671 | 20.8139 | 22.6519 | 24.4653 | 26.2634 | 28.0552 | 29.8422 | 31.615 | 33.42 | 35.2759 | 37.191 | 39.1388 | 41.0664 | 42.9603 | 44.815 | 46.6213 | 48.41 | 50.1766 | 51.9057 | 53.6305 | 55.3438 | 57.036 | 58.7273 | 60.4168 | 62.1037 | 63.7877 | 65.4699 | 67.151 | 68.831 | 70.5098 | 72.1874 | 14867.9277 | 17117.9707 | 18967.0529 | 20813.8937 | 22651.8675 | 24465.3218 | 26263.3881 | 28055.1679 | 29842.1544 | 31614.9842
51 | PMA | George Town | TC01 | Comalco | high | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | Camalco | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | PMA | George Town | TSW1 | Starwood | high | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | Starwood | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | PMA | George Town | TTE1 | Temco | high | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | Temco | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | PMA | North | TAL2 | Ax-Arthurs Lake 6.6 kV | high | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | Ax | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | PMA | North | TAV2 | Avoca 22 kV | high | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.000201 | 0.00087061 | 0.0025237 | 0.004455 | 0.006268 | 0.0078152 | 0.010361 | 0.014898 | 0.020597 | 0.033629 | 0.048641 | 0.065661 | 0.084995 | 0.10677 | 0.13105 | 0.15787 | 0.18728 | 0.21935 | 0.25386 | 0.29076 | 0.33012 | 0.37197 | 0.41554 | 0.46084 | 0.50788 | 0.5567 | 0.60731 | 0.65973 | 0.714 | 0.77014 | 0.82773 | 0.88678 | 0.9473 | 0.201 | 0.87061 | 2.5237 | 4.455 | 6.268 | 7.8152 | 10.3605 | 14.898 | 20.5971 | 33.6292
51 | PMA | North | TDE2 | Derby 22 kV | high | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.00019719 | 0.00088401 | 0.0020498 | 0.0031278 | 0.004326 | 0.0053377 | 0.0069634 | 0.009382 | 0.012359 | 0.020414 | 0.029436 | 0.039418 | 0.050493 | 0.0627 | 0.076041 | 0.090512 | 0.10611 | 0.12284 | 0.14058 | 0.15928 | 0.17895 | 0.19959 | 0.22082 | 0.24264 | 0.26504 | 0.28802 | 0.31158 | 0.33571 | 0.36041 | 0.38568 | 0.41133 | 0.43735 | 0.46376 | 0.19719 | 0.88401 | 2.0498 | 3.1278 | 4.326 | 5.3377 | 6.9634 | 9.382 | 12.359 | 20.4139
51 | PMA | North | THA3 | Hadspen 22 kV | high | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.0018598 | 0.0079058 | 0.022474 | 0.037143 | 0.049048 | 0.061082 | 0.080952 | 0.11304 | 0.15421 | 0.2515 | 0.36291 | 0.48859 | 0.63066 | 0.79 | 0.96691 | 1.1616 | 1.3745 | 1.6058 | 1.854 | 2.1187 | 2.4002 | 2.6987 | 3.0088 | 3.3305 | 3.6638 | 4.0089 | 4.3659 | 4.7349 | 5.116 | 5.5095 | 5.9122 | 6.3243 | 6.7459 | 1.8598 | 7.9058 | 22.4743 | 37.1426 | 49.0479 | 61.0817 | 80.9521 | 113.0391 | 154.2053 | 251.4975
51 | PMA | North | TMY2 | Mowbray 22 kV | high | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.0010972 | 0.004176 | 0.011584 | 0.018279 | 0.022771 | 0.02871 | 0.038277 | 0.052678 | 0.069065 | 0.11039 | 0.15716 | 0.2094 | 0.26787 | 0.33286 | 0.40441 | 0.48255 | 0.56733 | 0.65883 | 0.75635 | 0.85972 | 0.96899 | 1.0842 | 1.2032 | 1.326 | 1.4526 | 1.583 | 1.7172 | 1.8552 | 1.997 | 2.1426 | 2.291 | 2.442 | 2.5959 | 1.0972 | 4.176 | 11.5844 | 18.2787 | 22.771 | 28.7098 | 38.2766 | 52.6783 | 69.0653 | 110.3876
51 | PMA | North | TPM3 | Palmerston 22 kV | high | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 9.1428e-05 | 0.00040781 | 0.0011729 | 0.002031 | 0.002818 | 0.0034802 | 0.0045705 | 0.0065787 | 0.0092842 | 0.015305 | 0.02227 | 0.030194 | 0.039225 | 0.049426 | 0.060824 | 0.073442 | 0.087308 | 0.10245 | 0.11877 | 0.13625 | 0.15491 | 0.17478 | 0.19549 | 0.21704 | 0.23944 | 0.2627 | 0.28684 | 0.31187 | 0.3378 | 0.36465 | 0.39221 | 0.42049 | 0.4495 | 0.091428 | 0.40781 | 1.1729 | 2.031 | 2.818 | 3.4802 | 4.5705 | 6.5787 | 9.2842 | 15.305
51 | PMA | North | TSD2 | Scottsdale 22 kV | high | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.00054538 | 0.0024061 | 0.0056207 | 0.0084588 | 0.011328 | 0.01396 | 0.018163 | 0.024494 | 0.032443 | 0.053596 | 0.077336 | 0.10365 | 0.13288 | 0.16516 | 0.20047 | 0.23881 | 0.28019 | 0.3246 | 0.37172 | 0.42144 | 0.47376 | 0.52868 | 0.58522 | 0.64335 | 0.70306 | 0.76435 | 0.82719 | 0.89159 | 0.95754 | 1.025 | 1.0936 | 1.1631 | 1.2337 | 0.54538 | 2.4061 | 5.6207 | 8.4588 | 11.3276 | 13.9595 | 18.1634 | 24.4938 | 32.4432 | 53.5961
51 | PMA | North | TSL2 | St Leonards 22 kV | high | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.0011844 | 0.0049277 | 0.013762 | 0.022008 | 0.027691 | 0.034739 | 0.046298 | 0.063346 | 0.083537 | 0.13437 | 0.19199 | 0.25644 | 0.32871 | 0.40916 | 0.49789 | 0.59497 | 0.70048 | 0.81456 | 0.93636 | 1.0657 | 1.2026 | 1.3473 | 1.4969 | 1.6517 | 1.8114 | 1.9763 | 2.1462 | 2.3212 | 2.5014 | 2.6868 | 2.8759 | 3.0689 | 3.2656 | 1.1844 | 4.9277 | 13.762 | 22.0076 | 27.6913 | 34.7392 | 46.2978 | 63.3464 | 83.5366 | 134.3666
51 | PMA | North | TSL3 | St Leonards 22 kV (scheduled load) | high | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | Firmus Grid | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | PMA | North | TSM2 | St Marys 22 kV | high | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.00065645 | 0.0025778 | 0.0081009 | 0.014202 | 0.020584 | 0.026219 | 0.03628 | 0.049639 | 0.062307 | 0.097709 | 0.13739 | 0.18136 | 0.23026 | 0.28432 | 0.3436 | 0.40817 | 0.47806 | 0.55338 | 0.63359 | 0.71858 | 0.80841 | 0.90312 | 1.0011 | 1.1022 | 1.2066 | 1.3143 | 1.4252 | 1.5394 | 1.6569 | 1.7778 | 1.9011 | 2.0269 | 2.1551 | 0.65645 | 2.5778 | 8.1009 | 14.2024 | 20.584 | 26.2193 | 36.2803 | 49.639 | 62.3071 | 97.7087
51 | PMA | Northwest | TDP2 | Devonport 22 kV | high | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.0023154 | 0.0066217 | 0.016139 | 0.025227 | 0.032174 | 0.041608 | 0.058484 | 0.083284 | 0.10712 | 0.17089 | 0.24274 | 0.3227 | 0.41196 | 0.51099 | 0.6199 | 0.73881 | 0.86784 | 1.0071 | 1.1558 | 1.3135 | 1.4804 | 1.6566 | 1.8391 | 2.0277 | 2.2225 | 2.4235 | 2.6309 | 2.8445 | 3.0645 | 3.291 | 3.5222 | 3.7582 | 3.999 | 2.3154 | 6.6217 | 16.1386 | 25.2267 | 32.1736 | 41.6078 | 58.4838 | 83.2841 | 107.1162 | 170.8949
51 | PMA | Northwest | TEB2 | Emu Bay 11 kV | high | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | Emu Bay | MI | 0 | 0 | 0 | 0 | 2.9362e-05 | 0.00013855 | 0.00030927 | 0.00049691 | 0.00066337 | 0.0008463 | 0.0012033 | 0.0017763 | 0.0022387 | 0.0034829 | 0.0048762 | 0.0064174 | 0.0081263 | 0.010009 | 0.012065 | 0.014293 | 0.016693 | 0.019265 | 0.02199 | 0.024859 | 0.027875 | 0.031035 | 0.034283 | 0.037618 | 0.04104 | 0.044546 | 0.048137 | 0.051811 | 0.055569 | 0.059408 | 0.063302 | 0.067249 | 0.07125 | 0.029362 | 0.13855 | 0.30927 | 0.49691 | 0.66337 | 0.8463 | 1.2033 | 1.7763 | 2.2387 | 3.4829
51 | PMA | Northwest | THM2 | Hampshire | high | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | Hampshire | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | PMA | Northwest | TPL2 | Port Latta | high | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | Port Latta | MI | 0 | 0 | 0 | 0 | 0.00025066 | 0.0011659 | 0.0028408 | 0.0045179 | 0.0064475 | 0.0080508 | 0.010629 | 0.014971 | 0.019831 | 0.031975 | 0.045709 | 0.061029 | 0.078153 | 0.097153 | 0.11803 | 0.1408 | 0.16544 | 0.19199 | 0.22022 | 0.25007 | 0.28156 | 0.31469 | 0.34884 | 0.38401 | 0.42019 | 0.45737 | 0.49556 | 0.53474 | 0.57492 | 0.61609 | 0.65795 | 0.70049 | 0.74371 | 0.25066 | 1.1659 | 2.8408 | 4.5179 | 6.4475 | 8.0508 | 10.6292 | 14.9706 | 19.8312 | 31.9747
51 | PMA | Northwest | TRA2 | Railton 22 kV | high | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.0011415 | 0.004958 | 0.013841 | 0.023068 | 0.030213 | 0.038077 | 0.050479 | 0.070975 | 0.095245 | 0.15478 | 0.22265 | 0.29893 | 0.38488 | 0.48103 | 0.58755 | 0.7046 | 0.83235 | 0.97103 | 1.1197 | 1.2781 | 1.4465 | 1.6249 | 1.8103 | 2.0025 | 2.2016 | 2.4078 | 2.621 | 2.8414 | 3.069 | 3.304 | 3.5445 | 3.7907 | 4.0426 | 1.1415 | 4.958 | 13.8414 | 23.0676 | 30.2125 | 38.077 | 50.4787 | 70.9754 | 95.2455 | 154.781
51 | PMA | Northwest | TSH3 | Sheffield | high | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | PMA | Northwest | TST2 | Smithton 22 kV | high | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.00035907 | 0.0013368 | 0.0033721 | 0.0054407 | 0.0094549 | 0.011536 | 0.014551 | 0.020604 | 0.02998 | 0.049906 | 0.072857 | 0.098806 | 0.12816 | 0.16104 | 0.19743 | 0.23733 | 0.28071 | 0.32759 | 0.37755 | 0.43047 | 0.48634 | 0.54516 | 0.60576 | 0.66814 | 0.73227 | 0.79813 | 0.8657 | 0.93497 | 1.0059 | 1.0786 | 1.1523 | 1.2271 | 1.303 | 0.35907 | 1.3368 | 3.3721 | 5.4407 | 9.4549 | 11.5359 | 14.5511 | 20.6045 | 29.9801 | 49.9062
51 | PMA | Northwest | TUL2 | Ulverstone 22 kV | high | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.0010713 | 0.0056073 | 0.014092 | 0.022245 | 0.028676 | 0.037296 | 0.050515 | 0.072043 | 0.092464 | 0.14759 | 0.20949 | 0.27816 | 0.35457 | 0.43905 | 0.53165 | 0.63241 | 0.74138 | 0.85862 | 0.9833 | 1.1152 | 1.2543 | 1.4007 | 1.5517 | 1.7074 | 1.8677 | 2.0327 | 2.2022 | 2.3764 | 2.5552 | 2.7387 | 2.9254 | 3.1154 | 3.3087 | 1.0713 | 5.6073 | 14.0921 | 22.2447 | 28.6758 | 37.296 | 50.5154 | 72.0429 | 92.4644 | 147.5879
51 | PMA | Northwest | TWV2 | Wesley Vale 11 kV | high | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | Wesley Vale | MI | 0 | 0 | 0 | 0 | 0.0003829 | 0.0021187 | 0.006023 | 0.0094732 | 0.012557 | 0.016655 | 0.022717 | 0.031622 | 0.041437 | 0.066053 | 0.094199 | 0.12596 | 0.16192 | 0.20237 | 0.24743 | 0.29725 | 0.35198 | 0.41178 | 0.47631 | 0.54555 | 0.61966 | 0.69876 | 0.78144 | 0.86778 | 0.95784 | 1.0517 | 1.1495 | 1.2512 | 1.357 | 1.467 | 1.5803 | 1.6971 | 1.8174 | 0.3829 | 2.1187 | 6.023 | 9.4732 | 12.5573 | 16.6545 | 22.7168 | 31.6216 | 41.4369 | 66.0531
51 | PMA | Southern | TBW2 | Bridgewater 11 kV | high | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.00097473 | 0.0048569 | 0.012365 | 0.019986 | 0.026117 | 0.037474 | 0.052405 | 0.077921 | 0.10087 | 0.16151 | 0.23049 | 0.30804 | 0.39558 | 0.49379 | 0.60308 | 0.7238 | 0.85635 | 1.0012 | 1.1576 | 1.3255 | 1.5054 | 1.6976 | 1.8988 | 2.1093 | 2.3291 | 2.5587 | 2.7982 | 3.048 | 3.3082 | 3.5793 | 3.8592 | 4.1484 | 4.4468 | 0.97473 | 4.8569 | 12.3654 | 19.9862 | 26.1171 | 37.4741 | 52.4049 | 77.9205 | 100.8666 | 161.5075
51 | PMA | Southern | TBYA | Boyer SWA | high | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | Boyer | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | PMA | Southern | TBYB | Boyer SWB | high | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | Boyer | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | PMA | Southern | TCR2 | Creek Rd 33 kV | high | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.0044983 | 0.010337 | 0.023654 | 0.038628 | 0.048632 | 0.0631 | 0.086105 | 0.12571 | 0.16248 | 0.26192 | 0.37385 | 0.49836 | 0.63729 | 0.79138 | 0.96084 | 1.1458 | 1.3466 | 1.5633 | 1.7946 | 2.0401 | 2.3 | 2.5744 | 2.8586 | 3.1524 | 3.456 | 3.7695 | 4.0928 | 4.426 | 4.7694 | 5.1228 | 5.4837 | 5.8522 | 6.2284 | 4.4983 | 10.3369 | 23.6536 | 38.6276 | 48.6317 | 63.1001 | 86.1052 | 125.706 | 162.4797 | 261.9202
51 | PMA | Southern | TCS3 | Chapel St 11 kV | high | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.0022256 | 0.0049083 | 0.010358 | 0.0163 | 0.021472 | 0.028605 | 0.03957 | 0.058382 | 0.077225 | 0.12684 | 0.18283 | 0.24524 | 0.31501 | 0.39251 | 0.47783 | 0.57105 | 0.67228 | 0.78164 | 0.89835 | 1.0223 | 1.1534 | 1.292 | 1.4354 | 1.5837 | 1.7368 | 1.8949 | 2.058 | 2.226 | 2.399 | 2.577 | 2.7588 | 2.9443 | 3.1336 | 2.2256 | 4.9083 | 10.3581 | 16.2999 | 21.4721 | 28.6053 | 39.5696 | 58.3818 | 77.2252 | 126.8356
51 | PMA | Southern | TDB2 | Derwent Bridge 22 kV | high | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0 | 0 | 0 | 0 | 1.3916e-06 | 8.4641e-06 | 1.9313e-05 | 3.2982e-05 | 4.177e-05 | 5.7581e-05 | 7.8781e-05 | 0.00011703 | 0.00015044 | 0.00023978 | 0.00034059 | 0.00045301 | 0.00057878 | 0.0007186 | 0.00087273 | 0.0010414 | 0.0012248 | 0.0014233 | 0.0016356 | 0.0018613 | 0.0021008 | 0.0023542 | 0.002617 | 0.0028893 | 0.0031712 | 0.0034627 | 0.0037639 | 0.004075 | 0.004396 | 0.0047271 | 0.0050658 | 0.0054122 | 0.0057663 | 0.0013916 | 0.0084641 | 0.019313 | 0.032982 | 0.04177 | 0.057581 | 0.078781 | 0.11703 | 0.15044 | 0.23978
51 | PMA | Southern | TEL2 | Electrona 11 kV | high | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.00059419 | 0.002953 | 0.0093858 | 0.016098 | 0.020489 | 0.026719 | 0.035437 | 0.051607 | 0.067039 | 0.10814 | 0.15467 | 0.20671 | 0.26512 | 0.33028 | 0.40236 | 0.48151 | 0.5679 | 0.66172 | 0.76238 | 0.86982 | 0.9842 | 1.1057 | 1.2321 | 1.3634 | 1.4999 | 1.6414 | 1.7882 | 1.9403 | 2.0978 | 2.2607 | 2.428 | 2.5996 | 2.7756 | 0.59419 | 2.953 | 9.3858 | 16.0985 | 20.4886 | 26.7187 | 35.4365 | 51.6073 | 67.0391 | 108.1421
51 | PMA | Southern | THR2 | Huon River | high | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | Huon River | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | PMA | Southern | TK12 | Kingston 11 kV | high | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.0010586 | 0.0055611 | 0.017948 | 0.030875 | 0.039339 | 0.051368 | 0.068063 | 0.099164 | 0.12892 | 0.20809 | 0.29771 | 0.39798 | 0.51056 | 0.63617 | 0.77514 | 0.92776 | 1.0944 | 1.2753 | 1.4695 | 1.6768 | 1.8976 | 2.132 | 2.3759 | 2.6296 | 2.893 | 3.1663 | 3.4498 | 3.7435 | 4.0476 | 4.3624 | 4.6854 | 5.017 | 5.3571 | 1.0586 | 5.5611 | 17.9477 | 30.8749 | 39.3395 | 51.3683 | 68.0634 | 99.164 | 128.9236 | 208.0873
51 | PMA | Southern | TK13 | Kingston 33 kV | high | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | PMA | Southern | TKE2 | Kermandie 11 kV | high | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.00026623 | 0.0019548 | 0.0059286 | 0.0095236 | 0.011998 | 0.015073 | 0.020064 | 0.028693 | 0.03662 | 0.058168 | 0.08256 | 0.10987 | 0.14056 | 0.17485 | 0.21286 | 0.2547 | 0.30047 | 0.35032 | 0.40396 | 0.46137 | 0.52268 | 0.58797 | 0.65612 | 0.72718 | 0.8012 | 0.87825 | 0.95838 | 1.0417 | 1.1282 | 1.218 | 1.3105 | 1.4056 | 1.5036 | 0.26623 | 1.9548 | 5.9286 | 9.5236 | 11.9981 | 15.0731 | 20.0643 | 28.6931 | 36.6203 | 58.1677
51 | PMA | Southern | TLF2 | Lindisfarne 33 kV | high | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.00060384 | 0.0032151 | 0.010145 | 0.017084 | 0.022112 | 0.030731 | 0.043525 | 0.06671 | 0.086125 | 0.13778 | 0.19632 | 0.26188 | 0.33556 | 0.41786 | 0.50903 | 0.60928 | 0.71885 | 0.83802 | 0.96606 | 1.1029 | 1.2488 | 1.4039 | 1.5656 | 1.7338 | 1.9088 | 2.0906 | 2.2793 | 2.4751 | 2.6782 | 2.8885 | 3.1047 | 3.3268 | 3.555 | 0.60384 | 3.2151 | 10.1452 | 17.0839 | 22.1122 | 30.7307 | 43.5249 | 66.7097 | 86.1245 | 137.7837
51 | PMA | Southern | TMB2 | Meadowbank 22 kV | high | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 9.1783e-05 | 0.00052005 | 0.0012381 | 0.0020719 | 0.0026589 | 0.0037218 | 0.0051372 | 0.0076282 | 0.0098337 | 0.015701 | 0.022343 | 0.029774 | 0.038116 | 0.047425 | 0.057726 | 0.06904 | 0.081392 | 0.094814 | 0.10922 | 0.1246 | 0.14099 | 0.1584 | 0.17653 | 0.19539 | 0.21498 | 0.23533 | 0.25645 | 0.27834 | 0.30104 | 0.32454 | 0.34869 | 0.37349 | 0.39896 | 0.091783 | 0.52005 | 1.2381 | 2.0719 | 2.6589 | 3.7218 | 5.1372 | 7.6282 | 9.8337 | 15.7009
51 | PMA | Southern | TMT2 | Mornington 33 kV | high | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.00069408 | 0.003689 | 0.011671 | 0.019664 | 0.025451 | 0.03535 | 0.050074 | 0.076771 | 0.099112 | 0.15856 | 0.22593 | 0.30136 | 0.38614 | 0.48082 | 0.5857 | 0.70101 | 0.82702 | 0.96406 | 1.1113 | 1.2686 | 1.4364 | 1.6147 | 1.8005 | 1.9939 | 2.1949 | 2.4038 | 2.6206 | 2.8456 | 3.0788 | 3.3204 | 3.5687 | 3.8238 | 4.0857 | 0.69408 | 3.689 | 11.6706 | 19.6642 | 25.4511 | 35.3498 | 50.0737 | 76.7707 | 99.1121 | 158.5643
51 | PMA | Southern | TNH2 | North Hobart 11 kV | high | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.001801 | 0.0038426 | 0.008455 | 0.013804 | 0.017032 | 0.021812 | 0.029831 | 0.043373 | 0.055429 | 0.088599 | 0.12583 | 0.16713 | 0.2131 | 0.26396 | 0.31977 | 0.38056 | 0.44639 | 0.51733 | 0.59288 | 0.67292 | 0.75751 | 0.84668 | 0.93886 | 1.034 | 1.1322 | 1.2335 | 1.3377 | 1.445 | 1.5553 | 1.6688 | 1.7844 | 1.9023 | 2.0225 | 1.801 | 3.8426 | 8.455 | 13.8037 | 17.0316 | 21.8117 | 29.8311 | 43.3733 | 55.4289 | 88.599
51 | PMA | Southern | TNN2 | New Norfolk 22 kV | high | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | Brynn Estyn | MI | 0 | 0 | 0 | 0 | 0.00038606 | 0.002327 | 0.0053372 | 0.0090907 | 0.011531 | 0.015928 | 0.021817 | 0.032409 | 0.041675 | 0.066436 | 0.094391 | 0.12558 | 0.16048 | 0.19931 | 0.24213 | 0.28901 | 0.34002 | 0.39526 | 0.45435 | 0.51723 | 0.58397 | 0.65464 | 0.72797 | 0.804 | 0.88273 | 0.9642 | 1.0484 | 1.1355 | 1.2254 | 1.3181 | 1.4131 | 1.5102 | 1.6096 | 0.38606 | 2.327 | 5.3372 | 9.0907 | 11.5314 | 15.9282 | 21.8169 | 32.4092 | 41.6751 | 66.4364
51 | PMA | Southern | TR13 | Risdon 11 kV | high | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | Risdon | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | PMA | Southern | TR14 | Risdon 33 kV | high | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.001519 | 0.003391 | 0.0073061 | 0.011632 | 0.015028 | 0.019881 | 0.027436 | 0.040351 | 0.052832 | 0.086054 | 0.12351 | 0.16524 | 0.21187 | 0.26364 | 0.32063 | 0.38289 | 0.4505 | 0.52355 | 0.60153 | 0.68433 | 0.77203 | 0.86467 | 0.96061 | 1.0599 | 1.1624 | 1.2683 | 1.3776 | 1.4903 | 1.6063 | 1.7259 | 1.848 | 1.9726 | 2.0999 | 1.519 | 3.391 | 7.3061 | 11.632 | 15.0278 | 19.8814 | 27.4361 | 40.3507 | 52.8322 | 86.0535
51 | PMA | Southern | TRK2 | Rokeby 11 kV | high | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.00050673 | 0.0026936 | 0.008522 | 0.014359 | 0.018585 | 0.025813 | 0.036565 | 0.056059 | 0.072373 | 0.11579 | 0.16498 | 0.22006 | 0.28196 | 0.35111 | 0.42769 | 0.51189 | 0.6039 | 0.70397 | 0.81148 | 0.92638 | 1.0489 | 1.1791 | 1.3147 | 1.456 | 1.6028 | 1.7553 | 1.9136 | 2.0779 | 2.2482 | 2.4246 | 2.6059 | 2.7922 | 2.9835 | 0.50673 | 2.6936 | 8.522 | 14.3591 | 18.5848 | 25.813 | 36.5647 | 56.0595 | 72.3735 | 115.7863
51 | PMA | Southern | TS02 | Sorell | high | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.0012214 | 0.0062844 | 0.016556 | 0.027662 | 0.03786 | 0.052693 | 0.071502 | 0.10745 | 0.13764 | 0.21895 | 0.31107 | 0.41426 | 0.53029 | 0.65999 | 0.80381 | 0.96213 | 1.1354 | 1.3241 | 1.5272 | 1.7446 | 1.9768 | 2.2241 | 2.4823 | 2.7516 | 3.0321 | 3.3241 | 3.628 | 3.9438 | 4.272 | 4.6128 | 4.9637 | 5.3251 | 5.6971 | 1.2214 | 6.2844 | 16.5563 | 27.662 | 37.8598 | 52.6927 | 71.5023 | 107.4515 | 137.6408 | 218.9513
51 | PMA | Southern | TTB2 | Triabunna 22 kV | high | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.00024756 | 0.0012493 | 0.0040799 | 0.0062763 | 0.009217 | 0.011541 | 0.016754 | 0.022821 | 0.027814 | 0.043191 | 0.060338 | 0.079292 | 0.10034 | 0.1236 | 0.14915 | 0.17704 | 0.20734 | 0.2401 | 0.27516 | 0.31248 | 0.35214 | 0.39419 | 0.43792 | 0.48336 | 0.53054 | 0.57948 | 0.63022 | 0.68278 | 0.73722 | 0.79356 | 0.85141 | 0.9108 | 0.97176 | 0.24756 | 1.2493 | 4.0799 | 6.2763 | 9.217 | 11.5405 | 16.7537 | 22.8211 | 27.814 | 43.1908
51 | PMA | Southern | TTU2 | Tungatinah 22 kV | high | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0 | 0 | 0 | 0 | 1.957e-05 | 0.00011903 | 0.0002716 | 0.00046383 | 0.00058742 | 0.00080979 | 0.0011079 | 0.0016459 | 0.0021157 | 0.0033721 | 0.0047899 | 0.0063709 | 0.0081395 | 0.010106 | 0.012274 | 0.014645 | 0.017225 | 0.020017 | 0.023001 | 0.026176 | 0.029544 | 0.033108 | 0.036804 | 0.040634 | 0.044598 | 0.048698 | 0.052934 | 0.057309 | 0.061824 | 0.06648 | 0.071243 | 0.076115 | 0.081096 | 0.01957 | 0.11903 | 0.2716 | 0.46383 | 0.58742 | 0.80979 | 1.1079 | 1.6459 | 2.1157 | 3.3721
51 | PMA | Southern | TWA2 | Waddamana 22 kV | high | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0 | 0 | 0 | 0 | 6.9338e-05 | 0.00035532 | 0.00090348 | 0.0014634 | 0.0019146 | 0.0027466 | 0.0038394 | 0.0056991 | 0.0073727 | 0.011798 | 0.01683 | 0.022487 | 0.02887 | 0.03603 | 0.043996 | 0.052793 | 0.06245 | 0.073001 | 0.084389 | 0.096615 | 0.10971 | 0.1237 | 0.13835 | 0.15366 | 0.16965 | 0.18635 | 0.20377 | 0.22193 | 0.24086 | 0.26056 | 0.28092 | 0.30193 | 0.32362 | 0.069338 | 0.35532 | 0.90348 | 1.4634 | 1.9146 | 2.7466 | 3.8394 | 5.6991 | 7.3727 | 11.7977
51 | PMA | Western | TGO2 | Gordon | high | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0 | 0 | 0 | 0 | 1.3832e-06 | 8.4839e-06 | 1.9242e-05 | 3.3045e-05 | 4.1739e-05 | 5.7449e-05 | 7.8521e-05 | 0.00011763 | 0.00015373 | 0.00024684 | 0.0003524 | 0.00047054 | 0.00060317 | 0.00075107 | 0.00091452 | 0.0010938 | 0.0012891 | 0.0015009 | 0.0017276 | 0.0019691 | 0.0022257 | 0.0024974 | 0.0027795 | 0.003072 | 0.003375 | 0.0036886 | 0.0040129 | 0.004348 | 0.0046941 | 0.0050513 | 0.0054169 | 0.0057911 | 0.0061738 | 0.0013832 | 0.0084839 | 0.019242 | 0.033045 | 0.041739 | 0.057449 | 0.078521 | 0.11763 | 0.15373 | 0.24684
51 | PMA | Western | TNT2 | Newton 22 kV | high | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | PMA | Western | TNT3 | Ax-Newton 11 kV | high | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | Ax | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | PMA | Western | TQT2 | Queenstown 22 kV | high | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0 | 0 | 0 | 0 | 9.1654e-05 | 0.0002361 | 0.00049056 | 0.001174 | 0.0016275 | 0.0022676 | 0.0044148 | 0.0069982 | 0.0082419 | 0.012312 | 0.016808 | 0.021736 | 0.027159 | 0.033104 | 0.03958 | 0.046594 | 0.054156 | 0.062276 | 0.070905 | 0.080033 | 0.08967 | 0.099821 | 0.11032 | 0.12117 | 0.13237 | 0.14392 | 0.15583 | 0.16811 | 0.18075 | 0.19376 | 0.20704 | 0.22061 | 0.23447 | 0.091654 | 0.2361 | 0.49056 | 1.174 | 1.6275 | 2.2676 | 4.4148 | 6.9982 | 8.2419 | 12.3115
51 | PMA | Western | TQT3 | Queenstown 11 kV | high | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | Queenstown 11 kV | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | PMA | Western | TQU2 | Que | high | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | Que | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | PMA | Western | TRB2 | Rosebery 44 kV | high | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | Rosebery | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | PMA | Western | TSR2 | Savage River | high | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | Savage River | MI | 0 | 0 | 0 | 0 | 1.9607e-05 | 9.1384e-05 | 0.0002155 | 0.00034516 | 0.00047973 | 0.00060438 | 0.00082391 | 0.0011824 | 0.0015328 | 0.0024362 | 0.0034539 | 0.0045853 | 0.0058461 | 0.0072411 | 0.0087707 | 0.010435 | 0.012233 | 0.014166 | 0.01622 | 0.018389 | 0.020674 | 0.023075 | 0.025548 | 0.028092 | 0.030707 | 0.033393 | 0.036149 | 0.038975 | 0.041871 | 0.044835 | 0.047847 | 0.050907 | 0.054013 | 0.019607 | 0.091384 | 0.2155 | 0.34516 | 0.47973 | 0.60438 | 0.82391 | 1.1824 | 1.5328 | 2.4362
51 | PMA | Southern | BEZ | Bellerive | high | maximum | Battery | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0 | 0 | 0 | 0 | 0 | 0.0011522 | 0.0036454 | 0.0061422 | 0.0079498 | 0.011042 | 0.015641 | 0.02398 | 0.030958 | 0.049528 | 0.07057 | 0.094132 | 0.12061 | 0.15019 | 0.18295 | 0.21896 | 0.25832 | 0.30113 | 0.34712 | 0.39626 | 0.44865 | 0.50436 | 0.56239 | 0.62279 | 0.68559 | 0.75084 | 0.81857 | 0.88884 | 0.96168 | 1.0372 | 1.1147 | 1.1944 | 1.2762 | 0 | 1.1522 | 3.6454 | 6.1422 | 7.9498 | 11.0417 | 15.6408 | 23.9798 | 30.9582 | 49.5284
51 | PMA | Southern | CLZ | Claremont | high | maximum | Battery | non-coincident | POE50 | summer | zone | zone plus embedded | MW | 0 | Zs | 0 | 0 | 0 | 0 | 0 | 0.0023733 | 0.0049983 | 0.007835 | 0.010398 | 0.013929 | 0.019295 | 0.028514 | 0.037834 | 0.062277 | 0.089881 | 0.12067 | 0.1551 | 0.19337 | 0.23552 | 0.2816 | 0.33166 | 0.38575 | 0.44351 | 0.50485 | 0.56982 | 0.63845 | 0.70952 | 0.78303 | 0.85899 | 0.93741 | 1.0183 | 1.1017 | 1.1876 | 1.276 | 1.3664 | 1.4586 | 1.5527 | 0 | 2.3733 | 4.9983 | 7.835 | 10.3982 | 13.9289 | 19.2946 | 28.5136 | 37.8336 | 62.2766
51 | PMA | Southern | DPZ | Derwent Park | high | maximum | Battery | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0 | 0 | 0 | 0 | 0 | 0.00089199 | 0.0019393 | 0.0030523 | 0.0040367 | 0.0054766 | 0.007602 | 0.01126 | 0.014878 | 0.024374 | 0.035115 | 0.047112 | 0.060557 | 0.075525 | 0.092046 | 0.11014 | 0.12985 | 0.15119 | 0.17403 | 0.19833 | 0.22414 | 0.25147 | 0.27983 | 0.30924 | 0.3397 | 0.37122 | 0.40381 | 0.4375 | 0.47228 | 0.50819 | 0.54495 | 0.58257 | 0.62107 | 0 | 0.89199 | 1.9393 | 3.0523 | 4.0367 | 5.4766 | 7.602 | 11.2604 | 14.8776 | 24.3743
51 | PMA | Southern | EHZ | East Hobart | high | maximum | Battery | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0 | 0 | 0 | 0 | 0 | 0.00024612 | 0.00054165 | 0.00088445 | 0.0010909 | 0.0013969 | 0.0019103 | 0.0027773 | 0.0035486 | 0.0056714 | 0.0080537 | 0.010697 | 0.013639 | 0.016893 | 0.020464 | 0.024354 | 0.028566 | 0.033105 | 0.037939 | 0.04306 | 0.048473 | 0.054178 | 0.060075 | 0.066166 | 0.072448 | 0.078924 | 0.085593 | 0.092457 | 0.099517 | 0.10677 | 0.11417 | 0.12172 | 0.12941 | 0 | 0.24612 | 0.54165 | 0.88445 | 1.0909 | 1.3969 | 1.9103 | 2.7773 | 3.5486 | 5.6714
51 | PMA | Southern | GBZ | Geilston Bay | high | maximum | Battery | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0 | 0 | 0 | 0 | 0 | 0.0017655 | 0.005559 | 0.0093564 | 0.012111 | 0.016839 | 0.023847 | 0.036541 | 0.047176 | 0.075472 | 0.10754 | 0.14345 | 0.18382 | 0.22891 | 0.27887 | 0.33381 | 0.39385 | 0.45917 | 0.52935 | 0.60436 | 0.68435 | 0.7694 | 0.85804 | 0.9503 | 1.0463 | 1.146 | 1.2495 | 1.3569 | 1.4683 | 1.5837 | 1.7023 | 1.8242 | 1.9494 | 0 | 1.7655 | 5.559 | 9.3564 | 12.1106 | 16.8392 | 23.8473 | 36.5408 | 47.1761 | 75.4723
51 | PMA | Southern | GRZ | Gretna | high | maximum | Battery | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0 | 0 | 0 | 0 | 0 | 4.6565e-05 | 0.00010625 | 0.00018145 | 0.0002298 | 0.00031678 | 0.00043342 | 0.00064387 | 0.00082768 | 0.0013192 | 0.0018738 | 0.0024923 | 0.0031842 | 0.0039535 | 0.0048014 | 0.0057293 | 0.0067385 | 0.0078306 | 0.0089982 | 0.01024 | 0.011558 | 0.012952 | 0.014398 | 0.015896 | 0.017447 | 0.019051 | 0.020708 | 0.022419 | 0.024186 | 0.026007 | 0.027871 | 0.029776 | 0.031725 | 0 | 0.046565 | 0.10625 | 0.18145 | 0.2298 | 0.31678 | 0.43342 | 0.64387 | 0.82768 | 1.3192
51 | PMA | Southern | HOZ | Howrah | high | maximum | Battery | non-coincident | POE50 | summer | zone | zone plus embedded | MW | 0 | Zs | 0 | 0 | 0 | 0 | 0 | 0.0020148 | 0.0063739 | 0.010739 | 0.0139 | 0.019306 | 0.027347 | 0.041928 | 0.054129 | 0.086599 | 0.12339 | 0.16459 | 0.21089 | 0.2626 | 0.31988 | 0.38285 | 0.45167 | 0.52652 | 0.60693 | 0.69286 | 0.78446 | 0.88185 | 0.98332 | 1.0889 | 1.1987 | 1.3128 | 1.4312 | 1.5541 | 1.6815 | 1.8134 | 1.949 | 2.0883 | 2.2314 | 0 | 2.0148 | 6.3739 | 10.7395 | 13.9 | 19.3061 | 27.3474 | 41.9276 | 54.1293 | 86.5988
51 | PMA | Southern | NTZ | New Town | high | maximum | Battery | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0 | 0 | 0 | 0 | 0 | 0.0022529 | 0.0048252 | 0.0076953 | 0.0099002 | 0.013008 | 0.017924 | 0.026313 | 0.034406 | 0.056008 | 0.080345 | 0.10743 | 0.13768 | 0.17122 | 0.20812 | 0.24839 | 0.29209 | 0.33925 | 0.38956 | 0.44294 | 0.49941 | 0.55902 | 0.6207 | 0.68445 | 0.75028 | 0.81819 | 0.88819 | 0.9603 | 1.0345 | 1.1109 | 1.1888 | 1.2683 | 1.3494 | 0 | 2.2529 | 4.8252 | 7.6953 | 9.9002 | 13.0079 | 17.9238 | 26.313 | 34.406 | 56.0079
51 | PMA | Southern | RIZ | Richmond | high | maximum | Battery | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0 | 0 | 0 | 0 | 0 | 0.00049651 | 0.0013642 | 0.002303 | 0.0030612 | 0.0042216 | 0.0059294 | 0.0088472 | 0.01156 | 0.0186 | 0.026578 | 0.035507 | 0.045533 | 0.056715 | 0.069079 | 0.082645 | 0.097438 | 0.11349 | 0.13069 | 0.14903 | 0.16852 | 0.1892 | 0.2107 | 0.23301 | 0.25615 | 0.28014 | 0.30499 | 0.3307 | 0.35729 | 0.38478 | 0.41297 | 0.44187 | 0.47149 | 0 | 0.49651 | 1.3642 | 2.303 | 3.0612 | 4.2216 | 5.9294 | 8.8472 | 11.56 | 18.5996
51 | PMA | Southern | RPZ | Rosny Park | high | maximum | Battery | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0 | 0 | 0 | 0 | 0 | 0.001236 | 0.0039104 | 0.0065887 | 0.0085277 | 0.011844 | 0.016778 | 0.025723 | 0.033209 | 0.053129 | 0.0757 | 0.10098 | 0.12938 | 0.16111 | 0.19625 | 0.23488 | 0.2771 | 0.32302 | 0.37235 | 0.42507 | 0.48127 | 0.54102 | 0.60328 | 0.66807 | 0.73543 | 0.80542 | 0.87808 | 0.95345 | 1.0316 | 1.1126 | 1.1957 | 1.2812 | 1.369 | 0 | 1.236 | 3.9104 | 6.5887 | 8.5277 | 11.8444 | 16.7778 | 25.7231 | 33.2088 | 53.129
51 | PMA | Southern | SBZ | Sandy Bay | high | maximum | Battery | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0 | 0 | 0 | 0 | 0 | 0.0043081 | 0.010311 | 0.017079 | 0.021252 | 0.02737 | 0.037111 | 0.053998 | 0.069334 | 0.11113 | 0.15815 | 0.21044 | 0.26878 | 0.33347 | 0.40462 | 0.4823 | 0.56661 | 0.65766 | 0.75485 | 0.85804 | 0.96732 | 1.0828 | 1.2023 | 1.3261 | 1.4539 | 1.586 | 1.7223 | 1.8629 | 2.0077 | 2.1569 | 2.3094 | 2.4651 | 2.6241 | 0 | 4.3081 | 10.3108 | 17.0793 | 21.2519 | 27.3703 | 37.1115 | 53.9985 | 69.334 | 111.129
51 | PMA | Southern | SUZ | Summerleas Road | high | maximum | Battery | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0 | 0 | 0 | 0 | 0 | 0.0013928 | 0.0045151 | 0.007797 | 0.009941 | 0.013007 | 0.017229 | 0.025125 | 0.032696 | 0.052813 | 0.07559 | 0.10107 | 0.12968 | 0.1616 | 0.19691 | 0.23568 | 0.27801 | 0.32398 | 0.3733 | 0.42594 | 0.48199 | 0.5415 | 0.60343 | 0.66781 | 0.73465 | 0.80402 | 0.87593 | 0.95044 | 1.0276 | 1.1074 | 1.1893 | 1.2734 | 1.3596 | 0 | 1.3928 | 4.5151 | 7.797 | 9.941 | 13.0067 | 17.2291 | 25.1251 | 32.6956 | 52.8132
51 | PMA | Southern | TWY2 | Wayatinah | high | maximum | Battery | non-coincident | POE50 | summer | zone | zone | MW | 0 | RT | 0 | 0 | 0 | 0 | 4.5648e-06 | 2.7764e-05 | 6.3353e-05 | 0.00010819 | 0.00013702 | 0.00018889 | 0.00025843 | 0.00038392 | 0.0004935 | 0.00078653 | 0.0011172 | 0.001486 | 0.0018985 | 0.0023571 | 0.0028627 | 0.003416 | 0.0040176 | 0.0046687 | 0.0053649 | 0.0061054 | 0.0068909 | 0.0077221 | 0.0085842 | 0.0094775 | 0.010402 | 0.011358 | 0.012346 | 0.013367 | 0.01442 | 0.015506 | 0.016617 | 0.017753 | 0.018915 | 0.0045648 | 0.027764 | 0.063353 | 0.10819 | 0.13702 | 0.18889 | 0.25843 | 0.38392 | 0.4935 | 0.78653
51 | PMA | Southern | WHZ | West Hobart Zone | high | maximum | Battery | non-coincident | POE50 | summer | zone | zone plus embedded | MW | 0 | Zs | 0 | 0 | 0 | 0 | 0 | 0.0036555 | 0.0083445 | 0.013713 | 0.016982 | 0.021801 | 0.029699 | 0.043194 | 0.055312 | 0.088515 | 0.12582 | 0.16725 | 0.21341 | 0.26454 | 0.3207 | 0.38194 | 0.44831 | 0.51992 | 0.59625 | 0.67721 | 0.76285 | 0.85321 | 0.9467 | 1.0433 | 1.1431 | 1.246 | 1.3522 | 1.4615 | 1.574 | 1.6898 | 1.808 | 1.9286 | 2.0516 | 0 | 3.6555 | 8.3445 | 13.7133 | 16.9817 | 21.8009 | 29.6991 | 43.194 | 55.3121 | 88.5146
51 | PMA | Western | THZ | Trial Harbour | high | maximum | Battery | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0 | 0 | 0 | 0 | 0 | 7.7555e-05 | 0.00016114 | 0.00038565 | 0.00053461 | 0.00074486 | 0.0014502 | 0.0022988 | 0.0027073 | 0.0040441 | 0.0055211 | 0.0071397 | 0.0089211 | 0.010874 | 0.013001 | 0.015305 | 0.017789 | 0.020456 | 0.023291 | 0.026289 | 0.029455 | 0.032789 | 0.036238 | 0.039801 | 0.04348 | 0.047275 | 0.051188 | 0.05522 | 0.059372 | 0.063645 | 0.06801 | 0.072467 | 0.077018 | 0 | 0.077555 | 0.16114 | 0.38565 | 0.53461 | 0.74486 | 1.4502 | 2.2988 | 2.7073 | 4.0441
51 | PMA | Western | RBZ | Rosebery 22 kV | high | maximum | Battery | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0 | 0 | 0 | 0 | 8.151e-05 | 0.00024647 | 0.00053498 | 0.001128 | 0.0015649 | 0.0021232 | 0.0038186 | 0.0059427 | 0.007124 | 0.010773 | 0.014821 | 0.019273 | 0.024185 | 0.029582 | 0.03547 | 0.041855 | 0.048741 | 0.056138 | 0.063997 | 0.072309 | 0.081078 | 0.09031 | 0.099849 | 0.1097 | 0.11985 | 0.13032 | 0.1411 | 0.15219 | 0.16361 | 0.17534 | 0.18731 | 0.19951 | 0.21196 | 0.08151 | 0.24647 | 0.53498 | 1.128 | 1.5649 | 2.1232 | 3.8186 | 5.9427 | 7.124 | 10.7726
51 | PMA | total terminal |  | total terminal | high | maximum | Battery | non-coincident | POE50 | summer | zone | zone | MW | #N/A | #N/A | 0 | 0 | 0 | 0 | 0.034477 | 0.13522 | 0.36171 | 0.59079 | 0.76773 | 0.99551 | 1.3517 | 1.9361 | 2.5217 | 4.0498 | 5.7794 | 7.7127 | 9.8803 | 12.2949 | 14.9611 | 17.8829 | 21.0648 | 24.5125 | 28.2028 | 32.1316 | 36.3037 | 40.7226 | 45.3094 | 50.0655 | 54.9922 | 60.0918 | 65.366 | 70.8167 | 76.4468 | 82.2585 | 88.2089 | 94.2999 | 100.5333 | 34.4766 | 135.2206 | 361.7143 | 590.7933 | 767.7301 | 995.5084 | 1351.6796 | 1936.1089 | 2521.6923 | 4049.8381
51 | PMA | total zone |  | total zone | high | maximum | Battery | non-coincident | POE50 | summer | zone | zone | MW | #N/A | #N/A | 0 | 0 | 0 | 0 | 8.6075e-05 | 0.02292 | 0.059521 | 0.098911 | 0.12669 | 0.16966 | 0.23626 | 0.35278 | 0.45596 | 0.73266 | 1.0451 | 1.3938 | 1.7843 | 2.2188 | 2.6983 | 3.2237 | 3.7957 | 4.4155 | 5.0791 | 5.7859 | 6.5367 | 7.3322 | 8.1584 | 9.0157 | 9.9042 | 10.8243 | 11.7766 | 12.7614 | 13.7791 | 14.8303 | 15.9072 | 17.0103 | 18.1397 | 0.086075 | 22.9196 | 59.5206 | 98.9109 | 126.6913 | 169.664 | 236.259 | 352.7788 | 455.9566 | 732.6571
48 | PMA | George Town | TC01 | Comalco | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Camalco | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | George Town | TSW1 | Starwood | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Starwood | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | George Town | TTE1 | Temco | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Temco | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | North | TAL2 | Ax-Arthurs Lake 6.6 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | Ax | 0.00034908 | 0.00039755 | 0.00047542 | 0.00056389 | 0.00064917 | 0.0007212 | 0.00077566 | 0.00082811 | 0.00087891 | 0.00092637 | 0.00097104 | 0.0010132 | 0.0010523 | 0.0010886 | 0.0011232 | 0.0011555 | 0.0011856 | 0.0012147 | 0.0012432 | 0.0012709 | 0.0012977 | 0.0013234 | 0.0013482 | 0.0013722 | 0.0013952 | 0.0014175 | 0.0014391 | 0.0014596 | 0.0014795 | 0.0014985 | 0.0015167 | 0.0015342 | 0.001551 | 0.0015671 | 0.0015828 | 0.001598 | 0.0016127 | 0.64917 | 0.7212 | 0.77566 | 0.82811 | 0.87891 | 0.92637 | 0.97104 | 1.0132 | 1.0523 | 1.0886
48 | PMA | North | TAV2 | Avoca 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0.11792 | 0.14942 | 0.17489 | 0.19931 | 0.22958 | 0.26204 | 0.29118 | 0.31925 | 0.3461 | 0.37103 | 0.39432 | 0.41615 | 0.43622 | 0.45472 | 0.47219 | 0.48838 | 0.50334 | 0.51772 | 0.53167 | 0.54513 | 0.55805 | 0.57031 | 0.58208 | 0.59338 | 0.6041 | 0.61441 | 0.62427 | 0.63362 | 0.64256 | 0.65106 | 0.65913 | 0.66681 | 0.6741 | 0.68107 | 0.68775 | 0.69418 | 0.70037 | 229.5798 | 262.0416 | 291.1835 | 319.246 | 346.0993 | 371.0291 | 394.3222 | 416.1455 | 436.222 | 454.715
48 | PMA | North | TDE2 | Derby 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0.33085 | 0.3803 | 0.44369 | 0.5035 | 0.56922 | 0.63485 | 0.69251 | 0.7477 | 0.79989 | 0.84791 | 0.89239 | 0.93359 | 0.97114 | 1.0054 | 1.0374 | 1.0668 | 1.0936 | 1.1192 | 1.1438 | 1.1672 | 1.1895 | 1.2105 | 1.2304 | 1.2494 | 1.2671 | 1.2841 | 1.3002 | 1.3152 | 1.3295 | 1.343 | 1.3556 | 1.3676 | 1.3788 | 1.3894 | 1.3995 | 1.4091 | 1.4183 | 569.2204 | 634.8544 | 692.5107 | 747.7021 | 799.8929 | 847.9126 | 892.3895 | 933.5934 | 971.1352 | 1005.3678
48 | PMA | North | THA3 | Hadspen 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 2.9419 | 3.5359 | 4.1462 | 4.8132 | 5.594 | 6.3762 | 7.1135 | 7.8189 | 8.4918 | 9.1155 | 9.6963 | 10.2392 | 10.7373 | 11.1948 | 11.6259 | 12.0244 | 12.3915 | 12.7434 | 13.0838 | 13.4115 | 13.7251 | 14.0218 | 14.3061 | 14.5782 | 14.8355 | 15.0824 | 15.318 | 15.5408 | 15.7531 | 15.9544 | 16.1452 | 16.326 | 16.4974 | 16.6607 | 16.8169 | 16.9668 | 17.1106 | 5593.967 | 6376.1529 | 7113.4569 | 7818.8826 | 8491.8215 | 9115.4758 | 9696.3055 | 10239.2168 | 10737.2588 | 11194.7564
48 | PMA | North | TMY2 | Mowbray 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0.9257 | 1.1315 | 1.351 | 1.5707 | 1.7848 | 1.9648 | 2.1296 | 2.2857 | 2.4344 | 2.5712 | 2.6979 | 2.8157 | 2.9232 | 3.0214 | 3.1135 | 3.1981 | 3.2756 | 3.3494 | 3.4205 | 3.4886 | 3.5533 | 3.6142 | 3.6723 | 3.7275 | 3.7795 | 3.829 | 3.8761 | 3.9203 | 3.9622 | 4.0017 | 4.0389 | 4.074 | 4.107 | 4.1383 | 4.1681 | 4.1965 | 4.2236 | 1784.8481 | 1964.7566 | 2129.6241 | 2285.6724 | 2434.3915 | 2571.1787 | 2697.8737 | 2815.7368 | 2923.2225 | 3021.4243
48 | PMA | North | TPM3 | Palmerston 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | North | TSD2 | Scottsdale 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0.68795 | 0.77766 | 0.89744 | 1.0187 | 1.1449 | 1.2718 | 1.3856 | 1.4943 | 1.5973 | 1.6921 | 1.7799 | 1.8614 | 1.9357 | 2.0035 | 2.067 | 2.1253 | 2.1787 | 2.2295 | 2.2783 | 2.3251 | 2.3695 | 2.4113 | 2.4511 | 2.489 | 2.5246 | 2.5586 | 2.5908 | 2.621 | 2.6497 | 2.6767 | 2.7022 | 2.7262 | 2.7488 | 2.7703 | 2.7906 | 2.8101 | 2.8287 | 1144.9025 | 1271.8 | 1385.6446 | 1494.3068 | 1597.2659 | 1692.0602 | 1779.9103 | 1861.393 | 1935.6886 | 2003.4982
48 | PMA | North | TSL2 | St Leonards 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 1.3143 | 1.5404 | 1.8154 | 2.142 | 2.4434 | 2.6818 | 2.9004 | 3.1074 | 3.3047 | 3.4862 | 3.6542 | 3.8106 | 3.9533 | 4.0836 | 4.2057 | 4.318 | 4.4209 | 4.5189 | 4.6133 | 4.7036 | 4.7896 | 4.8705 | 4.9476 | 5.0209 | 5.0899 | 5.1558 | 5.2182 | 5.277 | 5.3326 | 5.3851 | 5.4346 | 5.4812 | 5.5251 | 5.5668 | 5.6063 | 5.6441 | 5.6801 | 2443.3811 | 2681.7732 | 2900.4355 | 3107.427 | 3304.695 | 3486.1592 | 3654.2466 | 3810.6275 | 3953.2512 | 4083.5657
48 | PMA | North | TSL3 | St Leonards 22 kV (scheduled load) | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Firmus Grid | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | North | TSM2 | St Marys 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0.94174 | 1.1809 | 1.4436 | 1.6677 | 1.8961 | 2.0737 | 2.2147 | 2.3494 | 2.4786 | 2.5973 | 2.7078 | 2.8108 | 2.905 | 2.9914 | 3.0725 | 3.1473 | 3.216 | 3.2817 | 3.3451 | 3.4059 | 3.464 | 3.5188 | 3.5712 | 3.6212 | 3.6683 | 3.7135 | 3.7564 | 3.7969 | 3.8354 | 3.8718 | 3.9063 | 3.9388 | 3.9696 | 3.9988 | 4.0267 | 4.0534 | 4.0789 | 1896.118 | 2073.7058 | 2214.748 | 2349.417 | 2478.5671 | 2597.346 | 2707.8062 | 2810.8256 | 2905.03 | 2991.3556
48 | PMA | Northwest | TDP2 | Devonport 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 1.8825 | 2.1757 | 2.5355 | 2.9784 | 3.4419 | 3.8174 | 4.126 | 4.4196 | 4.7 | 4.959 | 5.1996 | 5.4241 | 5.6294 | 5.8176 | 5.9945 | 6.1576 | 6.3075 | 6.4507 | 6.5891 | 6.7218 | 6.8486 | 6.9683 | 7.0826 | 7.1919 | 7.2948 | 7.3935 | 7.4873 | 7.5758 | 7.66 | 7.7396 | 7.8149 | 7.886 | 7.9533 | 8.0173 | 8.0783 | 8.1367 | 8.1926 | 3441.8621 | 3817.4032 | 4126.0268 | 4419.5824 | 4700.0363 | 4958.9612 | 5199.635 | 5424.0693 | 5629.4072 | 5817.586
48 | PMA | Northwest | TEB2 | Emu Bay 11 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Emu Bay | MI | 0.13673 | 0.16675 | 0.19871 | 0.23161 | 0.26534 | 0.29275 | 0.31225 | 0.33053 | 0.34802 | 0.36396 | 0.37866 | 0.39227 | 0.40462 | 0.41584 | 0.4263 | 0.43586 | 0.44458 | 0.45284 | 0.46075 | 0.46828 | 0.47541 | 0.48208 | 0.48841 | 0.4944 | 0.5 | 0.50531 | 0.51033 | 0.51502 | 0.51945 | 0.5236 | 0.52748 | 0.53113 | 0.53455 | 0.53777 | 0.54081 | 0.5437 | 0.54645 | 265.3371 | 292.7451 | 312.2479 | 330.5276 | 348.0208 | 363.9613 | 378.6647 | 392.275 | 404.6173 | 415.8369
48 | PMA | Northwest | THM2 | Hampshire | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Hampshire | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Northwest | TPL2 | Port Latta | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | Port Latta | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Northwest | TRA2 | Railton 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Northwest | TSH3 | Sheffield | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Northwest | TST2 | Smithton 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0.11298 | 0.13907 | 0.1642 | 0.18346 | 0.21307 | 0.24741 | 0.28166 | 0.31476 | 0.3456 | 0.3741 | 0.40037 | 0.42462 | 0.44666 | 0.46668 | 0.48535 | 0.50243 | 0.51798 | 0.53273 | 0.54685 | 0.5603 | 0.57303 | 0.58495 | 0.59624 | 0.60693 | 0.61693 | 0.62643 | 0.63539 | 0.64377 | 0.65167 | 0.65908 | 0.66603 | 0.67254 | 0.67865 | 0.6844 | 0.68985 | 0.69501 | 0.69991 | 213.0668 | 247.4094 | 281.6624 | 314.7564 | 345.5951 | 374.1009 | 400.3736 | 424.6187 | 446.6622 | 466.6846
48 | PMA | Northwest | TUL2 | Ulverstone 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 2.3973 | 2.7385 | 3.152 | 3.6105 | 4.1166 | 4.5701 | 4.9342 | 5.2795 | 5.6085 | 5.9113 | 6.1917 | 6.4523 | 6.69 | 6.907 | 7.1104 | 7.2972 | 7.4683 | 7.6313 | 7.7881 | 7.9381 | 8.0809 | 8.2151 | 8.343 | 8.4646 | 8.5789 | 8.688 | 8.7915 | 8.8886 | 8.9807 | 9.0675 | 9.1493 | 9.2263 | 9.2988 | 9.3675 | 9.4328 | 9.4951 | 9.5545 | 4116.5699 | 4570.097 | 4934.2228 | 5279.4811 | 5608.5022 | 5911.3163 | 6191.6824 | 6452.3257 | 6689.9917 | 6907.033
48 | PMA | Northwest | TWV2 | Wesley Vale 11 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | Wesley Vale | MI | 0.36594 | 0.43045 | 0.52262 | 0.62956 | 0.73429 | 0.82744 | 0.91217 | 0.9937 | 1.0723 | 1.1458 | 1.215 | 1.2802 | 1.3405 | 1.3964 | 1.4496 | 1.4993 | 1.5454 | 1.59 | 1.6335 | 1.6758 | 1.7167 | 1.7557 | 1.7934 | 1.8298 | 1.8646 | 1.8982 | 1.9306 | 1.9615 | 1.9912 | 2.0196 | 2.0468 | 2.0728 | 2.0977 | 2.1216 | 2.1447 | 2.167 | 2.1886 | 734.2942 | 827.4446 | 912.1748 | 993.7003 | 1072.3061 | 1145.8406 | 1214.9565 | 1280.1575 | 1340.4996 | 1396.4433
48 | PMA | Southern | TBW2 | Bridgewater 11 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 1.6264 | 1.8376 | 2.1832 | 2.5897 | 2.9725 | 3.2896 | 3.5297 | 3.7611 | 3.9854 | 4.195 | 4.3925 | 4.5792 | 4.7523 | 4.9131 | 5.0663 | 5.2095 | 5.3429 | 5.4723 | 5.5988 | 5.722 | 5.8413 | 5.9554 | 6.0661 | 6.1732 | 6.2756 | 6.3752 | 6.4712 | 6.5631 | 6.6517 | 6.7367 | 6.8183 | 6.8965 | 6.9715 | 7.0438 | 7.1139 | 7.1819 | 7.248 | 2972.4663 | 3289.5635 | 3529.7436 | 3761.1438 | 3985.3753 | 4195.0464 | 4392.539 | 4579.2239 | 4752.2984 | 4913.0967
48 | PMA | Southern | TBYA | Boyer SWA | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Boyer | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Southern | TBYB | Boyer SWB | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Boyer | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Southern | TCR2 | Creek Rd 33 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 2.5047 | 2.8775 | 3.3595 | 3.9287 | 4.5636 | 5.1389 | 5.5827 | 6.0034 | 6.4063 | 6.7785 | 7.1246 | 7.4479 | 7.744 | 8.0156 | 8.2713 | 8.5072 | 8.7243 | 8.932 | 9.1328 | 9.3258 | 9.5102 | 9.6845 | 9.8512 | 10.0106 | 10.1611 | 10.3053 | 10.4428 | 10.5725 | 10.696 | 10.813 | 10.9237 | 11.0285 | 11.1277 | 11.222 | 11.3121 | 11.3985 | 11.4813 | 4563.6299 | 5138.933 | 5582.673 | 6003.4019 | 6406.3186 | 6778.4881 | 7124.6308 | 7447.9318 | 7743.9852 | 8015.6085
48 | PMA | Southern | TCS3 | Chapel St 11 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 1.0991 | 1.249 | 1.4605 | 1.7133 | 1.9893 | 2.2592 | 2.4809 | 2.6903 | 2.8907 | 3.0757 | 3.2476 | 3.4081 | 3.555 | 3.6897 | 3.8163 | 3.9331 | 4.0405 | 4.1432 | 4.2424 | 4.3376 | 4.4286 | 4.5145 | 4.5966 | 4.675 | 4.749 | 4.8199 | 4.8874 | 4.951 | 5.0115 | 5.0688 | 5.123 | 5.1742 | 5.2226 | 5.2687 | 5.3126 | 5.3547 | 5.3949 | 1989.2595 | 2259.1565 | 2480.9457 | 2690.32 | 2890.6985 | 3075.6964 | 3247.6354 | 3408.1374 | 3554.9975 | 3689.6523
48 | PMA | Southern | TDB2 | Derwent Bridge 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0.0058532 | 0.0066611 | 0.0076296 | 0.0087712 | 0.010037 | 0.011187 | 0.012055 | 0.012881 | 0.013673 | 0.014407 | 0.015091 | 0.015732 | 0.01632 | 0.016861 | 0.017371 | 0.017843 | 0.018279 | 0.018696 | 0.019101 | 0.019491 | 0.019864 | 0.020218 | 0.020557 | 0.020882 | 0.02119 | 0.021485 | 0.021768 | 0.022035 | 0.02229 | 0.022532 | 0.022762 | 0.022979 | 0.023186 | 0.023383 | 0.023572 | 0.023753 | 0.023927 | 10.0369 | 11.1874 | 12.0551 | 12.8811 | 13.6731 | 14.4073 | 15.0915 | 15.7321 | 16.3201 | 16.8609
48 | PMA | Southern | TEL2 | Electrona 11 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0.27974 | 0.31639 | 0.3626 | 0.41424 | 0.46804 | 0.52105 | 0.56432 | 0.60568 | 0.64542 | 0.68239 | 0.71697 | 0.74946 | 0.77939 | 0.80702 | 0.83317 | 0.85745 | 0.87992 | 0.90155 | 0.92258 | 0.94291 | 0.96245 | 0.98102 | 0.9989 | 1.0161 | 1.0324 | 1.0481 | 1.0632 | 1.0775 | 1.0912 | 1.1043 | 1.1167 | 1.1285 | 1.1398 | 1.1506 | 1.1609 | 1.1709 | 1.1805 | 468.0364 | 521.047 | 564.3236 | 605.6753 | 645.4209 | 682.387 | 716.9719 | 749.463 | 779.3929 | 807.0167
48 | PMA | Southern | THR2 | Huon River | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Huon River | MI | 0.00077139 | 0.00089743 | 0.0010512 | 0.0012212 | 0.001407 | 0.0015801 | 0.0017183 | 0.0018512 | 0.0019797 | 0.0020995 | 0.0022121 | 0.0023183 | 0.0024165 | 0.0025074 | 0.0025939 | 0.0026744 | 0.0027492 | 0.0028215 | 0.002892 | 0.0029604 | 0.0030264 | 0.0030894 | 0.0031503 | 0.003209 | 0.0032649 | 0.0033191 | 0.0033711 | 0.0034208 | 0.0034685 | 0.0035141 | 0.0035576 | 0.0035992 | 0.003639 | 0.0036771 | 0.003714 | 0.0037496 | 0.003784 | 1.407 | 1.5801 | 1.7183 | 1.8512 | 1.9797 | 2.0995 | 2.2121 | 2.3183 | 2.4165 | 2.5074
48 | PMA | Southern | TK12 | Kingston 11 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 1.7336 | 1.9837 | 2.3406 | 2.7539 | 3.1922 | 3.5846 | 3.9058 | 4.2128 | 4.5078 | 4.7822 | 5.039 | 5.2802 | 5.5025 | 5.7076 | 5.9018 | 6.0822 | 6.2491 | 6.4098 | 6.566 | 6.717 | 6.8622 | 7.0002 | 7.1331 | 7.2608 | 7.3821 | 7.499 | 7.6111 | 7.7175 | 7.8194 | 7.9165 | 8.0089 | 8.0968 | 8.1806 | 8.2607 | 8.3377 | 8.4118 | 8.4833 | 3192.219 | 3584.623 | 3905.8354 | 4212.7778 | 4507.7941 | 4782.2149 | 5038.9766 | 5280.2171 | 5502.459 | 5707.5939
48 | PMA | Southern | TK13 | Kingston 33 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Southern | TKE2 | Kermandie 11 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0.20696 | 0.24483 | 0.28985 | 0.33256 | 0.3827 | 0.42947 | 0.46676 | 0.50262 | 0.5373 | 0.56966 | 0.60007 | 0.62874 | 0.65526 | 0.67982 | 0.70317 | 0.72493 | 0.74514 | 0.76468 | 0.78374 | 0.80224 | 0.8201 | 0.83712 | 0.85358 | 0.86946 | 0.88459 | 0.89924 | 0.91333 | 0.92676 | 0.93967 | 0.95201 | 0.9638 | 0.97506 | 0.98583 | 0.99617 | 1.0061 | 1.0158 | 1.0251 | 382.698 | 429.4741 | 466.7629 | 502.6209 | 537.3003 | 569.6585 | 600.071 | 628.7414 | 655.2563 | 679.8248
48 | PMA | Southern | TLF2 | Lindisfarne 33 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 1.3376 | 1.5206 | 1.7944 | 2.1302 | 2.5108 | 2.8549 | 3.1117 | 3.358 | 3.5951 | 3.8161 | 4.0232 | 4.2181 | 4.398 | 4.5643 | 4.722 | 4.8687 | 5.0046 | 5.1358 | 5.2634 | 5.3871 | 5.5062 | 5.6196 | 5.7289 | 5.8341 | 5.9343 | 6.031 | 6.1238 | 6.2121 | 6.2968 | 6.3776 | 6.4547 | 6.5281 | 6.5982 | 6.6653 | 6.7299 | 6.7923 | 6.8525 | 2510.7635 | 2854.9382 | 3111.6989 | 3358.0279 | 3595.0685 | 3816.0948 | 4023.2369 | 4218.1141 | 4397.9871 | 4564.2812
48 | PMA | Southern | TMB2 | Meadowbank 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Southern | TMT2 | Mornington 33 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 1.8847 | 2.1391 | 2.5251 | 3.0197 | 3.594 | 4.1066 | 4.4887 | 4.8552 | 5.2077 | 5.5364 | 5.8443 | 6.1338 | 6.401 | 6.648 | 6.8821 | 7.0998 | 7.3015 | 7.496 | 7.6853 | 7.8685 | 8.045 | 8.2129 | 8.3747 | 8.5305 | 8.6787 | 8.8217 | 8.959 | 9.0895 | 9.2146 | 9.3339 | 9.4477 | 9.5561 | 9.6594 | 9.7584 | 9.8537 | 9.9457 | 10.0344 | 3593.9952 | 4106.5919 | 4488.7071 | 4855.2004 | 5207.7406 | 5536.3757 | 5844.2698 | 6133.8407 | 6401.0359 | 6647.9801
48 | PMA | Southern | TNH2 | North Hobart 11 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0.45368 | 0.51946 | 0.59562 | 0.68753 | 0.79962 | 0.8991 | 0.97258 | 1.0422 | 1.1088 | 1.1702 | 1.2272 | 1.2804 | 1.329 | 1.3734 | 1.4152 | 1.4537 | 1.4891 | 1.5228 | 1.5554 | 1.5867 | 1.6165 | 1.6446 | 1.6714 | 1.697 | 1.7211 | 1.7442 | 1.7662 | 1.7868 | 1.8065 | 1.825 | 1.8426 | 1.8591 | 1.8748 | 1.8896 | 1.9038 | 1.9173 | 1.9302 | 799.6171 | 899.097 | 972.5847 | 1042.2182 | 1108.834 | 1170.2327 | 1227.2359 | 1280.3796 | 1328.9571 | 1373.442
48 | PMA | Southern | TNN2 | New Norfolk 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | Brynn Estyn | MI | 0.14705 | 0.1672 | 0.19176 | 0.22064 | 0.25239 | 0.28116 | 0.30285 | 0.32352 | 0.34335 | 0.36173 | 0.37887 | 0.39493 | 0.40967 | 0.42324 | 0.43605 | 0.4479 | 0.45884 | 0.46933 | 0.47951 | 0.48932 | 0.49872 | 0.50763 | 0.51618 | 0.52438 | 0.53214 | 0.5396 | 0.54673 | 0.55348 | 0.55993 | 0.56606 | 0.57187 | 0.57739 | 0.58263 | 0.58763 | 0.59242 | 0.59703 | 0.60145 | 252.3942 | 281.1583 | 302.854 | 323.5219 | 343.3459 | 361.7304 | 378.8717 | 394.927 | 409.6728 | 423.24
48 | PMA | Southern | TR13 | Risdon 11 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Risdon | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Southern | TR14 | Risdon 33 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0.91939 | 1.0443 | 1.201 | 1.4 | 1.6344 | 1.8461 | 2.0147 | 2.1742 | 2.3269 | 2.4679 | 2.599 | 2.7214 | 2.8334 | 2.9362 | 3.0329 | 3.1221 | 3.2042 | 3.2827 | 3.3586 | 3.4315 | 3.5011 | 3.5669 | 3.6298 | 3.69 | 3.7468 | 3.8011 | 3.853 | 3.9019 | 3.9484 | 3.9925 | 4.0342 | 4.0736 | 4.1109 | 4.1464 | 4.1804 | 4.2129 | 4.244 | 1634.3882 | 1846.1445 | 2014.7367 | 2174.1912 | 2326.8722 | 2467.8637 | 2598.9549 | 2721.3655 | 2833.419 | 2936.1986
48 | PMA | Southern | TRK2 | Rokeby 11 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 1.607 | 1.8442 | 2.1931 | 2.634 | 3.1514 | 3.6062 | 3.9452 | 4.2704 | 4.5831 | 4.8747 | 5.1478 | 5.4047 | 5.6417 | 5.8607 | 6.0684 | 6.2615 | 6.4404 | 6.6129 | 6.7808 | 6.9433 | 7.0998 | 7.2487 | 7.3922 | 7.5304 | 7.6618 | 7.7886 | 7.9103 | 8.0261 | 8.137 | 8.2428 | 8.3437 | 8.4398 | 8.5314 | 8.6192 | 8.7037 | 8.7852 | 8.8638 | 3151.4324 | 3606.2137 | 3945.2245 | 4270.3678 | 4583.123 | 4874.6652 | 5147.8004 | 5404.6749 | 5641.6945 | 5860.7448
48 | PMA | Southern | TS02 | Sorell | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0.7646 | 0.89123 | 1.0632 | 1.2586 | 1.4757 | 1.6708 | 1.8174 | 1.958 | 2.0937 | 2.2205 | 2.3394 | 2.4516 | 2.5553 | 2.6514 | 2.7427 | 2.8278 | 2.9068 | 2.9832 | 3.0578 | 3.1301 | 3.2 | 3.2666 | 3.331 | 3.3932 | 3.4525 | 3.5098 | 3.5651 | 3.6177 | 3.6684 | 3.7168 | 3.7631 | 3.8073 | 3.8497 | 3.8903 | 3.9296 | 3.9676 | 4.0044 | 1475.689 | 1670.7518 | 1817.4261 | 1958.011 | 2093.729 | 2220.4639 | 2339.4214 | 2451.6002 | 2555.3157 | 2651.3958
48 | PMA | Southern | TTB2 | Triabunna 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0.15761 | 0.19624 | 0.23445 | 0.27077 | 0.31435 | 0.34859 | 0.37417 | 0.39867 | 0.42226 | 0.44416 | 0.46466 | 0.4839 | 0.50162 | 0.51798 | 0.53345 | 0.54781 | 0.5611 | 0.57389 | 0.58632 | 0.59834 | 0.60989 | 0.62086 | 0.63142 | 0.64157 | 0.6512 | 0.6605 | 0.6694 | 0.67785 | 0.68594 | 0.69365 | 0.70099 | 0.70797 | 0.71462 | 0.72098 | 0.72709 | 0.73298 | 0.73866 | 314.355 | 348.5916 | 374.1659 | 398.6692 | 422.2581 | 444.1642 | 464.657 | 483.9021 | 501.6239 | 517.9751
48 | PMA | Southern | TTU2 | Tungatinah 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0.041793 | 0.047521 | 0.054392 | 0.06249 | 0.071464 | 0.079621 | 0.085772 | 0.091629 | 0.097243 | 0.10245 | 0.1073 | 0.11184 | 0.11601 | 0.11984 | 0.12346 | 0.12681 | 0.12989 | 0.13286 | 0.13572 | 0.13849 | 0.14113 | 0.14364 | 0.14605 | 0.14835 | 0.15053 | 0.15263 | 0.15463 | 0.15652 | 0.15833 | 0.16005 | 0.16168 | 0.16322 | 0.16469 | 0.16608 | 0.16742 | 0.16871 | 0.16994 | 71.4638 | 79.6206 | 85.7719 | 91.6286 | 97.2434 | 102.4486 | 107.2993 | 111.8408 | 116.0099 | 119.844
48 | PMA | Southern | TWA2 | Waddamana 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0.017701 | 0.02016 | 0.02411 | 0.028596 | 0.032926 | 0.036587 | 0.039356 | 0.042023 | 0.044605 | 0.047018 | 0.049289 | 0.051434 | 0.053422 | 0.055267 | 0.057024 | 0.058665 | 0.060192 | 0.061672 | 0.06312 | 0.064528 | 0.065891 | 0.067193 | 0.068455 | 0.069677 | 0.070844 | 0.071978 | 0.073071 | 0.074116 | 0.075123 | 0.07609 | 0.077016 | 0.077904 | 0.078755 | 0.079575 | 0.080369 | 0.08114 | 0.081888 | 32.926 | 36.5869 | 39.3562 | 42.0228 | 44.6052 | 47.018 | 49.289 | 51.4342 | 53.4216 | 55.2667
48 | PMA | Western | TGO2 | Gordon | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Western | TNT2 | Newton 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 7.924e-05 | 8.809e-05 | 9.9043e-05 | 0.00012121 | 0.0001499 | 0.0001675 | 0.00017669 | 0.00018544 | 0.00019381 | 0.00020156 | 0.00020877 | 0.00021551 | 0.00022168 | 0.00022735 | 0.0002327 | 0.00023763 | 0.00024217 | 0.00024652 | 0.00025072 | 0.00025477 | 0.00025864 | 0.0002623 | 0.0002658 | 0.00026915 | 0.00027232 | 0.00027536 | 0.00027825 | 0.00028099 | 0.0002836 | 0.00028607 | 0.00028841 | 0.00029062 | 0.00029272 | 0.00029472 | 0.00029663 | 0.00029846 | 0.00030021 | 0.1499 | 0.1675 | 0.17669 | 0.18544 | 0.19381 | 0.20156 | 0.20877 | 0.21551 | 0.22168 | 0.22735
48 | PMA | Western | TNT3 | Ax-Newton 11 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | Ax | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Western | TQT2 | Queenstown 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0.13383 | 0.14877 | 0.16727 | 0.2047 | 0.25316 | 0.28289 | 0.29841 | 0.31318 | 0.32732 | 0.34041 | 0.35258 | 0.36396 | 0.37439 | 0.38397 | 0.39299 | 0.40132 | 0.40899 | 0.41634 | 0.42344 | 0.43027 | 0.43681 | 0.44299 | 0.44891 | 0.45457 | 0.45991 | 0.46504 | 0.46993 | 0.47456 | 0.47896 | 0.48313 | 0.48708 | 0.49082 | 0.49436 | 0.49774 | 0.50096 | 0.50405 | 0.50702 | 253.161 | 282.8856 | 298.4135 | 313.183 | 327.3193 | 340.4054 | 352.5829 | 363.9633 | 374.3942 | 383.9707
48 | PMA | Western | TQT3 | Queenstown 11 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Queenstown 11 kV | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Western | TQU2 | Que | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Que | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Western | TRB2 | Rosebery 44 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Rosebery | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Western | TSR2 | Savage River | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Savage River | MI | 0.048061 | 0.056142 | 0.065245 | 0.074328 | 0.085222 | 0.094846 | 0.10261 | 0.10997 | 0.11696 | 0.12338 | 0.12931 | 0.13482 | 0.13983 | 0.14439 | 0.14866 | 0.15258 | 0.15615 | 0.15955 | 0.16282 | 0.16594 | 0.1689 | 0.17168 | 0.17432 | 0.17682 | 0.17918 | 0.18142 | 0.18354 | 0.18552 | 0.1874 | 0.18917 | 0.19084 | 0.1924 | 0.19387 | 0.19526 | 0.19658 | 0.19783 | 0.19902 | 85.2224 | 94.8455 | 102.6082 | 109.9685 | 116.9556 | 123.3784 | 129.3135 | 134.8181 | 139.8281 | 144.3936
48 | PMA | Southern | BEZ | Bellerive | low | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.5472 | 0.6176 | 0.72902 | 0.87404 | 1.0419 | 1.1909 | 1.3019 | 1.4084 | 1.5109 | 1.6063 | 1.6958 | 1.7799 | 1.8576 | 1.9293 | 1.9973 | 2.0606 | 2.1192 | 2.1757 | 2.2307 | 2.2839 | 2.3352 | 2.3839 | 2.4309 | 2.4762 | 2.5192 | 2.5608 | 2.6006 | 2.6385 | 2.6749 | 2.7095 | 2.7426 | 2.7741 | 2.8041 | 2.8328 | 2.8605 | 2.8872 | 2.9129 | 1041.9233 | 1190.8799 | 1301.9176 | 1408.4133 | 1510.8517 | 1606.342 | 1695.8035 | 1779.9391 | 1857.5716 | 1929.3185
48 | PMA | Southern | CLZ | Claremont | low | maximum | PV | non-coincident | POE50 | summer | zone | zone plus embedded | MW | 0 | Zs | 0.83836 | 0.95383 | 1.1451 | 1.3743 | 1.6105 | 1.8225 | 1.9969 | 2.1617 | 2.3196 | 2.4656 | 2.6014 | 2.7283 | 2.8445 | 2.9512 | 3.0517 | 3.1445 | 3.2299 | 3.3117 | 3.3907 | 3.4667 | 3.5395 | 3.6082 | 3.674 | 3.7369 | 3.7964 | 3.8534 | 3.9077 | 3.9591 | 4.008 | 4.0543 | 4.0982 | 4.1397 | 4.1791 | 4.2166 | 4.2524 | 4.2868 | 4.3197 | 1610.5236 | 1822.4644 | 1996.875 | 2161.7167 | 2319.6286 | 2465.5801 | 2601.3797 | 2728.283 | 2844.5293 | 2951.2371
48 | PMA | Southern | DPZ | Derwent Park | low | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.30994 | 0.35038 | 0.4067 | 0.4768 | 0.5529 | 0.6239 | 0.68196 | 0.73694 | 0.78967 | 0.83847 | 0.88393 | 0.92646 | 0.96548 | 1.0013 | 1.0352 | 1.0664 | 1.0952 | 1.1229 | 1.1496 | 1.1754 | 1.2 | 1.2234 | 1.2458 | 1.2672 | 1.2875 | 1.307 | 1.3256 | 1.3432 | 1.36 | 1.376 | 1.3911 | 1.4054 | 1.4191 | 1.432 | 1.4445 | 1.4564 | 1.4679 | 552.8968 | 623.8984 | 681.963 | 736.9414 | 789.6705 | 838.4667 | 883.9278 | 926.4634 | 965.4778 | 1001.3383
48 | PMA | Southern | EHZ | East Hobart | low | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.1669 | 0.19393 | 0.22298 | 0.25522 | 0.2961 | 0.33363 | 0.36136 | 0.38763 | 0.41277 | 0.43593 | 0.45744 | 0.47749 | 0.49582 | 0.51261 | 0.52838 | 0.5429 | 0.55624 | 0.56899 | 0.58127 | 0.59306 | 0.60431 | 0.61492 | 0.62504 | 0.63471 | 0.64381 | 0.65252 | 0.6608 | 0.6686 | 0.67601 | 0.68302 | 0.68963 | 0.69588 | 0.70178 | 0.70738 | 0.71272 | 0.71783 | 0.72271 | 296.0971 | 333.6307 | 361.3585 | 387.6322 | 412.7673 | 435.9341 | 457.4425 | 477.4948 | 495.8242 | 512.6094
48 | PMA | Southern | GBZ | Geilston Bay | low | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.85515 | 0.96363 | 1.1408 | 1.3486 | 1.5678 | 1.7698 | 1.9205 | 2.0651 | 2.2043 | 2.3341 | 2.4558 | 2.5703 | 2.6761 | 2.7739 | 2.8666 | 2.9529 | 3.033 | 3.1102 | 3.1854 | 3.2582 | 3.3284 | 3.3953 | 3.4597 | 3.5218 | 3.5809 | 3.638 | 3.6929 | 3.745 | 3.7951 | 3.8428 | 3.8884 | 3.9318 | 3.9733 | 4.0131 | 4.0513 | 4.0883 | 4.124 | 1567.7819 | 1769.8343 | 1920.4975 | 2065.0921 | 2204.284 | 2334.1028 | 2455.806 | 2570.3368 | 2676.0808 | 2773.8724
48 | PMA | Southern | GRZ | Gretna | low | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.0074076 | 0.0084189 | 0.0096327 | 0.011063 | 0.012648 | 0.014088 | 0.015174 | 0.016208 | 0.0172 | 0.018119 | 0.018975 | 0.019777 | 0.020513 | 0.02119 | 0.021829 | 0.02242 | 0.022965 | 0.023488 | 0.023994 | 0.024482 | 0.02495 | 0.025392 | 0.025817 | 0.026224 | 0.026609 | 0.026979 | 0.027333 | 0.027667 | 0.027986 | 0.028289 | 0.028577 | 0.028849 | 0.029108 | 0.029355 | 0.029591 | 0.029818 | 0.030036 | 12.6476 | 14.0878 | 15.174 | 16.2081 | 17.1996 | 18.1186 | 18.9752 | 19.7771 | 20.5132 | 21.1902
48 | PMA | Southern | HOZ | Howrah | low | maximum | PV | non-coincident | POE50 | summer | zone | zone plus embedded | MW | 0 | Zs | 0.89544 | 1.0103 | 1.1989 | 1.446 | 1.7293 | 1.9789 | 2.1649 | 2.3433 | 2.5149 | 2.6749 | 2.8247 | 2.9657 | 3.0957 | 3.2159 | 3.3299 | 3.4358 | 3.534 | 3.6286 | 3.7207 | 3.8099 | 3.8958 | 3.9775 | 4.0562 | 4.1321 | 4.2041 | 4.2737 | 4.3405 | 4.404 | 4.4649 | 4.523 | 4.5783 | 4.631 | 4.6813 | 4.7295 | 4.7758 | 4.8205 | 4.8637 | 1729.3437 | 1978.8783 | 2164.8929 | 2343.2981 | 2514.9059 | 2674.874 | 2824.7421 | 2965.6878 | 3095.7393 | 3215.9308
48 | PMA | Southern | NTZ | New Town | low | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.45273 | 0.51284 | 0.58701 | 0.68503 | 0.8037 | 0.90882 | 0.99264 | 1.0718 | 1.1476 | 1.2176 | 1.2825 | 1.3431 | 1.3986 | 1.4494 | 1.4972 | 1.5412 | 1.5817 | 1.6204 | 1.6578 | 1.6936 | 1.7279 | 1.7602 | 1.791 | 1.8205 | 1.8483 | 1.8749 | 1.9003 | 1.9241 | 1.9468 | 1.9683 | 1.9886 | 2.0078 | 2.0259 | 2.0431 | 2.0596 | 2.0753 | 2.0904 | 803.7032 | 908.8158 | 992.6356 | 1071.8366 | 1147.6213 | 1217.5511 | 1282.5203 | 1343.142 | 1398.5913 | 1449.4108
48 | PMA | Southern | RIZ | Richmond | low | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.31002 | 0.35457 | 0.41891 | 0.49458 | 0.57898 | 0.65705 | 0.71793 | 0.77627 | 0.8325 | 0.88481 | 0.93381 | 0.97988 | 1.0224 | 1.0616 | 1.0989 | 1.1335 | 1.1656 | 1.1965 | 1.2266 | 1.2558 | 1.2839 | 1.3106 | 1.3364 | 1.3612 | 1.3849 | 1.4077 | 1.4297 | 1.4506 | 1.4706 | 1.4898 | 1.508 | 1.5255 | 1.5421 | 1.5581 | 1.5735 | 1.5884 | 1.6027 | 578.9777 | 657.0494 | 717.9344 | 776.2682 | 832.4996 | 884.8076 | 933.8064 | 979.8838 | 1022.3787 | 1061.6487
48 | PMA | Southern | RPZ | Rosny Park | low | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.62925 | 0.70515 | 0.83117 | 0.99073 | 1.1673 | 1.3275 | 1.4469 | 1.5615 | 1.6717 | 1.7744 | 1.8707 | 1.9612 | 2.0448 | 2.122 | 2.1952 | 2.2633 | 2.3264 | 2.3872 | 2.4464 | 2.5038 | 2.559 | 2.6115 | 2.6621 | 2.7109 | 2.7572 | 2.802 | 2.845 | 2.8858 | 2.925 | 2.9623 | 2.9979 | 3.0319 | 3.0642 | 3.0952 | 3.1251 | 3.1539 | 3.1816 | 1167.2685 | 1327.4908 | 1446.9312 | 1561.4952 | 1671.7053 | 1774.447 | 1870.7102 | 1961.25 | 2044.7983 | 2122.019
48 | PMA | Southern | SBZ | Sandy Bay | low | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 1.3655 | 1.5686 | 1.8187 | 2.1206 | 2.4644 | 2.7698 | 3.0006 | 3.2197 | 3.4295 | 3.6232 | 3.8034 | 3.9717 | 4.1258 | 4.2671 | 4.4002 | 4.5229 | 4.6359 | 4.744 | 4.8484 | 4.9488 | 5.0447 | 5.1353 | 5.222 | 5.3049 | 5.3832 | 5.4581 | 5.5296 | 5.597 | 5.6612 | 5.722 | 5.7795 | 5.8339 | 5.8854 | 5.9344 | 5.9812 | 6.0261 | 6.069 | 2464.3623 | 2769.833 | 3000.6076 | 3219.6772 | 3429.4579 | 3623.2062 | 3803.3935 | 3971.6735 | 4125.7653 | 4267.1277
48 | PMA | Southern | SUZ | Summerleas Road | low | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.65883 | 0.75889 | 0.90746 | 1.0783 | 1.2585 | 1.4179 | 1.5485 | 1.6733 | 1.7932 | 1.9047 | 2.009 | 2.107 | 2.1973 | 2.2806 | 2.3594 | 2.4326 | 2.5003 | 2.5655 | 2.6289 | 2.6901 | 2.749 | 2.805 | 2.8588 | 2.9105 | 2.9597 | 3.007 | 3.0524 | 3.0955 | 3.1368 | 3.176 | 3.2134 | 3.249 | 3.2829 | 3.3152 | 3.3464 | 3.3763 | 3.4052 | 1258.5428 | 1417.8673 | 1548.5069 | 1673.3006 | 1793.2045 | 1904.72 | 2009.0342 | 2107.025 | 2197.2799 | 2280.5702
48 | PMA | Southern | TWY2 | Wayatinah | low | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | RT | 0.013722 | 0.015617 | 0.017888 | 0.020565 | 0.0029686 | 0.005667 | 0.0077019 | 0.0096394 | 0.011497 | 0.013219 | 0.014824 | 0.016326 | 0.017705 | 0.018973 | 0.02017 | 0.021277 | 0.022298 | 0.023278 | 0.024227 | 0.025141 | 0.026017 | 0.026846 | 0.027642 | 0.028404 | 0.029126 | 0.029819 | 0.030482 | 0.031108 | 0.031706 | 0.032274 | 0.032812 | 0.033323 | 0.033808 | 0.03427 | 0.034713 | 0.035139 | 0.035547 | 2.9686 | 5.667 | 7.7019 | 9.6394 | 11.4969 | 13.2188 | 14.8235 | 16.3259 | 17.7051 | 18.9735
48 | PMA | Southern | WHZ | West Hobart Zone | low | maximum | PV | non-coincident | POE50 | summer | zone | zone plus embedded | MW | 0 | Zs | 0.60518 | 0.69967 | 0.80934 | 0.93342 | 0.14371 | 0.27826 | 0.37966 | 0.47589 | 0.56804 | 0.65312 | 0.73224 | 0.80611 | 0.87374 | 0.93578 | 0.99415 | 1.048 | 1.0975 | 1.1449 | 1.1907 | 1.2347 | 1.2768 | 1.3165 | 1.3545 | 1.3908 | 1.425 | 1.4579 | 1.4891 | 1.5186 | 1.5467 | 1.5733 | 1.5985 | 1.6223 | 1.6448 | 1.6662 | 1.6867 | 1.7063 | 1.725 | 143.7146 | 278.2634 | 379.658 | 475.892 | 568.0367 | 653.121 | 732.236 | 806.1095 | 873.7421 | 935.7763
48 | PMA | Southern | WTZ | Wayatinah | low | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | #N/A | Zs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Western | THZ | Trial Harbour | low | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.063729 | 0.070961 | 0.07986 | 0.097555 | 0.022922 | 0.037113 | 0.044654 | 0.051828 | 0.05869 | 0.065041 | 0.070949 | 0.076468 | 0.081525 | 0.086166 | 0.090536 | 0.09457 | 0.098284 | 0.10184 | 0.10528 | 0.10858 | 0.11174 | 0.11473 | 0.11759 | 0.12032 | 0.1229 | 0.12538 | 0.12774 | 0.12997 | 0.13209 | 0.1341 | 0.13601 | 0.13781 | 0.13952 | 0.14114 | 0.14269 | 0.14418 | 0.14561 | 22.9219 | 37.1133 | 44.6536 | 51.8283 | 58.6899 | 65.0408 | 70.9488 | 76.4677 | 81.5247 | 86.1658
48 | PMA | Western | RBZ | Rosebery 22 kV | low | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.1152 | 0.12955 | 0.14681 | 0.17669 | 0.038245 | 0.063314 | 0.07791 | 0.091782 | 0.10503 | 0.11726 | 0.12863 | 0.13922 | 0.14892 | 0.1578 | 0.16614 | 0.17384 | 0.18091 | 0.18766 | 0.19418 | 0.20044 | 0.20642 | 0.21206 | 0.21744 | 0.22259 | 0.22744 | 0.23208 | 0.2365 | 0.24067 | 0.24463 | 0.24838 | 0.25192 | 0.25527 | 0.25844 | 0.26144 | 0.26431 | 0.26706 | 0.26969 | 38.2451 | 63.3141 | 77.9097 | 91.7823 | 105.0266 | 117.2629 | 128.6268 | 139.2235 | 148.9168 | 157.7974
48 | PMA | total terminal |  | total terminal | low | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | #N/A | #N/A | 33.5903 | 38.9738 | 45.725 | 53.4868 | 61.9118 | 69.4632 | 75.7022 | 81.6506 | 87.349 | 92.6285 | 97.5498 | 102.1553 | 106.3826 | 110.2698 | 113.9367 | 117.3286 | 120.4564 | 123.4571 | 126.3635 | 129.1639 | 131.8473 | 134.3882 | 136.8256 | 139.1616 | 141.3726 | 143.4972 | 145.5269 | 147.4479 | 149.2812 | 151.0224 | 152.6743 | 154.2415 | 155.7299 | 157.149 | 158.5092 | 159.8159 | 161.0713 | 61911.7947 | 69463.2134 | 75702.2217 | 81650.5982 | 87349.0349 | 92628.4765 | 97549.8173 | 102155.2594 | 106382.6267 | 110269.7574
48 | PMA | total zone |  | total zone | low | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | #N/A | #N/A | 8.6354 | 9.8513 | 11.5677 | 13.6795 | 14.8408 | 16.9747 | 18.6042 | 20.1583 | 21.6505 | 23.0359 | 24.3297 | 25.543 | 26.6587 | 27.6867 | 28.6584 | 29.5589 | 30.3909 | 31.1905 | 31.9666 | 32.7156 | 33.4348 | 34.1169 | 34.7725 | 35.4019 | 35.9987 | 36.5732 | 37.123 | 37.6443 | 38.1426 | 38.6166 | 39.0671 | 39.4953 | 39.9025 | 40.2915 | 40.6649 | 41.0242 | 41.3699 | 14840.7687 | 16974.7407 | 18604.154 | 20158.3179 | 21650.5385 | 23035.9046 | 24329.7252 | 25542.9628 | 26658.7429 | 27686.7492
51 | PMA | George Town | TC01 | Comalco | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | Camalco | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | PMA | George Town | TSW1 | Starwood | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | Starwood | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | PMA | George Town | TTE1 | Temco | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | Temco | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | PMA | North | TAL2 | Ax-Arthurs Lake 6.6 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | Ax | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | PMA | North | TAV2 | Avoca 22 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.000201 | 0.00087061 | 0.0025237 | 0.004455 | 0.006268 | 0.0074334 | 0.0089862 | 0.011573 | 0.014676 | 0.020013 | 0.026264 | 0.033444 | 0.041714 | 0.051144 | 0.061755 | 0.073568 | 0.086606 | 0.1009 | 0.1163 | 0.1328 | 0.1504 | 0.16913 | 0.18858 | 0.20876 | 0.22967 | 0.25133 | 0.27376 | 0.29697 | 0.32098 | 0.34579 | 0.37118 | 0.39716 | 0.42374 | 0.201 | 0.87061 | 2.5237 | 4.455 | 6.268 | 7.4334 | 8.9862 | 11.5732 | 14.6757 | 20.0127
51 | PMA | North | TDE2 | Derby 22 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.00019719 | 0.00088401 | 0.0020498 | 0.0031278 | 0.004326 | 0.0050849 | 0.0060757 | 0.0074546 | 0.0090753 | 0.012162 | 0.015691 | 0.019661 | 0.02414 | 0.02915 | 0.034691 | 0.040759 | 0.047353 | 0.054472 | 0.06204 | 0.070032 | 0.078448 | 0.087288 | 0.096355 | 0.10565 | 0.11517 | 0.12491 | 0.13488 | 0.14507 | 0.15549 | 0.16613 | 0.17689 | 0.18778 | 0.19879 | 0.19719 | 0.88401 | 2.0498 | 3.1278 | 4.326 | 5.0849 | 6.0757 | 7.4546 | 9.0753 | 12.162
51 | PMA | North | THA3 | Hadspen 22 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.0018598 | 0.0079058 | 0.022474 | 0.037143 | 0.049048 | 0.058182 | 0.070316 | 0.08861 | 0.11102 | 0.15033 | 0.19614 | 0.24854 | 0.30866 | 0.37695 | 0.45353 | 0.53851 | 0.63204 | 0.73424 | 0.84413 | 0.96146 | 1.0864 | 1.219 | 1.3563 | 1.4984 | 1.6454 | 1.7973 | 1.9543 | 2.1163 | 2.2835 | 2.456 | 2.6321 | 2.8118 | 2.9953 | 1.8598 | 7.9058 | 22.4743 | 37.1426 | 49.0479 | 58.1817 | 70.3161 | 88.6102 | 111.0202 | 150.3256
51 | PMA | North | TMY2 | Mowbray 22 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.0010972 | 0.004176 | 0.011584 | 0.018279 | 0.022771 | 0.027234 | 0.033084 | 0.041295 | 0.050216 | 0.066478 | 0.085245 | 0.10652 | 0.13072 | 0.15799 | 0.18834 | 0.22178 | 0.25833 | 0.29801 | 0.34041 | 0.38541 | 0.43303 | 0.48328 | 0.53505 | 0.58832 | 0.64313 | 0.69946 | 0.75733 | 0.81675 | 0.87774 | 0.94029 | 1.0038 | 1.0683 | 1.1338 | 1.0972 | 4.176 | 11.5844 | 18.2787 | 22.771 | 27.2341 | 33.0839 | 41.2949 | 50.2156 | 66.478
51 | PMA | North | TPM3 | Palmerston 22 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 9.1428e-05 | 0.00040781 | 0.0011729 | 0.002031 | 0.002818 | 0.0033204 | 0.0039856 | 0.0051306 | 0.0066034 | 0.0090964 | 0.012026 | 0.015399 | 0.019294 | 0.023744 | 0.028761 | 0.034356 | 0.04054 | 0.047327 | 0.054653 | 0.062505 | 0.070893 | 0.079831 | 0.089118 | 0.098759 | 0.10876 | 0.11913 | 0.12988 | 0.14101 | 0.15253 | 0.16445 | 0.17665 | 0.18915 | 0.20194 | 0.091428 | 0.40781 | 1.1729 | 2.031 | 2.818 | 3.3204 | 3.9856 | 5.1306 | 6.6034 | 9.0964
51 | PMA | North | TSD2 | Scottsdale 22 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.00054538 | 0.0024061 | 0.0056207 | 0.0084588 | 0.011328 | 0.013305 | 0.01587 | 0.019479 | 0.023806 | 0.031961 | 0.041299 | 0.051816 | 0.063699 | 0.077007 | 0.091737 | 0.10788 | 0.12544 | 0.14441 | 0.16459 | 0.18591 | 0.20837 | 0.23198 | 0.2562 | 0.28104 | 0.30649 | 0.33256 | 0.35923 | 0.38652 | 0.41442 | 0.44293 | 0.47178 | 0.50097 | 0.53051 | 0.54538 | 2.4061 | 5.6207 | 8.4588 | 11.3276 | 13.3055 | 15.8695 | 19.4787 | 23.8062 | 31.9605
51 | PMA | North | TSL2 | St Leonards 22 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.0011844 | 0.0049277 | 0.013762 | 0.022008 | 0.027691 | 0.033017 | 0.040081 | 0.049801 | 0.060792 | 0.080823 | 0.10398 | 0.13028 | 0.16024 | 0.19407 | 0.23179 | 0.27344 | 0.31905 | 0.36866 | 0.42177 | 0.47825 | 0.53813 | 0.60144 | 0.66678 | 0.73416 | 0.8036 | 0.87512 | 0.94874 | 1.0245 | 1.1023 | 1.1824 | 1.2638 | 1.3467 | 1.431 | 1.1844 | 4.9277 | 13.762 | 22.0076 | 27.6913 | 33.0168 | 40.0809 | 49.801 | 60.7921 | 80.8226
51 | PMA | North | TSL3 | St Leonards 22 kV (scheduled load) | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | Firmus Grid | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | PMA | North | TSM2 | St Marys 22 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.00065645 | 0.0025778 | 0.0081009 | 0.014202 | 0.020584 | 0.024802 | 0.030942 | 0.038558 | 0.045454 | 0.058902 | 0.074316 | 0.09171 | 0.11141 | 0.13356 | 0.15816 | 0.18524 | 0.21483 | 0.24696 | 0.2813 | 0.31779 | 0.35644 | 0.39727 | 0.43941 | 0.48286 | 0.52763 | 0.57375 | 0.62121 | 0.67004 | 0.72026 | 0.77187 | 0.82441 | 0.87788 | 0.93229 | 0.65645 | 2.5778 | 8.1009 | 14.2024 | 20.584 | 24.802 | 30.9416 | 38.5579 | 45.4541 | 58.9015
51 | PMA | Northwest | TDP2 | Devonport 22 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.0023154 | 0.0066217 | 0.016139 | 0.025227 | 0.032174 | 0.039398 | 0.049696 | 0.063836 | 0.076809 | 0.10141 | 0.12972 | 0.16177 | 0.19818 | 0.23921 | 0.2849 | 0.33529 | 0.39044 | 0.45039 | 0.51458 | 0.58284 | 0.65523 | 0.7318 | 0.81086 | 0.89245 | 0.97659 | 1.0633 | 1.1526 | 1.2446 | 1.3392 | 1.4366 | 1.5357 | 1.6367 | 1.7395 | 2.3154 | 6.6217 | 16.1386 | 25.2267 | 32.1736 | 39.3984 | 49.696 | 63.8358 | 76.8094 | 101.4067
51 | PMA | Northwest | TEB2 | Emu Bay 11 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | Emu Bay | MI | 0 | 0 | 0 | 0 | 2.9362e-05 | 0.00013855 | 0.00030927 | 0.00049691 | 0.00066337 | 0.00080424 | 0.001022 | 0.0013487 | 0.0016004 | 0.0020779 | 0.0026235 | 0.0032368 | 0.0039283 | 0.0047012 | 0.0055551 | 0.0064893 | 0.0075034 | 0.008597 | 0.0097585 | 0.010984 | 0.012272 | 0.013624 | 0.01501 | 0.016428 | 0.017879 | 0.019362 | 0.020878 | 0.022426 | 0.024007 | 0.025619 | 0.027248 | 0.028894 | 0.030557 | 0.029362 | 0.13855 | 0.30927 | 0.49691 | 0.66337 | 0.80424 | 1.022 | 1.3487 | 1.6004 | 2.0779
51 | PMA | Northwest | THM2 | Hampshire | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | Hampshire | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | PMA | Northwest | TPL2 | Port Latta | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | Port Latta | MI | 0 | 0 | 0 | 0 | 0.00025066 | 0.0011659 | 0.0028408 | 0.0045179 | 0.0064475 | 0.0076943 | 0.0092675 | 0.011743 | 0.014389 | 0.019179 | 0.024698 | 0.030944 | 0.038034 | 0.046005 | 0.054857 | 0.064588 | 0.075199 | 0.086689 | 0.098937 | 0.1119 | 0.12559 | 0.14 | 0.1548 | 0.17 | 0.18559 | 0.20158 | 0.21797 | 0.23475 | 0.25194 | 0.26952 | 0.28733 | 0.30537 | 0.32365 | 0.25066 | 1.1659 | 2.8408 | 4.5179 | 6.4475 | 7.6943 | 9.2675 | 11.7427 | 14.3888 | 19.1789
51 | PMA | Northwest | TRA2 | Railton 22 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.0011415 | 0.004958 | 0.013841 | 0.023068 | 0.030213 | 0.036248 | 0.043816 | 0.055503 | 0.068715 | 0.092432 | 0.11999 | 0.15143 | 0.18743 | 0.22825 | 0.27397 | 0.32465 | 0.38038 | 0.44124 | 0.50666 | 0.57647 | 0.65077 | 0.72964 | 0.81132 | 0.89586 | 0.98329 | 1.0737 | 1.167 | 1.2634 | 1.3629 | 1.4656 | 1.5704 | 1.6775 | 1.7868 | 1.1415 | 4.958 | 13.8414 | 23.0676 | 30.2125 | 36.248 | 43.8165 | 55.5025 | 68.7146 | 92.4322
51 | PMA | Northwest | TSH3 | Sheffield | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | PMA | Northwest | TST2 | Smithton 22 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.00035907 | 0.0013368 | 0.0033721 | 0.0054407 | 0.0094549 | 0.011121 | 0.012971 | 0.016422 | 0.021526 | 0.029883 | 0.039622 | 0.050734 | 0.063433 | 0.077784 | 0.093779 | 0.1114 | 0.13065 | 0.15151 | 0.17375 | 0.19728 | 0.22211 | 0.24822 | 0.275 | 0.30246 | 0.33058 | 0.35937 | 0.38881 | 0.41892 | 0.44967 | 0.48108 | 0.51283 | 0.54493 | 0.57736 | 0.35907 | 1.3368 | 3.3721 | 5.4407 | 9.4549 | 11.1211 | 12.9708 | 16.4221 | 21.526 | 29.8826
51 | PMA | Northwest | TUL2 | Ulverstone 22 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.0010713 | 0.0056073 | 0.014092 | 0.022245 | 0.028676 | 0.035243 | 0.043322 | 0.055596 | 0.066713 | 0.087882 | 0.11216 | 0.13955 | 0.17057 | 0.20538 | 0.24401 | 0.28646 | 0.33275 | 0.3829 | 0.43639 | 0.49308 | 0.55298 | 0.61612 | 0.68109 | 0.7479 | 0.81655 | 0.88707 | 0.95945 | 1.0337 | 1.1098 | 1.1879 | 1.2671 | 1.3474 | 1.429 | 1.0713 | 5.6073 | 14.0921 | 22.2447 | 28.6758 | 35.2433 | 43.3221 | 55.5959 | 66.7129 | 87.8819
51 | PMA | Northwest | TWV2 | Wesley Vale 11 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | Wesley Vale | MI | 0 | 0 | 0 | 0 | 0.0003829 | 0.0021187 | 0.006023 | 0.0094732 | 0.012557 | 0.015685 | 0.019376 | 0.024453 | 0.029796 | 0.039554 | 0.050948 | 0.064024 | 0.079088 | 0.096285 | 0.11568 | 0.13734 | 0.16133 | 0.18773 | 0.21632 | 0.24707 | 0.28005 | 0.31532 | 0.35214 | 0.39053 | 0.43054 | 0.47222 | 0.51561 | 0.56076 | 0.60772 | 0.65654 | 0.70679 | 0.75849 | 0.81168 | 0.3829 | 2.1187 | 6.023 | 9.4732 | 12.5573 | 15.6847 | 19.3761 | 24.4531 | 29.7963 | 39.5538
51 | PMA | Southern | TBW2 | Bridgewater 11 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.00097473 | 0.0048569 | 0.012365 | 0.019986 | 0.026117 | 0.034585 | 0.043708 | 0.058256 | 0.070747 | 0.094348 | 0.12182 | 0.15329 | 0.18948 | 0.23077 | 0.27733 | 0.32935 | 0.387 | 0.45051 | 0.51937 | 0.59354 | 0.67323 | 0.75862 | 0.84791 | 0.94123 | 1.0387 | 1.1405 | 1.2466 | 1.3574 | 1.4729 | 1.5933 | 1.7175 | 1.8456 | 1.9778 | 0.97473 | 4.8569 | 12.3654 | 19.9862 | 26.1171 | 34.5846 | 43.7084 | 58.256 | 70.7473 | 94.3475
51 | PMA | Southern | TBYA | Boyer SWA | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | Boyer | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | PMA | Southern | TBYB | Boyer SWB | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | Boyer | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | PMA | Southern | TCR2 | Creek Rd 33 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.0044983 | 0.010337 | 0.023654 | 0.038628 | 0.048632 | 0.059529 | 0.073556 | 0.096134 | 0.11615 | 0.15437 | 0.19834 | 0.24811 | 0.30466 | 0.36837 | 0.43932 | 0.51759 | 0.60326 | 0.69644 | 0.79622 | 0.90237 | 1.015 | 1.1341 | 1.2572 | 1.3843 | 1.5154 | 1.6505 | 1.7898 | 1.9332 | 2.0809 | 2.2328 | 2.3876 | 2.5453 | 2.7059 | 4.4983 | 10.3369 | 23.6536 | 38.6276 | 48.6317 | 59.5286 | 73.5563 | 96.1344 | 116.1531 | 154.3729
51 | PMA | Southern | TCS3 | Chapel St 11 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.0022256 | 0.0049083 | 0.010358 | 0.0163 | 0.021472 | 0.026765 | 0.033441 | 0.044166 | 0.054424 | 0.073669 | 0.095851 | 0.12099 | 0.14959 | 0.18183 | 0.21777 | 0.25742 | 0.30083 | 0.34804 | 0.39861 | 0.45239 | 0.50943 | 0.56977 | 0.63207 | 0.69637 | 0.76267 | 0.83099 | 0.90137 | 0.97382 | 1.0484 | 1.125 | 1.2031 | 1.2826 | 1.3635 | 2.2256 | 4.9083 | 10.3581 | 16.2999 | 21.4721 | 26.7647 | 33.4408 | 44.1664 | 54.4243 | 73.6691
51 | PMA | Southern | TDB2 | Derwent Bridge 22 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0 | 0 | 0 | 0 | 1.3916e-06 | 8.4641e-06 | 1.9313e-05 | 3.2982e-05 | 4.177e-05 | 5.3573e-05 | 6.6506e-05 | 8.8316e-05 | 0.0001065 | 0.000141 | 0.00018079 | 0.00022594 | 0.00027737 | 0.00033546 | 0.0004003 | 0.000472 | 0.00055066 | 0.00063639 | 0.00072841 | 0.00082651 | 0.00093079 | 0.0010414 | 0.0011558 | 0.0012742 | 0.0013966 | 0.001523 | 0.0016535 | 0.0017882 | 0.0019272 | 0.0020704 | 0.0022166 | 0.0023659 | 0.0025182 | 0.0013916 | 0.0084641 | 0.019313 | 0.032982 | 0.04177 | 0.053573 | 0.066506 | 0.088316 | 0.1065 | 0.141
51 | PMA | Southern | TEL2 | Electrona 11 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.00059419 | 0.002953 | 0.0093858 | 0.016098 | 0.020489 | 0.025274 | 0.030605 | 0.039824 | 0.048225 | 0.064142 | 0.082565 | 0.10354 | 0.12753 | 0.15472 | 0.18519 | 0.21901 | 0.25625 | 0.29701 | 0.34091 | 0.38789 | 0.43802 | 0.49139 | 0.54682 | 0.60437 | 0.66407 | 0.72598 | 0.79013 | 0.85658 | 0.92538 | 0.99658 | 1.0695 | 1.1442 | 1.2208 | 0.59419 | 2.953 | 9.3858 | 16.0985 | 20.4886 | 25.2739 | 30.6049 | 39.8245 | 48.2252 | 64.1418
51 | PMA | Southern | THR2 | Huon River | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | Huon River | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | PMA | Southern | TK12 | Kingston 11 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.0010586 | 0.0055611 | 0.017948 | 0.030875 | 0.039339 | 0.048587 | 0.058797 | 0.076529 | 0.092729 | 0.1234 | 0.15891 | 0.19935 | 0.2456 | 0.29804 | 0.35681 | 0.42205 | 0.49391 | 0.57255 | 0.65728 | 0.74796 | 0.84474 | 0.94777 | 1.0548 | 1.1659 | 1.2812 | 1.4008 | 1.5247 | 1.6531 | 1.7861 | 1.9236 | 2.0646 | 2.209 | 2.357 | 1.0586 | 5.5611 | 17.9477 | 30.8749 | 39.3395 | 48.5866 | 58.797 | 76.5288 | 92.7292 | 123.3998
51 | PMA | Southern | TK13 | Kingston 33 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | PMA | Southern | TKE2 | Kermandie 11 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.00026623 | 0.0019548 | 0.0059286 | 0.0095236 | 0.011998 | 0.014314 | 0.01736 | 0.02228 | 0.026595 | 0.034892 | 0.044507 | 0.055477 | 0.068048 | 0.082335 | 0.098389 | 0.11626 | 0.13601 | 0.15769 | 0.18112 | 0.20628 | 0.23322 | 0.26199 | 0.29199 | 0.32325 | 0.35579 | 0.38965 | 0.42486 | 0.46147 | 0.49951 | 0.53902 | 0.57965 | 0.62142 | 0.66436 | 0.26623 | 1.9548 | 5.9286 | 9.5236 | 11.9981 | 14.3138 | 17.3604 | 22.2801 | 26.5954 | 34.8916
51 | PMA | Southern | TLF2 | Lindisfarne 33 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.00060384 | 0.0032151 | 0.010145 | 0.017084 | 0.022112 | 0.028636 | 0.036433 | 0.049652 | 0.060221 | 0.080244 | 0.10345 | 0.12992 | 0.16022 | 0.19462 | 0.23323 | 0.27614 | 0.32348 | 0.37535 | 0.43132 | 0.4913 | 0.5554 | 0.62373 | 0.69482 | 0.76873 | 0.84552 | 0.92527 | 1.008 | 1.0939 | 1.1829 | 1.2752 | 1.3698 | 1.4669 | 1.5665 | 0.60384 | 3.2151 | 10.1452 | 17.0839 | 22.1122 | 28.6359 | 36.4334 | 49.652 | 60.2209 | 80.244
51 | PMA | Southern | TMB2 | Meadowbank 22 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 9.1783e-05 | 0.00052005 | 0.0012381 | 0.0020719 | 0.0026589 | 0.0034518 | 0.0043159 | 0.0057362 | 0.0069368 | 0.0092098 | 0.011841 | 0.014838 | 0.018265 | 0.022151 | 0.026507 | 0.031344 | 0.036672 | 0.042505 | 0.048792 | 0.055523 | 0.06271 | 0.070365 | 0.078323 | 0.08659 | 0.095175 | 0.10408 | 0.11332 | 0.12291 | 0.13284 | 0.14312 | 0.15368 | 0.1645 | 0.1756 | 0.091783 | 0.52005 | 1.2381 | 2.0719 | 2.6589 | 3.4518 | 4.3159 | 5.7362 | 6.9368 | 9.2098
51 | PMA | Southern | TMT2 | Mornington 33 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.00069408 | 0.003689 | 0.011671 | 0.019664 | 0.025451 | 0.032945 | 0.041919 | 0.05714 | 0.069302 | 0.092344 | 0.11905 | 0.1495 | 0.18436 | 0.22393 | 0.26833 | 0.31769 | 0.37212 | 0.43177 | 0.49611 | 0.56506 | 0.63874 | 0.71728 | 0.79898 | 0.8839 | 0.97213 | 1.0637 | 1.1588 | 1.2574 | 1.3596 | 1.4656 | 1.5742 | 1.6857 | 1.8001 | 0.69408 | 3.689 | 11.6706 | 19.6642 | 25.4511 | 32.9453 | 41.9185 | 57.1396 | 69.3017 | 92.3436
51 | PMA | Southern | TNH2 | North Hobart 11 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.001801 | 0.0038426 | 0.008455 | 0.013804 | 0.017032 | 0.020634 | 0.025523 | 0.033244 | 0.039807 | 0.052472 | 0.067004 | 0.083413 | 0.10201 | 0.12292 | 0.14615 | 0.17173 | 0.19967 | 0.23 | 0.26242 | 0.29684 | 0.3333 | 0.37181 | 0.41152 | 0.45245 | 0.49461 | 0.538 | 0.58264 | 0.62853 | 0.6757 | 0.72416 | 0.77345 | 0.82357 | 0.87455 | 1.801 | 3.8426 | 8.455 | 13.8037 | 17.0316 | 20.6338 | 25.5229 | 33.2439 | 39.8067 | 52.472
51 | PMA | Southern | TNN2 | New Norfolk 22 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | Brynn Estyn | MI | 0 | 0 | 0 | 0 | 0.00038606 | 0.002327 | 0.0053372 | 0.0090907 | 0.011531 | 0.014813 | 0.018406 | 0.024445 | 0.029489 | 0.039055 | 0.050094 | 0.062626 | 0.076909 | 0.093048 | 0.11108 | 0.13102 | 0.15291 | 0.17679 | 0.20243 | 0.22978 | 0.25887 | 0.28974 | 0.32172 | 0.3548 | 0.38903 | 0.42441 | 0.46096 | 0.49871 | 0.53767 | 0.57787 | 0.61893 | 0.66087 | 0.7037 | 0.38606 | 2.327 | 5.3372 | 9.0907 | 11.5314 | 14.8132 | 18.4061 | 24.4452 | 29.4893 | 39.055
51 | PMA | Southern | TR13 | Risdon 11 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | Risdon | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | PMA | Southern | TR14 | Risdon 33 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.001519 | 0.003391 | 0.0073061 | 0.011632 | 0.015028 | 0.018644 | 0.023247 | 0.03061 | 0.037404 | 0.050244 | 0.065036 | 0.081796 | 0.10086 | 0.12235 | 0.1463 | 0.17273 | 0.20168 | 0.23318 | 0.26692 | 0.30282 | 0.34092 | 0.38124 | 0.4229 | 0.46591 | 0.51029 | 0.55606 | 0.60323 | 0.65182 | 0.70185 | 0.75333 | 0.8058 | 0.85926 | 0.91373 | 1.519 | 3.391 | 7.3061 | 11.632 | 15.0278 | 18.6442 | 23.2467 | 30.6098 | 37.4045 | 50.2442
51 | PMA | Southern | TRK2 | Rokeby 11 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.00050673 | 0.0026936 | 0.008522 | 0.014359 | 0.018585 | 0.024057 | 0.03061 | 0.041724 | 0.050605 | 0.067431 | 0.08693 | 0.10916 | 0.13462 | 0.16352 | 0.19594 | 0.23198 | 0.27173 | 0.31528 | 0.36227 | 0.41262 | 0.46642 | 0.52377 | 0.58343 | 0.64544 | 0.70986 | 0.77676 | 0.84617 | 0.91818 | 0.99282 | 1.0702 | 1.1495 | 1.2309 | 1.3144 | 0.50673 | 2.6936 | 8.522 | 14.3591 | 18.5848 | 24.0572 | 30.6096 | 41.7244 | 50.6054 | 67.4309
51 | PMA | Southern | TS02 | Sorell | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.0012214 | 0.0062844 | 0.016556 | 0.027662 | 0.03786 | 0.049063 | 0.06055 | 0.081046 | 0.09748 | 0.12888 | 0.16529 | 0.20685 | 0.25448 | 0.30862 | 0.36947 | 0.43721 | 0.51206 | 0.59423 | 0.68306 | 0.77844 | 0.88058 | 0.9897 | 1.1035 | 1.222 | 1.3454 | 1.4739 | 1.6075 | 1.7465 | 1.8909 | 2.041 | 2.1953 | 2.3541 | 2.5173 | 1.2214 | 6.2844 | 16.5563 | 27.662 | 37.8598 | 49.0625 | 60.5496 | 81.0457 | 97.48 | 128.8819
51 | PMA | Southern | TTB2 | Triabunna 22 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.00024756 | 0.0012493 | 0.0040799 | 0.0062763 | 0.009217 | 0.010972 | 0.014155 | 0.017614 | 0.020332 | 0.026004 | 0.032496 | 0.039827 | 0.048145 | 0.05752 | 0.067978 | 0.079547 | 0.092254 | 0.10613 | 0.12107 | 0.13704 | 0.15407 | 0.1722 | 0.19104 | 0.21061 | 0.23092 | 0.252 | 0.27386 | 0.29652 | 0.32001 | 0.34433 | 0.36928 | 0.39486 | 0.4211 | 0.24756 | 1.2493 | 4.0799 | 6.2763 | 9.217 | 10.9719 | 14.1546 | 17.6139 | 20.3319 | 26.0044
51 | PMA | Southern | TTU2 | Tungatinah 22 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0 | 0 | 0 | 0 | 1.957e-05 | 0.00011903 | 0.0002716 | 0.00046383 | 0.00058742 | 0.00075341 | 0.0009353 | 0.001242 | 0.0014978 | 0.0019829 | 0.0025425 | 0.0031775 | 0.0039008 | 0.0047177 | 0.0056296 | 0.0066379 | 0.0077441 | 0.0089499 | 0.010244 | 0.011624 | 0.01309 | 0.014645 | 0.016255 | 0.01792 | 0.019641 | 0.021419 | 0.023255 | 0.025149 | 0.027103 | 0.029118 | 0.031174 | 0.033273 | 0.035415 | 0.01957 | 0.11903 | 0.2716 | 0.46383 | 0.58742 | 0.75341 | 0.9353 | 1.242 | 1.4978 | 1.9829
51 | PMA | Southern | TWA2 | Waddamana 22 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0 | 0 | 0 | 0 | 6.9338e-05 | 0.00035532 | 0.00090348 | 0.0014634 | 0.0019146 | 0.0025347 | 0.0032026 | 0.0042629 | 0.005174 | 0.0068956 | 0.0088992 | 0.011194 | 0.013832 | 0.016841 | 0.020234 | 0.024023 | 0.028222 | 0.032846 | 0.037859 | 0.043258 | 0.049056 | 0.055269 | 0.061765 | 0.068552 | 0.07564 | 0.083039 | 0.090759 | 0.09881 | 0.1072 | 0.11595 | 0.12498 | 0.13429 | 0.14389 | 0.069338 | 0.35532 | 0.90348 | 1.4634 | 1.9146 | 2.5347 | 3.2026 | 4.2629 | 5.174 | 6.8956
51 | PMA | Western | TGO2 | Gordon | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0 | 0 | 0 | 0 | 1.3832e-06 | 8.4839e-06 | 1.9242e-05 | 3.3045e-05 | 4.1739e-05 | 5.3462e-05 | 6.6315e-05 | 8.8611e-05 | 0.00010827 | 0.0001447 | 0.00018687 | 0.00023486 | 0.00028966 | 0.0003517 | 0.00042109 | 0.00049793 | 0.00058236 | 0.00067452 | 0.00077353 | 0.00087918 | 0.00099161 | 0.0011109 | 0.0012345 | 0.0013624 | 0.0014947 | 0.0016315 | 0.0017728 | 0.0019187 | 0.0020693 | 0.0022246 | 0.0023833 | 0.0025453 | 0.0027107 | 0.0013832 | 0.0084839 | 0.019242 | 0.033045 | 0.041739 | 0.053462 | 0.066315 | 0.088611 | 0.10827 | 0.1447
51 | PMA | Western | TNT2 | Newton 22 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | PMA | Western | TNT3 | Ax-Newton 11 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | Ax | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | PMA | Western | TQT2 | Queenstown 22 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0 | 0 | 0 | 0 | 9.1654e-05 | 0.0002361 | 0.00049056 | 0.001174 | 0.0016275 | 0.0021261 | 0.0034223 | 0.0048952 | 0.0055722 | 0.0070423 | 0.0087091 | 0.010575 | 0.012674 | 0.01502 | 0.017616 | 0.020467 | 0.023575 | 0.026945 | 0.030548 | 0.034376 | 0.038432 | 0.04272 | 0.047151 | 0.051727 | 0.056449 | 0.06132 | 0.066341 | 0.071516 | 0.076846 | 0.082334 | 0.08793 | 0.093637 | 0.099455 | 0.091654 | 0.2361 | 0.49056 | 1.174 | 1.6275 | 2.1261 | 3.4223 | 4.8952 | 5.5722 | 7.0423
51 | PMA | Western | TQT3 | Queenstown 11 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | Queenstown 11 kV | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | PMA | Western | TQU2 | Que | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | Que | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | PMA | Western | TRB2 | Rosebery 44 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | Rosebery | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | PMA | Western | TSR2 | Savage River | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | Savage River | MI | 0 | 0 | 0 | 0 | 1.9607e-05 | 9.1384e-05 | 0.0002155 | 0.00034516 | 0.00047973 | 0.00057629 | 0.00071016 | 0.00091455 | 0.0011053 | 0.0014575 | 0.0018621 | 0.0023187 | 0.0028358 | 0.0034159 | 0.0040591 | 0.004765 | 0.0055335 | 0.0063647 | 0.0072497 | 0.0081855 | 0.0091724 | 0.01021 | 0.011276 | 0.012369 | 0.01349 | 0.014638 | 0.015814 | 0.017018 | 0.018249 | 0.019508 | 0.020782 | 0.022073 | 0.023378 | 0.019607 | 0.091384 | 0.2155 | 0.34516 | 0.47973 | 0.57629 | 0.71016 | 0.91455 | 1.1053 | 1.4575
51 | PMA | Southern | BEZ | Bellerive | low | maximum | Battery | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0 | 0 | 0 | 0 | 0 | 0.0011522 | 0.0036454 | 0.0061422 | 0.0079498 | 0.010291 | 0.013093 | 0.017848 | 0.021647 | 0.028844 | 0.037185 | 0.046696 | 0.057584 | 0.069945 | 0.083815 | 0.099232 | 0.11623 | 0.13486 | 0.15496 | 0.1765 | 0.19951 | 0.22405 | 0.24956 | 0.27609 | 0.30365 | 0.33226 | 0.36196 | 0.39276 | 0.42469 | 0.45777 | 0.49172 | 0.52654 | 0.56226 | 0 | 1.1522 | 3.6454 | 6.1422 | 7.9498 | 10.2906 | 13.0935 | 17.8479 | 21.6468 | 28.844
51 | PMA | Southern | CLZ | Claremont | low | maximum | Battery | non-coincident | POE50 | summer | zone | zone plus embedded | MW | 0 | Zs | 0 | 0 | 0 | 0 | 0 | 0.0023733 | 0.0049983 | 0.007835 | 0.010398 | 0.013014 | 0.016281 | 0.021537 | 0.026611 | 0.036107 | 0.047058 | 0.059477 | 0.073609 | 0.089552 | 0.10733 | 0.12695 | 0.14844 | 0.17182 | 0.19687 | 0.22352 | 0.2518 | 0.28173 | 0.31264 | 0.34455 | 0.37746 | 0.4114 | 0.44636 | 0.48237 | 0.51943 | 0.55756 | 0.5964 | 0.63596 | 0.67625 | 0 | 2.3733 | 4.9983 | 7.835 | 10.3982 | 13.0143 | 16.2813 | 21.5374 | 26.611 | 36.1069
51 | PMA | Southern | DPZ | Derwent Park | low | maximum | Battery | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0 | 0 | 0 | 0 | 0 | 0.00089199 | 0.0019393 | 0.0030523 | 0.0040367 | 0.0051053 | 0.0064002 | 0.008486 | 0.010455 | 0.014146 | 0.018411 | 0.023257 | 0.028783 | 0.035031 | 0.042012 | 0.049738 | 0.05822 | 0.067472 | 0.077408 | 0.088008 | 0.099283 | 0.11125 | 0.12364 | 0.13646 | 0.14972 | 0.16344 | 0.1776 | 0.19224 | 0.20734 | 0.22293 | 0.23885 | 0.25511 | 0.27173 | 0 | 0.89199 | 1.9393 | 3.0523 | 4.0367 | 5.1053 | 6.4002 | 8.486 | 10.4551 | 14.1463
51 | PMA | Southern | EHZ | East Hobart | low | maximum | Battery | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0 | 0 | 0 | 0 | 0 | 0.00024612 | 0.00054165 | 0.00088445 | 0.0010909 | 0.0013215 | 0.0016345 | 0.0021288 | 0.0025487 | 0.0033592 | 0.004289 | 0.005339 | 0.006529 | 0.0078667 | 0.0093532 | 0.01099 | 0.012777 | 0.014718 | 0.016792 | 0.018995 | 0.021327 | 0.023791 | 0.026332 | 0.02895 | 0.031647 | 0.034423 | 0.037279 | 0.040215 | 0.043233 | 0.046333 | 0.049486 | 0.052693 | 0.055954 | 0 | 0.24612 | 0.54165 | 0.88445 | 1.0909 | 1.3215 | 1.6345 | 2.1288 | 2.5487 | 3.3592
51 | PMA | Southern | GBZ | Geilston Bay | low | maximum | Battery | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0 | 0 | 0 | 0 | 0 | 0.0017655 | 0.005559 | 0.0093564 | 0.012111 | 0.015689 | 0.019961 | 0.027198 | 0.032987 | 0.043955 | 0.056669 | 0.071168 | 0.08777 | 0.10662 | 0.12778 | 0.1513 | 0.17724 | 0.20568 | 0.23636 | 0.26924 | 0.30439 | 0.34186 | 0.38085 | 0.42138 | 0.4635 | 0.50725 | 0.55265 | 0.59976 | 0.6486 | 0.69923 | 0.75118 | 0.80449 | 0.85917 | 0 | 1.7655 | 5.559 | 9.3564 | 12.1106 | 15.6893 | 19.9605 | 27.1976 | 32.9872 | 43.9554
51 | PMA | Southern | GRZ | Gretna | low | maximum | Battery | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0 | 0 | 0 | 0 | 0 | 4.6565e-05 | 0.00010625 | 0.00018145 | 0.0002298 | 0.00029473 | 0.00036588 | 0.00048587 | 0.00058593 | 0.00077572 | 0.00099464 | 0.001243 | 0.001526 | 0.0018456 | 0.0022023 | 0.0025968 | 0.0030295 | 0.0035012 | 0.0040075 | 0.0045472 | 0.0051209 | 0.0057293 | 0.006359 | 0.0070103 | 0.0076836 | 0.0083791 | 0.0090973 | 0.0098384 | 0.010603 | 0.011391 | 0.012195 | 0.013017 | 0.013855 | 0 | 0.046565 | 0.10625 | 0.18145 | 0.2298 | 0.29473 | 0.36588 | 0.48587 | 0.58593 | 0.77572
51 | PMA | Southern | HOZ | Howrah | low | maximum | Battery | non-coincident | POE50 | summer | zone | zone plus embedded | MW | 0 | Zs | 0 | 0 | 0 | 0 | 0 | 0.0020148 | 0.0063739 | 0.010739 | 0.0139 | 0.017993 | 0.022893 | 0.031206 | 0.037849 | 0.050433 | 0.065017 | 0.081646 | 0.10068 | 0.1223 | 0.14655 | 0.1735 | 0.20323 | 0.23581 | 0.27095 | 0.3086 | 0.34884 | 0.39174 | 0.43635 | 0.48274 | 0.53092 | 0.58095 | 0.63287 | 0.68672 | 0.74255 | 0.8004 | 0.85976 | 0.92064 | 0.98309 | 0 | 2.0148 | 6.3739 | 10.7395 | 13.9 | 17.9929 | 22.8935 | 31.2063 | 37.8486 | 50.4328
51 | PMA | Southern | NTZ | New Town | low | maximum | Battery | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0 | 0 | 0 | 0 | 0 | 0.0022529 | 0.0048252 | 0.0076953 | 0.0099002 | 0.012217 | 0.015212 | 0.019995 | 0.024401 | 0.032739 | 0.042336 | 0.0532 | 0.065545 | 0.07945 | 0.094933 | 0.11201 | 0.13068 | 0.15099 | 0.17272 | 0.19582 | 0.22031 | 0.2462 | 0.27293 | 0.3005 | 0.32892 | 0.3582 | 0.38835 | 0.41937 | 0.45127 | 0.48408 | 0.51747 | 0.55146 | 0.58604 | 0 | 2.2529 | 4.8252 | 7.6953 | 9.9002 | 12.2174 | 15.2119 | 19.995 | 24.4006 | 32.7388
51 | PMA | Southern | RIZ | Richmond | low | maximum | Battery | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0 | 0 | 0 | 0 | 0 | 0.00049651 | 0.0013642 | 0.002303 | 0.0030612 | 0.0039301 | 0.0049726 | 0.0066361 | 0.0081129 | 0.010862 | 0.014044 | 0.017665 | 0.021803 | 0.026489 | 0.031734 | 0.037548 | 0.04394 | 0.050924 | 0.058437 | 0.066462 | 0.075013 | 0.084101 | 0.093526 | 0.1033 | 0.11342 | 0.1239 | 0.13474 | 0.14596 | 0.15756 | 0.16956 | 0.18183 | 0.19439 | 0.20724 | 0 | 0.49651 | 1.3642 | 2.303 | 3.0612 | 3.9301 | 4.9726 | 6.6361 | 8.1129 | 10.8616
51 | PMA | Southern | RPZ | Rosny Park | low | maximum | Battery | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0 | 0 | 0 | 0 | 0 | 0.001236 | 0.0039104 | 0.0065887 | 0.0085277 | 0.011039 | 0.014045 | 0.019145 | 0.02322 | 0.030941 | 0.039888 | 0.050091 | 0.06177 | 0.07503 | 0.089909 | 0.10645 | 0.12468 | 0.14467 | 0.16623 | 0.18933 | 0.21402 | 0.24033 | 0.26771 | 0.29616 | 0.32572 | 0.35642 | 0.38827 | 0.42131 | 0.45556 | 0.49105 | 0.52747 | 0.56482 | 0.60313 | 0 | 1.236 | 3.9104 | 6.5887 | 8.5277 | 11.0387 | 14.0453 | 19.1454 | 23.2205 | 30.9409
51 | PMA | Southern | SBZ | Sandy Bay | low | maximum | Battery | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0 | 0 | 0 | 0 | 0 | 0.0043081 | 0.010311 | 0.017079 | 0.021252 | 0.025891 | 0.031834 | 0.041462 | 0.049811 | 0.065834 | 0.084264 | 0.10513 | 0.12883 | 0.15554 | 0.18529 | 0.21812 | 0.25407 | 0.29318 | 0.33509 | 0.37969 | 0.42702 | 0.47714 | 0.52893 | 0.58242 | 0.63764 | 0.6946 | 0.75333 | 0.81386 | 0.8762 | 0.94038 | 1.0058 | 1.0725 | 1.1405 | 0 | 4.3081 | 10.3108 | 17.0793 | 21.2519 | 25.8907 | 31.8343 | 41.4623 | 49.8106 | 65.834
51 | PMA | Southern | SUZ | Summerleas Road | low | maximum | Battery | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0 | 0 | 0 | 0 | 0 | 0.0013928 | 0.0045151 | 0.007797 | 0.009941 | 0.0123 | 0.014883 | 0.019384 | 0.023506 | 0.031302 | 0.040328 | 0.050608 | 0.062362 | 0.075688 | 0.090622 | 0.1072 | 0.12545 | 0.14543 | 0.16695 | 0.18998 | 0.21455 | 0.2407 | 0.26787 | 0.29607 | 0.32533 | 0.35567 | 0.3871 | 0.41966 | 0.45337 | 0.48825 | 0.52399 | 0.56059 | 0.59808 | 0 | 1.3928 | 4.5151 | 7.797 | 9.941 | 12.2999 | 14.8825 | 19.3843 | 23.5056 | 31.3022
51 | PMA | Southern | TWY2 | Wayatinah | low | maximum | Battery | non-coincident | POE50 | summer | zone | zone | MW | 0 | RT | 0 | 0 | 0 | 0 | 4.5648e-06 | 2.7764e-05 | 6.3353e-05 | 0.00010819 | 0.00013702 | 0.00017574 | 0.00021817 | 0.00028971 | 0.00034936 | 0.00046252 | 0.00059304 | 0.00074114 | 0.00090984 | 0.0011004 | 0.0013131 | 0.0015482 | 0.0018062 | 0.0020875 | 0.0023893 | 0.0027111 | 0.0030532 | 0.0034159 | 0.0037913 | 0.0041796 | 0.004581 | 0.0049957 | 0.0054239 | 0.0058658 | 0.0063215 | 0.0067914 | 0.0072711 | 0.0077607 | 0.0082603 | 0.0045648 | 0.027764 | 0.063353 | 0.10819 | 0.13702 | 0.17574 | 0.21817 | 0.28971 | 0.34936 | 0.46252
51 | PMA | Southern | WHZ | West Hobart Zone | low | maximum | Battery | non-coincident | POE50 | summer | zone | zone plus embedded | MW | 0 | Zs | 0 | 0 | 0 | 0 | 0 | 0.0036555 | 0.0083445 | 0.013713 | 0.016982 | 0.020624 | 0.025441 | 0.033135 | 0.039731 | 0.052432 | 0.06702 | 0.083511 | 0.10222 | 0.12328 | 0.14671 | 0.17252 | 0.20075 | 0.23143 | 0.26426 | 0.29916 | 0.33615 | 0.37527 | 0.41565 | 0.4573 | 0.50025 | 0.5445 | 0.59008 | 0.63698 | 0.68524 | 0.73486 | 0.78539 | 0.83683 | 0.8892 | 0 | 3.6555 | 8.3445 | 13.7133 | 16.9817 | 20.6236 | 25.4407 | 33.1346 | 39.7314 | 52.4319
51 | PMA | Southern | WTZ | Wayatinah | low | maximum | Battery | non-coincident | POE50 | summer | zone | zone | MW | #N/A | Zs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | PMA | Western | THZ | Trial Harbour | low | maximum | Battery | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0 | 0 | 0 | 0 | 0 | 7.7555e-05 | 0.00016114 | 0.00038565 | 0.00053461 | 0.0006984 | 0.0011241 | 0.001608 | 0.0018304 | 0.0023132 | 0.0028607 | 0.0034737 | 0.0041631 | 0.0049337 | 0.0057865 | 0.0067229 | 0.0077439 | 0.008851 | 0.010035 | 0.011292 | 0.012624 | 0.014033 | 0.015488 | 0.016991 | 0.018542 | 0.020142 | 0.021792 | 0.023491 | 0.025242 | 0.027045 | 0.028883 | 0.030758 | 0.032669 | 0 | 0.077555 | 0.16114 | 0.38565 | 0.53461 | 0.6984 | 1.1241 | 1.608 | 1.8304 | 2.3132
51 | PMA | Western | RBZ | Rosebery 22 kV | low | maximum | Battery | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0 | 0 | 0 | 0 | 8.151e-05 | 0.00024647 | 0.00053498 | 0.001128 | 0.0015649 | 0.0019993 | 0.0030239 | 0.004235 | 0.0048781 | 0.0062191 | 0.0077443 | 0.0094551 | 0.011382 | 0.013539 | 0.015926 | 0.018547 | 0.021404 | 0.0245 | 0.027806 | 0.031314 | 0.035028 | 0.038949 | 0.042995 | 0.047166 | 0.051464 | 0.055891 | 0.060448 | 0.065136 | 0.069957 | 0.074914 | 0.07996 | 0.085097 | 0.090326 | 0.08151 | 0.24647 | 0.53498 | 1.128 | 1.5649 | 1.9993 | 3.0239 | 4.235 | 4.8781 | 6.2191
51 | PMA | total terminal |  | total terminal | low | maximum | Battery | non-coincident | POE50 | summer | zone | zone | MW | #N/A | #N/A | 0 | 0 | 0 | 0 | 0.034477 | 0.13522 | 0.36171 | 0.59079 | 0.76773 | 0.94034 | 1.1577 | 1.4909 | 1.8097 | 2.405 | 3.0931 | 3.8754 | 4.768 | 5.7775 | 6.9058 | 8.1548 | 9.5264 | 11.023 | 12.6305 | 14.3456 | 16.1703 | 18.1068 | 20.1126 | 22.1887 | 24.3364 | 26.5569 | 28.8515 | 31.2214 | 33.6681 | 36.1928 | 38.7725 | 41.408 | 44.1002 | 34.4766 | 135.2206 | 361.7143 | 590.7933 | 767.7301 | 940.3353 | 1157.7341 | 1490.9417 | 1809.7196 | 2404.9827
51 | PMA | total zone |  | total zone | low | maximum | Battery | non-coincident | POE50 | summer | zone | zone | MW | #N/A | #N/A | 0 | 0 | 0 | 0 | 8.6075e-05 | 0.02292 | 0.059521 | 0.098911 | 0.12669 | 0.15915 | 0.19974 | 0.26617 | 0.32234 | 0.42914 | 0.55244 | 0.69251 | 0.85224 | 1.0329 | 1.2348 | 1.4583 | 1.7039 | 1.972 | 2.2602 | 2.5679 | 2.8954 | 3.2433 | 3.6039 | 3.9775 | 4.3643 | 4.7645 | 5.1784 | 5.6063 | 6.0483 | 6.5048 | 6.9716 | 7.4488 | 7.9367 | 0.086075 | 22.9196 | 59.5206 | 98.9109 | 126.6913 | 159.1522 | 199.742 | 266.1748 | 322.3423 | 429.1391
48 | PMA | George Town | TC01 | Comalco | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Camalco | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | George Town | TSW1 | Starwood | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Starwood | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | George Town | TTE1 | Temco | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Temco | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | North | TAL2 | Ax-Arthurs Lake 6.6 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | Ax | 0.00034908 | 0.00039755 | 0.00047542 | 0.00056389 | 0.00064917 | 0.0007212 | 0.00077566 | 0.00082811 | 0.00087891 | 0.00092637 | 0.00097104 | 0.0010132 | 0.0010523 | 0.0010886 | 0.0011232 | 0.0011555 | 0.0011856 | 0.0012147 | 0.0012432 | 0.0012709 | 0.0012977 | 0.0013234 | 0.0013482 | 0.0013722 | 0.0013952 | 0.0014175 | 0.0014391 | 0.0014596 | 0.0014795 | 0.0014985 | 0.0015167 | 0.0015342 | 0.001551 | 0.0015671 | 0.0015828 | 0.001598 | 0.0016127 | 0.64917 | 0.7212 | 0.77566 | 0.82811 | 0.87891 | 0.92637 | 0.97104 | 1.0132 | 1.0523 | 1.0886
48 | PMA | North | TAV2 | Avoca 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0.11792 | 0.14942 | 0.17489 | 0.19931 | 0.22958 | 0.26204 | 0.29118 | 0.31925 | 0.3461 | 0.37103 | 0.39432 | 0.41615 | 0.43622 | 0.45472 | 0.47219 | 0.48838 | 0.50334 | 0.51772 | 0.53167 | 0.54513 | 0.55805 | 0.57031 | 0.58208 | 0.59338 | 0.6041 | 0.61441 | 0.62427 | 0.63362 | 0.64256 | 0.65106 | 0.65913 | 0.66681 | 0.6741 | 0.68107 | 0.68775 | 0.69418 | 0.70037 | 229.5798 | 262.0416 | 291.1835 | 319.246 | 346.0993 | 371.0291 | 394.3222 | 416.1455 | 436.222 | 454.715
48 | PMA | North | TDE2 | Derby 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0.33085 | 0.3803 | 0.44369 | 0.5035 | 0.56922 | 0.63485 | 0.69251 | 0.7477 | 0.79989 | 0.84791 | 0.89239 | 0.93359 | 0.97114 | 1.0054 | 1.0374 | 1.0668 | 1.0936 | 1.1192 | 1.1438 | 1.1672 | 1.1895 | 1.2105 | 1.2304 | 1.2494 | 1.2671 | 1.2841 | 1.3002 | 1.3152 | 1.3295 | 1.343 | 1.3556 | 1.3676 | 1.3788 | 1.3894 | 1.3995 | 1.4091 | 1.4183 | 569.2204 | 634.8544 | 692.5107 | 747.7021 | 799.8929 | 847.9126 | 892.3895 | 933.5934 | 971.1352 | 1005.3678
48 | PMA | North | THA3 | Hadspen 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 2.9419 | 3.5359 | 4.1462 | 4.8132 | 5.594 | 6.3762 | 7.1135 | 7.8189 | 8.4918 | 9.1155 | 9.6963 | 10.2392 | 10.7373 | 11.1948 | 11.6259 | 12.0244 | 12.3915 | 12.7434 | 13.0838 | 13.4115 | 13.7251 | 14.0218 | 14.3061 | 14.5782 | 14.8355 | 15.0824 | 15.318 | 15.5408 | 15.7531 | 15.9544 | 16.1452 | 16.326 | 16.4974 | 16.6607 | 16.8169 | 16.9668 | 17.1106 | 5593.967 | 6376.1529 | 7113.4569 | 7818.8826 | 8491.8215 | 9115.4758 | 9696.3055 | 10239.2168 | 10737.2588 | 11194.7564
48 | PMA | North | TMY2 | Mowbray 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0.9257 | 1.1315 | 1.351 | 1.5707 | 1.7848 | 1.9648 | 2.1296 | 2.2857 | 2.4344 | 2.5712 | 2.6979 | 2.8157 | 2.9232 | 3.0214 | 3.1135 | 3.1981 | 3.2756 | 3.3494 | 3.4205 | 3.4886 | 3.5533 | 3.6142 | 3.6723 | 3.7275 | 3.7795 | 3.829 | 3.8761 | 3.9203 | 3.9622 | 4.0017 | 4.0389 | 4.074 | 4.107 | 4.1383 | 4.1681 | 4.1965 | 4.2236 | 1784.8481 | 1964.7566 | 2129.6241 | 2285.6724 | 2434.3915 | 2571.1787 | 2697.8737 | 2815.7368 | 2923.2225 | 3021.4243
48 | PMA | North | TPM3 | Palmerston 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | North | TSD2 | Scottsdale 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0.68795 | 0.77766 | 0.89744 | 1.0187 | 1.1449 | 1.2718 | 1.3856 | 1.4943 | 1.5973 | 1.6921 | 1.7799 | 1.8614 | 1.9357 | 2.0035 | 2.067 | 2.1253 | 2.1787 | 2.2295 | 2.2783 | 2.3251 | 2.3695 | 2.4113 | 2.4511 | 2.489 | 2.5246 | 2.5586 | 2.5908 | 2.621 | 2.6497 | 2.6767 | 2.7022 | 2.7262 | 2.7488 | 2.7703 | 2.7906 | 2.8101 | 2.8287 | 1144.9025 | 1271.8 | 1385.6446 | 1494.3068 | 1597.2659 | 1692.0602 | 1779.9103 | 1861.393 | 1935.6886 | 2003.4982
48 | PMA | North | TSL2 | St Leonards 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 1.3143 | 1.5404 | 1.8154 | 2.142 | 2.4434 | 2.6818 | 2.9004 | 3.1074 | 3.3047 | 3.4862 | 3.6542 | 3.8106 | 3.9533 | 4.0836 | 4.2057 | 4.318 | 4.4209 | 4.5189 | 4.6133 | 4.7036 | 4.7896 | 4.8705 | 4.9476 | 5.0209 | 5.0899 | 5.1558 | 5.2182 | 5.277 | 5.3326 | 5.3851 | 5.4346 | 5.4812 | 5.5251 | 5.5668 | 5.6063 | 5.6441 | 5.6801 | 2443.3811 | 2681.7732 | 2900.4355 | 3107.427 | 3304.695 | 3486.1592 | 3654.2466 | 3810.6275 | 3953.2512 | 4083.5657
48 | PMA | North | TSL3 | St Leonards 22 kV (scheduled load) | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Firmus Grid | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | North | TSM2 | St Marys 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0.94174 | 1.1809 | 1.4436 | 1.6677 | 1.8961 | 2.0737 | 2.2147 | 2.3494 | 2.4786 | 2.5973 | 2.7078 | 2.8108 | 2.905 | 2.9914 | 3.0725 | 3.1473 | 3.216 | 3.2817 | 3.3451 | 3.4059 | 3.464 | 3.5188 | 3.5712 | 3.6212 | 3.6683 | 3.7135 | 3.7564 | 3.7969 | 3.8354 | 3.8718 | 3.9063 | 3.9388 | 3.9696 | 3.9988 | 4.0267 | 4.0534 | 4.0789 | 1896.118 | 2073.7058 | 2214.748 | 2349.417 | 2478.5671 | 2597.346 | 2707.8062 | 2810.8256 | 2905.03 | 2991.3556
48 | PMA | Northwest | TDP2 | Devonport 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 1.8825 | 2.1757 | 2.5355 | 2.9784 | 3.4419 | 3.8174 | 4.126 | 4.4196 | 4.7 | 4.959 | 5.1996 | 5.4241 | 5.6294 | 5.8176 | 5.9945 | 6.1576 | 6.3075 | 6.4507 | 6.5891 | 6.7218 | 6.8486 | 6.9683 | 7.0826 | 7.1919 | 7.2948 | 7.3935 | 7.4873 | 7.5758 | 7.66 | 7.7396 | 7.8149 | 7.886 | 7.9533 | 8.0173 | 8.0783 | 8.1367 | 8.1926 | 3441.8621 | 3817.4032 | 4126.0268 | 4419.5824 | 4700.0363 | 4958.9612 | 5199.635 | 5424.0693 | 5629.4072 | 5817.586
48 | PMA | Northwest | TEB2 | Emu Bay 11 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Emu Bay | MI | 0.13673 | 0.16675 | 0.19871 | 0.23161 | 0.26534 | 0.29275 | 0.31225 | 0.33053 | 0.34802 | 0.36396 | 0.37866 | 0.39227 | 0.40462 | 0.41584 | 0.4263 | 0.43586 | 0.44458 | 0.45284 | 0.46075 | 0.46828 | 0.47541 | 0.48208 | 0.48841 | 0.4944 | 0.5 | 0.50531 | 0.51033 | 0.51502 | 0.51945 | 0.5236 | 0.52748 | 0.53113 | 0.53455 | 0.53777 | 0.54081 | 0.5437 | 0.54645 | 265.3371 | 292.7451 | 312.2479 | 330.5276 | 348.0208 | 363.9613 | 378.6647 | 392.275 | 404.6173 | 415.8369
48 | PMA | Northwest | THM2 | Hampshire | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Hampshire | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Northwest | TPL2 | Port Latta | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | Port Latta | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Northwest | TRA2 | Railton 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Northwest | TSH3 | Sheffield | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Northwest | TST2 | Smithton 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0.11298 | 0.13907 | 0.1642 | 0.18346 | 0.21307 | 0.24741 | 0.28166 | 0.31476 | 0.3456 | 0.3741 | 0.40037 | 0.42462 | 0.44666 | 0.46668 | 0.48535 | 0.50243 | 0.51798 | 0.53273 | 0.54685 | 0.5603 | 0.57303 | 0.58495 | 0.59624 | 0.60693 | 0.61693 | 0.62643 | 0.63539 | 0.64377 | 0.65167 | 0.65908 | 0.66603 | 0.67254 | 0.67865 | 0.6844 | 0.68985 | 0.69501 | 0.69991 | 213.0668 | 247.4094 | 281.6624 | 314.7564 | 345.5951 | 374.1009 | 400.3736 | 424.6187 | 446.6622 | 466.6846
48 | PMA | Northwest | TUL2 | Ulverstone 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 2.3973 | 2.7385 | 3.152 | 3.6105 | 4.1166 | 4.5701 | 4.9342 | 5.2795 | 5.6085 | 5.9113 | 6.1917 | 6.4523 | 6.69 | 6.907 | 7.1104 | 7.2972 | 7.4683 | 7.6313 | 7.7881 | 7.9381 | 8.0809 | 8.2151 | 8.343 | 8.4646 | 8.5789 | 8.688 | 8.7915 | 8.8886 | 8.9807 | 9.0675 | 9.1493 | 9.2263 | 9.2988 | 9.3675 | 9.4328 | 9.4951 | 9.5545 | 4116.5699 | 4570.097 | 4934.2228 | 5279.4811 | 5608.5022 | 5911.3163 | 6191.6824 | 6452.3257 | 6689.9917 | 6907.033
48 | PMA | Northwest | TWV2 | Wesley Vale 11 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | Wesley Vale | MI | 0.36594 | 0.43045 | 0.52262 | 0.62956 | 0.73429 | 0.82744 | 0.91217 | 0.9937 | 1.0723 | 1.1458 | 1.215 | 1.2802 | 1.3405 | 1.3964 | 1.4496 | 1.4993 | 1.5454 | 1.59 | 1.6335 | 1.6758 | 1.7167 | 1.7557 | 1.7934 | 1.8298 | 1.8646 | 1.8982 | 1.9306 | 1.9615 | 1.9912 | 2.0196 | 2.0468 | 2.0728 | 2.0977 | 2.1216 | 2.1447 | 2.167 | 2.1886 | 734.2942 | 827.4446 | 912.1748 | 993.7003 | 1072.3061 | 1145.8406 | 1214.9565 | 1280.1575 | 1340.4996 | 1396.4433
48 | PMA | Southern | TBW2 | Bridgewater 11 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 1.6264 | 1.8376 | 2.1832 | 2.5897 | 2.9725 | 3.2896 | 3.5297 | 3.7611 | 3.9854 | 4.195 | 4.3925 | 4.5792 | 4.7523 | 4.9131 | 5.0663 | 5.2095 | 5.3429 | 5.4723 | 5.5988 | 5.722 | 5.8413 | 5.9554 | 6.0661 | 6.1732 | 6.2756 | 6.3752 | 6.4712 | 6.5631 | 6.6517 | 6.7367 | 6.8183 | 6.8965 | 6.9715 | 7.0438 | 7.1139 | 7.1819 | 7.248 | 2972.4663 | 3289.5635 | 3529.7436 | 3761.1438 | 3985.3753 | 4195.0464 | 4392.539 | 4579.2239 | 4752.2984 | 4913.0967
48 | PMA | Southern | TBYA | Boyer SWA | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Boyer | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Southern | TBYB | Boyer SWB | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Boyer | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Southern | TCR2 | Creek Rd 33 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 2.5047 | 2.8775 | 3.3595 | 3.9287 | 4.5636 | 5.1389 | 5.5827 | 6.0034 | 6.4063 | 6.7785 | 7.1246 | 7.4479 | 7.744 | 8.0156 | 8.2713 | 8.5072 | 8.7243 | 8.932 | 9.1328 | 9.3258 | 9.5102 | 9.6845 | 9.8512 | 10.0106 | 10.1611 | 10.3053 | 10.4428 | 10.5725 | 10.696 | 10.813 | 10.9237 | 11.0285 | 11.1277 | 11.222 | 11.3121 | 11.3985 | 11.4813 | 4563.6299 | 5138.933 | 5582.673 | 6003.4019 | 6406.3186 | 6778.4881 | 7124.6308 | 7447.9318 | 7743.9852 | 8015.6085
48 | PMA | Southern | TCS3 | Chapel St 11 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 1.0991 | 1.249 | 1.4605 | 1.7133 | 1.9893 | 2.2592 | 2.4809 | 2.6903 | 2.8907 | 3.0757 | 3.2476 | 3.4081 | 3.555 | 3.6897 | 3.8163 | 3.9331 | 4.0405 | 4.1432 | 4.2424 | 4.3376 | 4.4286 | 4.5145 | 4.5966 | 4.675 | 4.749 | 4.8199 | 4.8874 | 4.951 | 5.0115 | 5.0688 | 5.123 | 5.1742 | 5.2226 | 5.2687 | 5.3126 | 5.3547 | 5.3949 | 1989.2595 | 2259.1565 | 2480.9457 | 2690.32 | 2890.6985 | 3075.6964 | 3247.6354 | 3408.1374 | 3554.9975 | 3689.6523
48 | PMA | Southern | TDB2 | Derwent Bridge 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0.0058532 | 0.0066611 | 0.0076296 | 0.0087712 | 0.010037 | 0.011187 | 0.012055 | 0.012881 | 0.013673 | 0.014407 | 0.015091 | 0.015732 | 0.01632 | 0.016861 | 0.017371 | 0.017843 | 0.018279 | 0.018696 | 0.019101 | 0.019491 | 0.019864 | 0.020218 | 0.020557 | 0.020882 | 0.02119 | 0.021485 | 0.021768 | 0.022035 | 0.02229 | 0.022532 | 0.022762 | 0.022979 | 0.023186 | 0.023383 | 0.023572 | 0.023753 | 0.023927 | 10.0369 | 11.1874 | 12.0551 | 12.8811 | 13.6731 | 14.4073 | 15.0915 | 15.7321 | 16.3201 | 16.8609
48 | PMA | Southern | TEL2 | Electrona 11 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0.27974 | 0.31639 | 0.3626 | 0.41424 | 0.46804 | 0.52105 | 0.56432 | 0.60568 | 0.64542 | 0.68239 | 0.71697 | 0.74946 | 0.77939 | 0.80702 | 0.83317 | 0.85745 | 0.87992 | 0.90155 | 0.92258 | 0.94291 | 0.96245 | 0.98102 | 0.9989 | 1.0161 | 1.0324 | 1.0481 | 1.0632 | 1.0775 | 1.0912 | 1.1043 | 1.1167 | 1.1285 | 1.1398 | 1.1506 | 1.1609 | 1.1709 | 1.1805 | 468.0364 | 521.047 | 564.3236 | 605.6753 | 645.4209 | 682.387 | 716.9719 | 749.463 | 779.3929 | 807.0167
48 | PMA | Southern | THR2 | Huon River | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Huon River | MI | 0.00077139 | 0.00089743 | 0.0010512 | 0.0012212 | 0.001407 | 0.0015801 | 0.0017183 | 0.0018512 | 0.0019797 | 0.0020995 | 0.0022121 | 0.0023183 | 0.0024165 | 0.0025074 | 0.0025939 | 0.0026744 | 0.0027492 | 0.0028215 | 0.002892 | 0.0029604 | 0.0030264 | 0.0030894 | 0.0031503 | 0.003209 | 0.0032649 | 0.0033191 | 0.0033711 | 0.0034208 | 0.0034685 | 0.0035141 | 0.0035576 | 0.0035992 | 0.003639 | 0.0036771 | 0.003714 | 0.0037496 | 0.003784 | 1.407 | 1.5801 | 1.7183 | 1.8512 | 1.9797 | 2.0995 | 2.2121 | 2.3183 | 2.4165 | 2.5074
48 | PMA | Southern | TK12 | Kingston 11 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 1.7336 | 1.9837 | 2.3406 | 2.7539 | 3.1922 | 3.5846 | 3.9058 | 4.2128 | 4.5078 | 4.7822 | 5.039 | 5.2802 | 5.5025 | 5.7076 | 5.9018 | 6.0822 | 6.2491 | 6.4098 | 6.566 | 6.717 | 6.8622 | 7.0002 | 7.1331 | 7.2608 | 7.3821 | 7.499 | 7.6111 | 7.7175 | 7.8194 | 7.9165 | 8.0089 | 8.0968 | 8.1806 | 8.2607 | 8.3377 | 8.4118 | 8.4833 | 3192.219 | 3584.623 | 3905.8354 | 4212.7778 | 4507.7941 | 4782.2149 | 5038.9766 | 5280.2171 | 5502.459 | 5707.5939
48 | PMA | Southern | TK13 | Kingston 33 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Southern | TKE2 | Kermandie 11 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0.20696 | 0.24483 | 0.28985 | 0.33256 | 0.3827 | 0.42947 | 0.46676 | 0.50262 | 0.5373 | 0.56966 | 0.60007 | 0.62874 | 0.65526 | 0.67982 | 0.70317 | 0.72493 | 0.74514 | 0.76468 | 0.78374 | 0.80224 | 0.8201 | 0.83712 | 0.85358 | 0.86946 | 0.88459 | 0.89924 | 0.91333 | 0.92676 | 0.93967 | 0.95201 | 0.9638 | 0.97506 | 0.98583 | 0.99617 | 1.0061 | 1.0158 | 1.0251 | 382.698 | 429.4741 | 466.7629 | 502.6209 | 537.3003 | 569.6585 | 600.071 | 628.7414 | 655.2563 | 679.8248
48 | PMA | Southern | TLF2 | Lindisfarne 33 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 1.3376 | 1.5206 | 1.7944 | 2.1302 | 2.5108 | 2.8549 | 3.1117 | 3.358 | 3.5951 | 3.8161 | 4.0232 | 4.2181 | 4.398 | 4.5643 | 4.722 | 4.8687 | 5.0046 | 5.1358 | 5.2634 | 5.3871 | 5.5062 | 5.6196 | 5.7289 | 5.8341 | 5.9343 | 6.031 | 6.1238 | 6.2121 | 6.2968 | 6.3776 | 6.4547 | 6.5281 | 6.5982 | 6.6653 | 6.7299 | 6.7923 | 6.8525 | 2510.7635 | 2854.9382 | 3111.6989 | 3358.0279 | 3595.0685 | 3816.0948 | 4023.2369 | 4218.1141 | 4397.9871 | 4564.2812
48 | PMA | Southern | TMB2 | Meadowbank 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Southern | TMT2 | Mornington 33 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 1.8847 | 2.1391 | 2.5251 | 3.0197 | 3.594 | 4.1066 | 4.4887 | 4.8552 | 5.2077 | 5.5364 | 5.8443 | 6.1338 | 6.401 | 6.648 | 6.8821 | 7.0998 | 7.3015 | 7.496 | 7.6853 | 7.8685 | 8.045 | 8.2129 | 8.3747 | 8.5305 | 8.6787 | 8.8217 | 8.959 | 9.0895 | 9.2146 | 9.3339 | 9.4477 | 9.5561 | 9.6594 | 9.7584 | 9.8537 | 9.9457 | 10.0344 | 3593.9952 | 4106.5919 | 4488.7071 | 4855.2004 | 5207.7406 | 5536.3757 | 5844.2698 | 6133.8407 | 6401.0359 | 6647.9801
48 | PMA | Southern | TNH2 | North Hobart 11 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0.45368 | 0.51946 | 0.59562 | 0.68753 | 0.79962 | 0.8991 | 0.97258 | 1.0422 | 1.1088 | 1.1702 | 1.2272 | 1.2804 | 1.329 | 1.3734 | 1.4152 | 1.4537 | 1.4891 | 1.5228 | 1.5554 | 1.5867 | 1.6165 | 1.6446 | 1.6714 | 1.697 | 1.7211 | 1.7442 | 1.7662 | 1.7868 | 1.8065 | 1.825 | 1.8426 | 1.8591 | 1.8748 | 1.8896 | 1.9038 | 1.9173 | 1.9302 | 799.6171 | 899.097 | 972.5847 | 1042.2182 | 1108.834 | 1170.2327 | 1227.2359 | 1280.3796 | 1328.9571 | 1373.442
48 | PMA | Southern | TNN2 | New Norfolk 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | Brynn Estyn | MI | 0.14705 | 0.1672 | 0.19176 | 0.22064 | 0.25239 | 0.28116 | 0.30285 | 0.32352 | 0.34335 | 0.36173 | 0.37887 | 0.39493 | 0.40967 | 0.42324 | 0.43605 | 0.4479 | 0.45884 | 0.46933 | 0.47951 | 0.48932 | 0.49872 | 0.50763 | 0.51618 | 0.52438 | 0.53214 | 0.5396 | 0.54673 | 0.55348 | 0.55993 | 0.56606 | 0.57187 | 0.57739 | 0.58263 | 0.58763 | 0.59242 | 0.59703 | 0.60145 | 252.3942 | 281.1583 | 302.854 | 323.5219 | 343.3459 | 361.7304 | 378.8717 | 394.927 | 409.6728 | 423.24
48 | PMA | Southern | TR13 | Risdon 11 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Risdon | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Southern | TR14 | Risdon 33 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0.91939 | 1.0443 | 1.201 | 1.4 | 1.6344 | 1.8461 | 2.0147 | 2.1742 | 2.3269 | 2.4679 | 2.599 | 2.7214 | 2.8334 | 2.9362 | 3.0329 | 3.1221 | 3.2042 | 3.2827 | 3.3586 | 3.4315 | 3.5011 | 3.5669 | 3.6298 | 3.69 | 3.7468 | 3.8011 | 3.853 | 3.9019 | 3.9484 | 3.9925 | 4.0342 | 4.0736 | 4.1109 | 4.1464 | 4.1804 | 4.2129 | 4.244 | 1634.3882 | 1846.1445 | 2014.7367 | 2174.1912 | 2326.8722 | 2467.8637 | 2598.9549 | 2721.3655 | 2833.419 | 2936.1986
48 | PMA | Southern | TRK2 | Rokeby 11 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 1.607 | 1.8442 | 2.1931 | 2.634 | 3.1514 | 3.6062 | 3.9452 | 4.2704 | 4.5831 | 4.8747 | 5.1478 | 5.4047 | 5.6417 | 5.8607 | 6.0684 | 6.2615 | 6.4404 | 6.6129 | 6.7808 | 6.9433 | 7.0998 | 7.2487 | 7.3922 | 7.5304 | 7.6618 | 7.7886 | 7.9103 | 8.0261 | 8.137 | 8.2428 | 8.3437 | 8.4398 | 8.5314 | 8.6192 | 8.7037 | 8.7852 | 8.8638 | 3151.4324 | 3606.2137 | 3945.2245 | 4270.3678 | 4583.123 | 4874.6652 | 5147.8004 | 5404.6749 | 5641.6945 | 5860.7448
48 | PMA | Southern | TS02 | Sorell | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0.7646 | 0.89123 | 1.0632 | 1.2586 | 1.4757 | 1.6708 | 1.8174 | 1.958 | 2.0937 | 2.2205 | 2.3394 | 2.4516 | 2.5553 | 2.6514 | 2.7427 | 2.8278 | 2.9068 | 2.9832 | 3.0578 | 3.1301 | 3.2 | 3.2666 | 3.331 | 3.3932 | 3.4525 | 3.5098 | 3.5651 | 3.6177 | 3.6684 | 3.7168 | 3.7631 | 3.8073 | 3.8497 | 3.8903 | 3.9296 | 3.9676 | 4.0044 | 1475.689 | 1670.7518 | 1817.4261 | 1958.011 | 2093.729 | 2220.4639 | 2339.4214 | 2451.6002 | 2555.3157 | 2651.3958
48 | PMA | Southern | TTB2 | Triabunna 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0.15761 | 0.19624 | 0.23445 | 0.27077 | 0.31435 | 0.34859 | 0.37417 | 0.39867 | 0.42226 | 0.44416 | 0.46466 | 0.4839 | 0.50162 | 0.51798 | 0.53345 | 0.54781 | 0.5611 | 0.57389 | 0.58632 | 0.59834 | 0.60989 | 0.62086 | 0.63142 | 0.64157 | 0.6512 | 0.6605 | 0.6694 | 0.67785 | 0.68594 | 0.69365 | 0.70099 | 0.70797 | 0.71462 | 0.72098 | 0.72709 | 0.73298 | 0.73866 | 314.355 | 348.5916 | 374.1659 | 398.6692 | 422.2581 | 444.1642 | 464.657 | 483.9021 | 501.6239 | 517.9751
48 | PMA | Southern | TTU2 | Tungatinah 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0.041793 | 0.047521 | 0.054392 | 0.06249 | 0.071464 | 0.079621 | 0.085772 | 0.091629 | 0.097243 | 0.10245 | 0.1073 | 0.11184 | 0.11601 | 0.11984 | 0.12346 | 0.12681 | 0.12989 | 0.13286 | 0.13572 | 0.13849 | 0.14113 | 0.14364 | 0.14605 | 0.14835 | 0.15053 | 0.15263 | 0.15463 | 0.15652 | 0.15833 | 0.16005 | 0.16168 | 0.16322 | 0.16469 | 0.16608 | 0.16742 | 0.16871 | 0.16994 | 71.4638 | 79.6206 | 85.7719 | 91.6286 | 97.2434 | 102.4486 | 107.2993 | 111.8408 | 116.0099 | 119.844
48 | PMA | Southern | TWA2 | Waddamana 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0.017701 | 0.02016 | 0.02411 | 0.028596 | 0.032926 | 0.036587 | 0.039356 | 0.042023 | 0.044605 | 0.047018 | 0.049289 | 0.051434 | 0.053422 | 0.055267 | 0.057024 | 0.058665 | 0.060192 | 0.061672 | 0.06312 | 0.064528 | 0.065891 | 0.067193 | 0.068455 | 0.069677 | 0.070844 | 0.071978 | 0.073071 | 0.074116 | 0.075123 | 0.07609 | 0.077016 | 0.077904 | 0.078755 | 0.079575 | 0.080369 | 0.08114 | 0.081888 | 32.926 | 36.5869 | 39.3562 | 42.0228 | 44.6052 | 47.018 | 49.289 | 51.4342 | 53.4216 | 55.2667
48 | PMA | Western | TGO2 | Gordon | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Western | TNT2 | Newton 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 7.924e-05 | 8.809e-05 | 9.9043e-05 | 0.00012121 | 0.0001499 | 0.0001675 | 0.00017669 | 0.00018544 | 0.00019381 | 0.00020156 | 0.00020877 | 0.00021551 | 0.00022168 | 0.00022735 | 0.0002327 | 0.00023763 | 0.00024217 | 0.00024652 | 0.00025072 | 0.00025477 | 0.00025864 | 0.0002623 | 0.0002658 | 0.00026915 | 0.00027232 | 0.00027536 | 0.00027825 | 0.00028099 | 0.0002836 | 0.00028607 | 0.00028841 | 0.00029062 | 0.00029272 | 0.00029472 | 0.00029663 | 0.00029846 | 0.00030021 | 0.1499 | 0.1675 | 0.17669 | 0.18544 | 0.19381 | 0.20156 | 0.20877 | 0.21551 | 0.22168 | 0.22735
48 | PMA | Western | TNT3 | Ax-Newton 11 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | Ax | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Western | TQT2 | Queenstown 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0.13383 | 0.14877 | 0.16727 | 0.2047 | 0.25316 | 0.28289 | 0.29841 | 0.31318 | 0.32732 | 0.34041 | 0.35258 | 0.36396 | 0.37439 | 0.38397 | 0.39299 | 0.40132 | 0.40899 | 0.41634 | 0.42344 | 0.43027 | 0.43681 | 0.44299 | 0.44891 | 0.45457 | 0.45991 | 0.46504 | 0.46993 | 0.47456 | 0.47896 | 0.48313 | 0.48708 | 0.49082 | 0.49436 | 0.49774 | 0.50096 | 0.50405 | 0.50702 | 253.161 | 282.8856 | 298.4135 | 313.183 | 327.3193 | 340.4054 | 352.5829 | 363.9633 | 374.3942 | 383.9707
48 | PMA | Western | TQT3 | Queenstown 11 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Queenstown 11 kV | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Western | TQU2 | Que | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Que | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Western | TRB2 | Rosebery 44 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Rosebery | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Western | TSR2 | Savage River | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Savage River | MI | 0.048061 | 0.056142 | 0.065245 | 0.074328 | 0.085222 | 0.094846 | 0.10261 | 0.10997 | 0.11696 | 0.12338 | 0.12931 | 0.13482 | 0.13983 | 0.14439 | 0.14866 | 0.15258 | 0.15615 | 0.15955 | 0.16282 | 0.16594 | 0.1689 | 0.17168 | 0.17432 | 0.17682 | 0.17918 | 0.18142 | 0.18354 | 0.18552 | 0.1874 | 0.18917 | 0.19084 | 0.1924 | 0.19387 | 0.19526 | 0.19658 | 0.19783 | 0.19902 | 85.2224 | 94.8455 | 102.6082 | 109.9685 | 116.9556 | 123.3784 | 129.3135 | 134.8181 | 139.8281 | 144.3936
48 | PMA | Southern | BEZ | Bellerive | low | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.5472 | 0.6176 | 0.72902 | 0.87404 | 1.0419 | 1.1909 | 1.3019 | 1.4084 | 1.5109 | 1.6063 | 1.6958 | 1.7799 | 1.8576 | 1.9293 | 1.9973 | 2.0606 | 2.1192 | 2.1757 | 2.2307 | 2.2839 | 2.3352 | 2.3839 | 2.4309 | 2.4762 | 2.5192 | 2.5608 | 2.6006 | 2.6385 | 2.6749 | 2.7095 | 2.7426 | 2.7741 | 2.8041 | 2.8328 | 2.8605 | 2.8872 | 2.9129 | 1041.9233 | 1190.8799 | 1301.9176 | 1408.4133 | 1510.8517 | 1606.342 | 1695.8035 | 1779.9391 | 1857.5716 | 1929.3185
48 | PMA | Southern | CLZ | Claremont | low | maximum | PV | non-coincident | POE50 | summer | zone | zone plus embedded | MW | 0 | Zs | 0.83836 | 0.95383 | 1.1451 | 1.3743 | 1.6105 | 1.8225 | 1.9969 | 2.1617 | 2.3196 | 2.4656 | 2.6014 | 2.7283 | 2.8445 | 2.9512 | 3.0517 | 3.1445 | 3.2299 | 3.3117 | 3.3907 | 3.4667 | 3.5395 | 3.6082 | 3.674 | 3.7369 | 3.7964 | 3.8534 | 3.9077 | 3.9591 | 4.008 | 4.0543 | 4.0982 | 4.1397 | 4.1791 | 4.2166 | 4.2524 | 4.2868 | 4.3197 | 1610.5236 | 1822.4644 | 1996.875 | 2161.7167 | 2319.6286 | 2465.5801 | 2601.3797 | 2728.283 | 2844.5293 | 2951.2371
48 | PMA | Southern | DPZ | Derwent Park | low | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.30994 | 0.35038 | 0.4067 | 0.4768 | 0.5529 | 0.6239 | 0.68196 | 0.73694 | 0.78967 | 0.83847 | 0.88393 | 0.92646 | 0.96548 | 1.0013 | 1.0352 | 1.0664 | 1.0952 | 1.1229 | 1.1496 | 1.1754 | 1.2 | 1.2234 | 1.2458 | 1.2672 | 1.2875 | 1.307 | 1.3256 | 1.3432 | 1.36 | 1.376 | 1.3911 | 1.4054 | 1.4191 | 1.432 | 1.4445 | 1.4564 | 1.4679 | 552.8968 | 623.8984 | 681.963 | 736.9414 | 789.6705 | 838.4667 | 883.9278 | 926.4634 | 965.4778 | 1001.3383
48 | PMA | Southern | EHZ | East Hobart | low | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.1669 | 0.19393 | 0.22298 | 0.25522 | 0.2961 | 0.33363 | 0.36136 | 0.38763 | 0.41277 | 0.43593 | 0.45744 | 0.47749 | 0.49582 | 0.51261 | 0.52838 | 0.5429 | 0.55624 | 0.56899 | 0.58127 | 0.59306 | 0.60431 | 0.61492 | 0.62504 | 0.63471 | 0.64381 | 0.65252 | 0.6608 | 0.6686 | 0.67601 | 0.68302 | 0.68963 | 0.69588 | 0.70178 | 0.70738 | 0.71272 | 0.71783 | 0.72271 | 296.0971 | 333.6307 | 361.3585 | 387.6322 | 412.7673 | 435.9341 | 457.4425 | 477.4948 | 495.8242 | 512.6094
48 | PMA | Southern | GBZ | Geilston Bay | low | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.85515 | 0.96363 | 1.1408 | 1.3486 | 1.5678 | 1.7698 | 1.9205 | 2.0651 | 2.2043 | 2.3341 | 2.4558 | 2.5703 | 2.6761 | 2.7739 | 2.8666 | 2.9529 | 3.033 | 3.1102 | 3.1854 | 3.2582 | 3.3284 | 3.3953 | 3.4597 | 3.5218 | 3.5809 | 3.638 | 3.6929 | 3.745 | 3.7951 | 3.8428 | 3.8884 | 3.9318 | 3.9733 | 4.0131 | 4.0513 | 4.0883 | 4.124 | 1567.7819 | 1769.8343 | 1920.4975 | 2065.0921 | 2204.284 | 2334.1028 | 2455.806 | 2570.3368 | 2676.0808 | 2773.8724
48 | PMA | Southern | GRZ | Gretna | low | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.0074076 | 0.0084189 | 0.0096327 | 0.011063 | 0.012648 | 0.014088 | 0.015174 | 0.016208 | 0.0172 | 0.018119 | 0.018975 | 0.019777 | 0.020513 | 0.02119 | 0.021829 | 0.02242 | 0.022965 | 0.023488 | 0.023994 | 0.024482 | 0.02495 | 0.025392 | 0.025817 | 0.026224 | 0.026609 | 0.026979 | 0.027333 | 0.027667 | 0.027986 | 0.028289 | 0.028577 | 0.028849 | 0.029108 | 0.029355 | 0.029591 | 0.029818 | 0.030036 | 12.6476 | 14.0878 | 15.174 | 16.2081 | 17.1996 | 18.1186 | 18.9752 | 19.7771 | 20.5132 | 21.1902
48 | PMA | Southern | HOZ | Howrah | low | maximum | PV | non-coincident | POE50 | summer | zone | zone plus embedded | MW | 0 | Zs | 0.89544 | 1.0103 | 1.1989 | 1.446 | 1.7293 | 1.9789 | 2.1649 | 2.3433 | 2.5149 | 2.6749 | 2.8247 | 2.9657 | 3.0957 | 3.2159 | 3.3299 | 3.4358 | 3.534 | 3.6286 | 3.7207 | 3.8099 | 3.8958 | 3.9775 | 4.0562 | 4.1321 | 4.2041 | 4.2737 | 4.3405 | 4.404 | 4.4649 | 4.523 | 4.5783 | 4.631 | 4.6813 | 4.7295 | 4.7758 | 4.8205 | 4.8637 | 1729.3437 | 1978.8783 | 2164.8929 | 2343.2981 | 2514.9059 | 2674.874 | 2824.7421 | 2965.6878 | 3095.7393 | 3215.9308
48 | PMA | Southern | NTZ | New Town | low | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.45273 | 0.51284 | 0.58701 | 0.68503 | 0.8037 | 0.90882 | 0.99264 | 1.0718 | 1.1476 | 1.2176 | 1.2825 | 1.3431 | 1.3986 | 1.4494 | 1.4972 | 1.5412 | 1.5817 | 1.6204 | 1.6578 | 1.6936 | 1.7279 | 1.7602 | 1.791 | 1.8205 | 1.8483 | 1.8749 | 1.9003 | 1.9241 | 1.9468 | 1.9683 | 1.9886 | 2.0078 | 2.0259 | 2.0431 | 2.0596 | 2.0753 | 2.0904 | 803.7032 | 908.8158 | 992.6356 | 1071.8366 | 1147.6213 | 1217.5511 | 1282.5203 | 1343.142 | 1398.5913 | 1449.4108
48 | PMA | Southern | RIZ | Richmond | low | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.31002 | 0.35457 | 0.41891 | 0.49458 | 0.57898 | 0.65705 | 0.71793 | 0.77627 | 0.8325 | 0.88481 | 0.93381 | 0.97988 | 1.0224 | 1.0616 | 1.0989 | 1.1335 | 1.1656 | 1.1965 | 1.2266 | 1.2558 | 1.2839 | 1.3106 | 1.3364 | 1.3612 | 1.3849 | 1.4077 | 1.4297 | 1.4506 | 1.4706 | 1.4898 | 1.508 | 1.5255 | 1.5421 | 1.5581 | 1.5735 | 1.5884 | 1.6027 | 578.9777 | 657.0494 | 717.9344 | 776.2682 | 832.4996 | 884.8076 | 933.8064 | 979.8838 | 1022.3787 | 1061.6487
48 | PMA | Southern | RPZ | Rosny Park | low | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.62925 | 0.70515 | 0.83117 | 0.99073 | 1.1673 | 1.3275 | 1.4469 | 1.5615 | 1.6717 | 1.7744 | 1.8707 | 1.9612 | 2.0448 | 2.122 | 2.1952 | 2.2633 | 2.3264 | 2.3872 | 2.4464 | 2.5038 | 2.559 | 2.6115 | 2.6621 | 2.7109 | 2.7572 | 2.802 | 2.845 | 2.8858 | 2.925 | 2.9623 | 2.9979 | 3.0319 | 3.0642 | 3.0952 | 3.1251 | 3.1539 | 3.1816 | 1167.2685 | 1327.4908 | 1446.9312 | 1561.4952 | 1671.7053 | 1774.447 | 1870.7102 | 1961.25 | 2044.7983 | 2122.019
48 | PMA | Southern | SBZ | Sandy Bay | low | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 1.3655 | 1.5686 | 1.8187 | 2.1206 | 2.4644 | 2.7698 | 3.0006 | 3.2197 | 3.4295 | 3.6232 | 3.8034 | 3.9717 | 4.1258 | 4.2671 | 4.4002 | 4.5229 | 4.6359 | 4.744 | 4.8484 | 4.9488 | 5.0447 | 5.1353 | 5.222 | 5.3049 | 5.3832 | 5.4581 | 5.5296 | 5.597 | 5.6612 | 5.722 | 5.7795 | 5.8339 | 5.8854 | 5.9344 | 5.9812 | 6.0261 | 6.069 | 2464.3623 | 2769.833 | 3000.6076 | 3219.6772 | 3429.4579 | 3623.2062 | 3803.3935 | 3971.6735 | 4125.7653 | 4267.1277
48 | PMA | Southern | SUZ | Summerleas Road | low | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.65883 | 0.75889 | 0.90746 | 1.0783 | 1.2585 | 1.4179 | 1.5485 | 1.6733 | 1.7932 | 1.9047 | 2.009 | 2.107 | 2.1973 | 2.2806 | 2.3594 | 2.4326 | 2.5003 | 2.5655 | 2.6289 | 2.6901 | 2.749 | 2.805 | 2.8588 | 2.9105 | 2.9597 | 3.007 | 3.0524 | 3.0955 | 3.1368 | 3.176 | 3.2134 | 3.249 | 3.2829 | 3.3152 | 3.3464 | 3.3763 | 3.4052 | 1258.5428 | 1417.8673 | 1548.5069 | 1673.3006 | 1793.2045 | 1904.72 | 2009.0342 | 2107.025 | 2197.2799 | 2280.5702
48 | PMA | Southern | TWY2 | Wayatinah | low | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | RT | 0.013722 | 0.015617 | 0.017888 | 0.020565 | 0.0029686 | 0.005667 | 0.0077019 | 0.0096394 | 0.011497 | 0.013219 | 0.014824 | 0.016326 | 0.017705 | 0.018973 | 0.02017 | 0.021277 | 0.022298 | 0.023278 | 0.024227 | 0.025141 | 0.026017 | 0.026846 | 0.027642 | 0.028404 | 0.029126 | 0.029819 | 0.030482 | 0.031108 | 0.031706 | 0.032274 | 0.032812 | 0.033323 | 0.033808 | 0.03427 | 0.034713 | 0.035139 | 0.035547 | 2.9686 | 5.667 | 7.7019 | 9.6394 | 11.4969 | 13.2188 | 14.8235 | 16.3259 | 17.7051 | 18.9735
48 | PMA | Southern | WHZ | West Hobart Zone | low | maximum | PV | non-coincident | POE50 | summer | zone | zone plus embedded | MW | 0 | Zs | 0.60518 | 0.69967 | 0.80934 | 0.93342 | 0.14371 | 0.27826 | 0.37966 | 0.47589 | 0.56804 | 0.65312 | 0.73224 | 0.80611 | 0.87374 | 0.93578 | 0.99415 | 1.048 | 1.0975 | 1.1449 | 1.1907 | 1.2347 | 1.2768 | 1.3165 | 1.3545 | 1.3908 | 1.425 | 1.4579 | 1.4891 | 1.5186 | 1.5467 | 1.5733 | 1.5985 | 1.6223 | 1.6448 | 1.6662 | 1.6867 | 1.7063 | 1.725 | 143.7146 | 278.2634 | 379.658 | 475.892 | 568.0367 | 653.121 | 732.236 | 806.1095 | 873.7421 | 935.7763
48 | PMA | Western | THZ | Trial Harbour | low | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.063729 | 0.070961 | 0.07986 | 0.097555 | 0.022922 | 0.037113 | 0.044654 | 0.051828 | 0.05869 | 0.065041 | 0.070949 | 0.076468 | 0.081525 | 0.086166 | 0.090536 | 0.09457 | 0.098284 | 0.10184 | 0.10528 | 0.10858 | 0.11174 | 0.11473 | 0.11759 | 0.12032 | 0.1229 | 0.12538 | 0.12774 | 0.12997 | 0.13209 | 0.1341 | 0.13601 | 0.13781 | 0.13952 | 0.14114 | 0.14269 | 0.14418 | 0.14561 | 22.9219 | 37.1133 | 44.6536 | 51.8283 | 58.6899 | 65.0408 | 70.9488 | 76.4677 | 81.5247 | 86.1658
48 | PMA | Western | RBZ | Rosebery 22 kV | low | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.1152 | 0.12955 | 0.14681 | 0.17669 | 0.038245 | 0.063314 | 0.07791 | 0.091782 | 0.10503 | 0.11726 | 0.12863 | 0.13922 | 0.14892 | 0.1578 | 0.16614 | 0.17384 | 0.18091 | 0.18766 | 0.19418 | 0.20044 | 0.20642 | 0.21206 | 0.21744 | 0.22259 | 0.22744 | 0.23208 | 0.2365 | 0.24067 | 0.24463 | 0.24838 | 0.25192 | 0.25527 | 0.25844 | 0.26144 | 0.26431 | 0.26706 | 0.26969 | 38.2451 | 63.3141 | 77.9097 | 91.7823 | 105.0266 | 117.2629 | 128.6268 | 139.2235 | 148.9168 | 157.7974
48 | PMA | total terminal |  | total terminal | low | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | #N/A | #N/A | 33.5903 | 38.9738 | 45.725 | 53.4868 | 61.9118 | 69.4632 | 75.7022 | 81.6506 | 87.349 | 92.6285 | 97.5498 | 102.1553 | 106.3826 | 110.2698 | 113.9367 | 117.3286 | 120.4564 | 123.4571 | 126.3635 | 129.1639 | 131.8473 | 134.3882 | 136.8256 | 139.1616 | 141.3726 | 143.4972 | 145.5269 | 147.4479 | 149.2812 | 151.0224 | 152.6743 | 154.2415 | 155.7299 | 157.149 | 158.5092 | 159.8159 | 161.0713 | 61911.7947 | 69463.2134 | 75702.2217 | 81650.5982 | 87349.0349 | 92628.4765 | 97549.8173 | 102155.2594 | 106382.6267 | 110269.7574
48 | PMA | total zone |  | total zone | low | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | #N/A | #N/A | 8.6354 | 9.8513 | 11.5677 | 13.6795 | 14.8408 | 16.9747 | 18.6042 | 20.1583 | 21.6505 | 23.0359 | 24.3297 | 25.543 | 26.6587 | 27.6867 | 28.6584 | 29.5589 | 30.3909 | 31.1905 | 31.9666 | 32.7156 | 33.4348 | 34.1169 | 34.7725 | 35.4019 | 35.9987 | 36.5732 | 37.123 | 37.6443 | 38.1426 | 38.6166 | 39.0671 | 39.4953 | 39.9025 | 40.2915 | 40.6649 | 41.0242 | 41.3699 | 14840.7687 | 16974.7407 | 18604.154 | 20158.3179 | 21650.5385 | 23035.9046 | 24329.7252 | 25542.9628 | 26658.7429 | 27686.7492
51 | PMA | George Town | TC01 | Comalco | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | Camalco | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | PMA | George Town | TSW1 | Starwood | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | Starwood | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | PMA | George Town | TTE1 | Temco | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | Temco | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | PMA | North | TAL2 | Ax-Arthurs Lake 6.6 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | Ax | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | PMA | North | TAV2 | Avoca 22 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.000201 | 0.00087061 | 0.0025237 | 0.004455 | 0.006268 | 0.0074334 | 0.0089862 | 0.011573 | 0.014676 | 0.020013 | 0.026264 | 0.033444 | 0.041714 | 0.051144 | 0.061755 | 0.073568 | 0.086606 | 0.1009 | 0.1163 | 0.1328 | 0.1504 | 0.16913 | 0.18858 | 0.20876 | 0.22967 | 0.25133 | 0.27376 | 0.29697 | 0.32098 | 0.34579 | 0.37118 | 0.39716 | 0.42374 | 0.201 | 0.87061 | 2.5237 | 4.455 | 6.268 | 7.4334 | 8.9862 | 11.5732 | 14.6757 | 20.0127
51 | PMA | North | TDE2 | Derby 22 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.00019719 | 0.00088401 | 0.0020498 | 0.0031278 | 0.004326 | 0.0050849 | 0.0060757 | 0.0074546 | 0.0090753 | 0.012162 | 0.015691 | 0.019661 | 0.02414 | 0.02915 | 0.034691 | 0.040759 | 0.047353 | 0.054472 | 0.06204 | 0.070032 | 0.078448 | 0.087288 | 0.096355 | 0.10565 | 0.11517 | 0.12491 | 0.13488 | 0.14507 | 0.15549 | 0.16613 | 0.17689 | 0.18778 | 0.19879 | 0.19719 | 0.88401 | 2.0498 | 3.1278 | 4.326 | 5.0849 | 6.0757 | 7.4546 | 9.0753 | 12.162
51 | PMA | North | THA3 | Hadspen 22 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.0018598 | 0.0079058 | 0.022474 | 0.037143 | 0.049048 | 0.058182 | 0.070316 | 0.08861 | 0.11102 | 0.15033 | 0.19614 | 0.24854 | 0.30866 | 0.37695 | 0.45353 | 0.53851 | 0.63204 | 0.73424 | 0.84413 | 0.96146 | 1.0864 | 1.219 | 1.3563 | 1.4984 | 1.6454 | 1.7973 | 1.9543 | 2.1163 | 2.2835 | 2.456 | 2.6321 | 2.8118 | 2.9953 | 1.8598 | 7.9058 | 22.4743 | 37.1426 | 49.0479 | 58.1817 | 70.3161 | 88.6102 | 111.0202 | 150.3256
51 | PMA | North | TMY2 | Mowbray 22 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.0010972 | 0.004176 | 0.011584 | 0.018279 | 0.022771 | 0.027234 | 0.033084 | 0.041295 | 0.050216 | 0.066478 | 0.085245 | 0.10652 | 0.13072 | 0.15799 | 0.18834 | 0.22178 | 0.25833 | 0.29801 | 0.34041 | 0.38541 | 0.43303 | 0.48328 | 0.53505 | 0.58832 | 0.64313 | 0.69946 | 0.75733 | 0.81675 | 0.87774 | 0.94029 | 1.0038 | 1.0683 | 1.1338 | 1.0972 | 4.176 | 11.5844 | 18.2787 | 22.771 | 27.2341 | 33.0839 | 41.2949 | 50.2156 | 66.478
51 | PMA | North | TPM3 | Palmerston 22 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 9.1428e-05 | 0.00040781 | 0.0011729 | 0.002031 | 0.002818 | 0.0033204 | 0.0039856 | 0.0051306 | 0.0066034 | 0.0090964 | 0.012026 | 0.015399 | 0.019294 | 0.023744 | 0.028761 | 0.034356 | 0.04054 | 0.047327 | 0.054653 | 0.062505 | 0.070893 | 0.079831 | 0.089118 | 0.098759 | 0.10876 | 0.11913 | 0.12988 | 0.14101 | 0.15253 | 0.16445 | 0.17665 | 0.18915 | 0.20194 | 0.091428 | 0.40781 | 1.1729 | 2.031 | 2.818 | 3.3204 | 3.9856 | 5.1306 | 6.6034 | 9.0964
51 | PMA | North | TSD2 | Scottsdale 22 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.00054538 | 0.0024061 | 0.0056207 | 0.0084588 | 0.011328 | 0.013305 | 0.01587 | 0.019479 | 0.023806 | 0.031961 | 0.041299 | 0.051816 | 0.063699 | 0.077007 | 0.091737 | 0.10788 | 0.12544 | 0.14441 | 0.16459 | 0.18591 | 0.20837 | 0.23198 | 0.2562 | 0.28104 | 0.30649 | 0.33256 | 0.35923 | 0.38652 | 0.41442 | 0.44293 | 0.47178 | 0.50097 | 0.53051 | 0.54538 | 2.4061 | 5.6207 | 8.4588 | 11.3276 | 13.3055 | 15.8695 | 19.4787 | 23.8062 | 31.9605
51 | PMA | North | TSL2 | St Leonards 22 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.0011844 | 0.0049277 | 0.013762 | 0.022008 | 0.027691 | 0.033017 | 0.040081 | 0.049801 | 0.060792 | 0.080823 | 0.10398 | 0.13028 | 0.16024 | 0.19407 | 0.23179 | 0.27344 | 0.31905 | 0.36866 | 0.42177 | 0.47825 | 0.53813 | 0.60144 | 0.66678 | 0.73416 | 0.8036 | 0.87512 | 0.94874 | 1.0245 | 1.1023 | 1.1824 | 1.2638 | 1.3467 | 1.431 | 1.1844 | 4.9277 | 13.762 | 22.0076 | 27.6913 | 33.0168 | 40.0809 | 49.801 | 60.7921 | 80.8226
51 | PMA | North | TSL3 | St Leonards 22 kV (scheduled load) | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | Firmus Grid | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | PMA | North | TSM2 | St Marys 22 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.00065645 | 0.0025778 | 0.0081009 | 0.014202 | 0.020584 | 0.024802 | 0.030942 | 0.038558 | 0.045454 | 0.058902 | 0.074316 | 0.09171 | 0.11141 | 0.13356 | 0.15816 | 0.18524 | 0.21483 | 0.24696 | 0.2813 | 0.31779 | 0.35644 | 0.39727 | 0.43941 | 0.48286 | 0.52763 | 0.57375 | 0.62121 | 0.67004 | 0.72026 | 0.77187 | 0.82441 | 0.87788 | 0.93229 | 0.65645 | 2.5778 | 8.1009 | 14.2024 | 20.584 | 24.802 | 30.9416 | 38.5579 | 45.4541 | 58.9015
51 | PMA | Northwest | TDP2 | Devonport 22 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.0023154 | 0.0066217 | 0.016139 | 0.025227 | 0.032174 | 0.039398 | 0.049696 | 0.063836 | 0.076809 | 0.10141 | 0.12972 | 0.16177 | 0.19818 | 0.23921 | 0.2849 | 0.33529 | 0.39044 | 0.45039 | 0.51458 | 0.58284 | 0.65523 | 0.7318 | 0.81086 | 0.89245 | 0.97659 | 1.0633 | 1.1526 | 1.2446 | 1.3392 | 1.4366 | 1.5357 | 1.6367 | 1.7395 | 2.3154 | 6.6217 | 16.1386 | 25.2267 | 32.1736 | 39.3984 | 49.696 | 63.8358 | 76.8094 | 101.4067
51 | PMA | Northwest | TEB2 | Emu Bay 11 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | Emu Bay | MI | 0 | 0 | 0 | 0 | 2.9362e-05 | 0.00013855 | 0.00030927 | 0.00049691 | 0.00066337 | 0.00080424 | 0.001022 | 0.0013487 | 0.0016004 | 0.0020779 | 0.0026235 | 0.0032368 | 0.0039283 | 0.0047012 | 0.0055551 | 0.0064893 | 0.0075034 | 0.008597 | 0.0097585 | 0.010984 | 0.012272 | 0.013624 | 0.01501 | 0.016428 | 0.017879 | 0.019362 | 0.020878 | 0.022426 | 0.024007 | 0.025619 | 0.027248 | 0.028894 | 0.030557 | 0.029362 | 0.13855 | 0.30927 | 0.49691 | 0.66337 | 0.80424 | 1.022 | 1.3487 | 1.6004 | 2.0779
51 | PMA | Northwest | THM2 | Hampshire | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | Hampshire | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | PMA | Northwest | TPL2 | Port Latta | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | Port Latta | MI | 0 | 0 | 0 | 0 | 0.00025066 | 0.0011659 | 0.0028408 | 0.0045179 | 0.0064475 | 0.0076943 | 0.0092675 | 0.011743 | 0.014389 | 0.019179 | 0.024698 | 0.030944 | 0.038034 | 0.046005 | 0.054857 | 0.064588 | 0.075199 | 0.086689 | 0.098937 | 0.1119 | 0.12559 | 0.14 | 0.1548 | 0.17 | 0.18559 | 0.20158 | 0.21797 | 0.23475 | 0.25194 | 0.26952 | 0.28733 | 0.30537 | 0.32365 | 0.25066 | 1.1659 | 2.8408 | 4.5179 | 6.4475 | 7.6943 | 9.2675 | 11.7427 | 14.3888 | 19.1789
51 | PMA | Northwest | TRA2 | Railton 22 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.0011415 | 0.004958 | 0.013841 | 0.023068 | 0.030213 | 0.036248 | 0.043816 | 0.055503 | 0.068715 | 0.092432 | 0.11999 | 0.15143 | 0.18743 | 0.22825 | 0.27397 | 0.32465 | 0.38038 | 0.44124 | 0.50666 | 0.57647 | 0.65077 | 0.72964 | 0.81132 | 0.89586 | 0.98329 | 1.0737 | 1.167 | 1.2634 | 1.3629 | 1.4656 | 1.5704 | 1.6775 | 1.7868 | 1.1415 | 4.958 | 13.8414 | 23.0676 | 30.2125 | 36.248 | 43.8165 | 55.5025 | 68.7146 | 92.4322
51 | PMA | Northwest | TSH3 | Sheffield | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | PMA | Northwest | TST2 | Smithton 22 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.00035907 | 0.0013368 | 0.0033721 | 0.0054407 | 0.0094549 | 0.011121 | 0.012971 | 0.016422 | 0.021526 | 0.029883 | 0.039622 | 0.050734 | 0.063433 | 0.077784 | 0.093779 | 0.1114 | 0.13065 | 0.15151 | 0.17375 | 0.19728 | 0.22211 | 0.24822 | 0.275 | 0.30246 | 0.33058 | 0.35937 | 0.38881 | 0.41892 | 0.44967 | 0.48108 | 0.51283 | 0.54493 | 0.57736 | 0.35907 | 1.3368 | 3.3721 | 5.4407 | 9.4549 | 11.1211 | 12.9708 | 16.4221 | 21.526 | 29.8826
51 | PMA | Northwest | TUL2 | Ulverstone 22 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.0010713 | 0.0056073 | 0.014092 | 0.022245 | 0.028676 | 0.035243 | 0.043322 | 0.055596 | 0.066713 | 0.087882 | 0.11216 | 0.13955 | 0.17057 | 0.20538 | 0.24401 | 0.28646 | 0.33275 | 0.3829 | 0.43639 | 0.49308 | 0.55298 | 0.61612 | 0.68109 | 0.7479 | 0.81655 | 0.88707 | 0.95945 | 1.0337 | 1.1098 | 1.1879 | 1.2671 | 1.3474 | 1.429 | 1.0713 | 5.6073 | 14.0921 | 22.2447 | 28.6758 | 35.2433 | 43.3221 | 55.5959 | 66.7129 | 87.8819
51 | PMA | Northwest | TWV2 | Wesley Vale 11 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | Wesley Vale | MI | 0 | 0 | 0 | 0 | 0.0003829 | 0.0021187 | 0.006023 | 0.0094732 | 0.012557 | 0.015685 | 0.019376 | 0.024453 | 0.029796 | 0.039554 | 0.050948 | 0.064024 | 0.079088 | 0.096285 | 0.11568 | 0.13734 | 0.16133 | 0.18773 | 0.21632 | 0.24707 | 0.28005 | 0.31532 | 0.35214 | 0.39053 | 0.43054 | 0.47222 | 0.51561 | 0.56076 | 0.60772 | 0.65654 | 0.70679 | 0.75849 | 0.81168 | 0.3829 | 2.1187 | 6.023 | 9.4732 | 12.5573 | 15.6847 | 19.3761 | 24.4531 | 29.7963 | 39.5538
51 | PMA | Southern | TBW2 | Bridgewater 11 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.00097473 | 0.0048569 | 0.012365 | 0.019986 | 0.026117 | 0.034585 | 0.043708 | 0.058256 | 0.070747 | 0.094348 | 0.12182 | 0.15329 | 0.18948 | 0.23077 | 0.27733 | 0.32935 | 0.387 | 0.45051 | 0.51937 | 0.59354 | 0.67323 | 0.75862 | 0.84791 | 0.94123 | 1.0387 | 1.1405 | 1.2466 | 1.3574 | 1.4729 | 1.5933 | 1.7175 | 1.8456 | 1.9778 | 0.97473 | 4.8569 | 12.3654 | 19.9862 | 26.1171 | 34.5846 | 43.7084 | 58.256 | 70.7473 | 94.3475
51 | PMA | Southern | TBYA | Boyer SWA | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | Boyer | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | PMA | Southern | TBYB | Boyer SWB | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | Boyer | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | PMA | Southern | TCR2 | Creek Rd 33 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.0044983 | 0.010337 | 0.023654 | 0.038628 | 0.048632 | 0.059529 | 0.073556 | 0.096134 | 0.11615 | 0.15437 | 0.19834 | 0.24811 | 0.30466 | 0.36837 | 0.43932 | 0.51759 | 0.60326 | 0.69644 | 0.79622 | 0.90237 | 1.015 | 1.1341 | 1.2572 | 1.3843 | 1.5154 | 1.6505 | 1.7898 | 1.9332 | 2.0809 | 2.2328 | 2.3876 | 2.5453 | 2.7059 | 4.4983 | 10.3369 | 23.6536 | 38.6276 | 48.6317 | 59.5286 | 73.5563 | 96.1344 | 116.1531 | 154.3729
51 | PMA | Southern | TCS3 | Chapel St 11 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.0022256 | 0.0049083 | 0.010358 | 0.0163 | 0.021472 | 0.026765 | 0.033441 | 0.044166 | 0.054424 | 0.073669 | 0.095851 | 0.12099 | 0.14959 | 0.18183 | 0.21777 | 0.25742 | 0.30083 | 0.34804 | 0.39861 | 0.45239 | 0.50943 | 0.56977 | 0.63207 | 0.69637 | 0.76267 | 0.83099 | 0.90137 | 0.97382 | 1.0484 | 1.125 | 1.2031 | 1.2826 | 1.3635 | 2.2256 | 4.9083 | 10.3581 | 16.2999 | 21.4721 | 26.7647 | 33.4408 | 44.1664 | 54.4243 | 73.6691
51 | PMA | Southern | TDB2 | Derwent Bridge 22 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0 | 0 | 0 | 0 | 1.3916e-06 | 8.4641e-06 | 1.9313e-05 | 3.2982e-05 | 4.177e-05 | 5.3573e-05 | 6.6506e-05 | 8.8316e-05 | 0.0001065 | 0.000141 | 0.00018079 | 0.00022594 | 0.00027737 | 0.00033546 | 0.0004003 | 0.000472 | 0.00055066 | 0.00063639 | 0.00072841 | 0.00082651 | 0.00093079 | 0.0010414 | 0.0011558 | 0.0012742 | 0.0013966 | 0.001523 | 0.0016535 | 0.0017882 | 0.0019272 | 0.0020704 | 0.0022166 | 0.0023659 | 0.0025182 | 0.0013916 | 0.0084641 | 0.019313 | 0.032982 | 0.04177 | 0.053573 | 0.066506 | 0.088316 | 0.1065 | 0.141
51 | PMA | Southern | TEL2 | Electrona 11 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.00059419 | 0.002953 | 0.0093858 | 0.016098 | 0.020489 | 0.025274 | 0.030605 | 0.039824 | 0.048225 | 0.064142 | 0.082565 | 0.10354 | 0.12753 | 0.15472 | 0.18519 | 0.21901 | 0.25625 | 0.29701 | 0.34091 | 0.38789 | 0.43802 | 0.49139 | 0.54682 | 0.60437 | 0.66407 | 0.72598 | 0.79013 | 0.85658 | 0.92538 | 0.99658 | 1.0695 | 1.1442 | 1.2208 | 0.59419 | 2.953 | 9.3858 | 16.0985 | 20.4886 | 25.2739 | 30.6049 | 39.8245 | 48.2252 | 64.1418
51 | PMA | Southern | THR2 | Huon River | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | Huon River | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | PMA | Southern | TK12 | Kingston 11 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.0010586 | 0.0055611 | 0.017948 | 0.030875 | 0.039339 | 0.048587 | 0.058797 | 0.076529 | 0.092729 | 0.1234 | 0.15891 | 0.19935 | 0.2456 | 0.29804 | 0.35681 | 0.42205 | 0.49391 | 0.57255 | 0.65728 | 0.74796 | 0.84474 | 0.94777 | 1.0548 | 1.1659 | 1.2812 | 1.4008 | 1.5247 | 1.6531 | 1.7861 | 1.9236 | 2.0646 | 2.209 | 2.357 | 1.0586 | 5.5611 | 17.9477 | 30.8749 | 39.3395 | 48.5866 | 58.797 | 76.5288 | 92.7292 | 123.3998
51 | PMA | Southern | TK13 | Kingston 33 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | PMA | Southern | TKE2 | Kermandie 11 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.00026623 | 0.0019548 | 0.0059286 | 0.0095236 | 0.011998 | 0.014314 | 0.01736 | 0.02228 | 0.026595 | 0.034892 | 0.044507 | 0.055477 | 0.068048 | 0.082335 | 0.098389 | 0.11626 | 0.13601 | 0.15769 | 0.18112 | 0.20628 | 0.23322 | 0.26199 | 0.29199 | 0.32325 | 0.35579 | 0.38965 | 0.42486 | 0.46147 | 0.49951 | 0.53902 | 0.57965 | 0.62142 | 0.66436 | 0.26623 | 1.9548 | 5.9286 | 9.5236 | 11.9981 | 14.3138 | 17.3604 | 22.2801 | 26.5954 | 34.8916
51 | PMA | Southern | TLF2 | Lindisfarne 33 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.00060384 | 0.0032151 | 0.010145 | 0.017084 | 0.022112 | 0.028636 | 0.036433 | 0.049652 | 0.060221 | 0.080244 | 0.10345 | 0.12992 | 0.16022 | 0.19462 | 0.23323 | 0.27614 | 0.32348 | 0.37535 | 0.43132 | 0.4913 | 0.5554 | 0.62373 | 0.69482 | 0.76873 | 0.84552 | 0.92527 | 1.008 | 1.0939 | 1.1829 | 1.2752 | 1.3698 | 1.4669 | 1.5665 | 0.60384 | 3.2151 | 10.1452 | 17.0839 | 22.1122 | 28.6359 | 36.4334 | 49.652 | 60.2209 | 80.244
51 | PMA | Southern | TMB2 | Meadowbank 22 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 9.1783e-05 | 0.00052005 | 0.0012381 | 0.0020719 | 0.0026589 | 0.0034518 | 0.0043159 | 0.0057362 | 0.0069368 | 0.0092098 | 0.011841 | 0.014838 | 0.018265 | 0.022151 | 0.026507 | 0.031344 | 0.036672 | 0.042505 | 0.048792 | 0.055523 | 0.06271 | 0.070365 | 0.078323 | 0.08659 | 0.095175 | 0.10408 | 0.11332 | 0.12291 | 0.13284 | 0.14312 | 0.15368 | 0.1645 | 0.1756 | 0.091783 | 0.52005 | 1.2381 | 2.0719 | 2.6589 | 3.4518 | 4.3159 | 5.7362 | 6.9368 | 9.2098
51 | PMA | Southern | TMT2 | Mornington 33 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.00069408 | 0.003689 | 0.011671 | 0.019664 | 0.025451 | 0.032945 | 0.041919 | 0.05714 | 0.069302 | 0.092344 | 0.11905 | 0.1495 | 0.18436 | 0.22393 | 0.26833 | 0.31769 | 0.37212 | 0.43177 | 0.49611 | 0.56506 | 0.63874 | 0.71728 | 0.79898 | 0.8839 | 0.97213 | 1.0637 | 1.1588 | 1.2574 | 1.3596 | 1.4656 | 1.5742 | 1.6857 | 1.8001 | 0.69408 | 3.689 | 11.6706 | 19.6642 | 25.4511 | 32.9453 | 41.9185 | 57.1396 | 69.3017 | 92.3436
51 | PMA | Southern | TNH2 | North Hobart 11 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.001801 | 0.0038426 | 0.008455 | 0.013804 | 0.017032 | 0.020634 | 0.025523 | 0.033244 | 0.039807 | 0.052472 | 0.067004 | 0.083413 | 0.10201 | 0.12292 | 0.14615 | 0.17173 | 0.19967 | 0.23 | 0.26242 | 0.29684 | 0.3333 | 0.37181 | 0.41152 | 0.45245 | 0.49461 | 0.538 | 0.58264 | 0.62853 | 0.6757 | 0.72416 | 0.77345 | 0.82357 | 0.87455 | 1.801 | 3.8426 | 8.455 | 13.8037 | 17.0316 | 20.6338 | 25.5229 | 33.2439 | 39.8067 | 52.472
51 | PMA | Southern | TNN2 | New Norfolk 22 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | Brynn Estyn | MI | 0 | 0 | 0 | 0 | 0.00038606 | 0.002327 | 0.0053372 | 0.0090907 | 0.011531 | 0.014813 | 0.018406 | 0.024445 | 0.029489 | 0.039055 | 0.050094 | 0.062626 | 0.076909 | 0.093048 | 0.11108 | 0.13102 | 0.15291 | 0.17679 | 0.20243 | 0.22978 | 0.25887 | 0.28974 | 0.32172 | 0.3548 | 0.38903 | 0.42441 | 0.46096 | 0.49871 | 0.53767 | 0.57787 | 0.61893 | 0.66087 | 0.7037 | 0.38606 | 2.327 | 5.3372 | 9.0907 | 11.5314 | 14.8132 | 18.4061 | 24.4452 | 29.4893 | 39.055
51 | PMA | Southern | TR13 | Risdon 11 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | Risdon | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | PMA | Southern | TR14 | Risdon 33 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.001519 | 0.003391 | 0.0073061 | 0.011632 | 0.015028 | 0.018644 | 0.023247 | 0.03061 | 0.037404 | 0.050244 | 0.065036 | 0.081796 | 0.10086 | 0.12235 | 0.1463 | 0.17273 | 0.20168 | 0.23318 | 0.26692 | 0.30282 | 0.34092 | 0.38124 | 0.4229 | 0.46591 | 0.51029 | 0.55606 | 0.60323 | 0.65182 | 0.70185 | 0.75333 | 0.8058 | 0.85926 | 0.91373 | 1.519 | 3.391 | 7.3061 | 11.632 | 15.0278 | 18.6442 | 23.2467 | 30.6098 | 37.4045 | 50.2442
51 | PMA | Southern | TRK2 | Rokeby 11 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.00050673 | 0.0026936 | 0.008522 | 0.014359 | 0.018585 | 0.024057 | 0.03061 | 0.041724 | 0.050605 | 0.067431 | 0.08693 | 0.10916 | 0.13462 | 0.16352 | 0.19594 | 0.23198 | 0.27173 | 0.31528 | 0.36227 | 0.41262 | 0.46642 | 0.52377 | 0.58343 | 0.64544 | 0.70986 | 0.77676 | 0.84617 | 0.91818 | 0.99282 | 1.0702 | 1.1495 | 1.2309 | 1.3144 | 0.50673 | 2.6936 | 8.522 | 14.3591 | 18.5848 | 24.0572 | 30.6096 | 41.7244 | 50.6054 | 67.4309
51 | PMA | Southern | TS02 | Sorell | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.0012214 | 0.0062844 | 0.016556 | 0.027662 | 0.03786 | 0.049063 | 0.06055 | 0.081046 | 0.09748 | 0.12888 | 0.16529 | 0.20685 | 0.25448 | 0.30862 | 0.36947 | 0.43721 | 0.51206 | 0.59423 | 0.68306 | 0.77844 | 0.88058 | 0.9897 | 1.1035 | 1.222 | 1.3454 | 1.4739 | 1.6075 | 1.7465 | 1.8909 | 2.041 | 2.1953 | 2.3541 | 2.5173 | 1.2214 | 6.2844 | 16.5563 | 27.662 | 37.8598 | 49.0625 | 60.5496 | 81.0457 | 97.48 | 128.8819
51 | PMA | Southern | TTB2 | Triabunna 22 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.00024756 | 0.0012493 | 0.0040799 | 0.0062763 | 0.009217 | 0.010972 | 0.014155 | 0.017614 | 0.020332 | 0.026004 | 0.032496 | 0.039827 | 0.048145 | 0.05752 | 0.067978 | 0.079547 | 0.092254 | 0.10613 | 0.12107 | 0.13704 | 0.15407 | 0.1722 | 0.19104 | 0.21061 | 0.23092 | 0.252 | 0.27386 | 0.29652 | 0.32001 | 0.34433 | 0.36928 | 0.39486 | 0.4211 | 0.24756 | 1.2493 | 4.0799 | 6.2763 | 9.217 | 10.9719 | 14.1546 | 17.6139 | 20.3319 | 26.0044
51 | PMA | Southern | TTU2 | Tungatinah 22 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0 | 0 | 0 | 0 | 1.957e-05 | 0.00011903 | 0.0002716 | 0.00046383 | 0.00058742 | 0.00075341 | 0.0009353 | 0.001242 | 0.0014978 | 0.0019829 | 0.0025425 | 0.0031775 | 0.0039008 | 0.0047177 | 0.0056296 | 0.0066379 | 0.0077441 | 0.0089499 | 0.010244 | 0.011624 | 0.01309 | 0.014645 | 0.016255 | 0.01792 | 0.019641 | 0.021419 | 0.023255 | 0.025149 | 0.027103 | 0.029118 | 0.031174 | 0.033273 | 0.035415 | 0.01957 | 0.11903 | 0.2716 | 0.46383 | 0.58742 | 0.75341 | 0.9353 | 1.242 | 1.4978 | 1.9829
51 | PMA | Southern | TWA2 | Waddamana 22 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0 | 0 | 0 | 0 | 6.9338e-05 | 0.00035532 | 0.00090348 | 0.0014634 | 0.0019146 | 0.0025347 | 0.0032026 | 0.0042629 | 0.005174 | 0.0068956 | 0.0088992 | 0.011194 | 0.013832 | 0.016841 | 0.020234 | 0.024023 | 0.028222 | 0.032846 | 0.037859 | 0.043258 | 0.049056 | 0.055269 | 0.061765 | 0.068552 | 0.07564 | 0.083039 | 0.090759 | 0.09881 | 0.1072 | 0.11595 | 0.12498 | 0.13429 | 0.14389 | 0.069338 | 0.35532 | 0.90348 | 1.4634 | 1.9146 | 2.5347 | 3.2026 | 4.2629 | 5.174 | 6.8956
51 | PMA | Western | TGO2 | Gordon | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0 | 0 | 0 | 0 | 1.3832e-06 | 8.4839e-06 | 1.9242e-05 | 3.3045e-05 | 4.1739e-05 | 5.3462e-05 | 6.6315e-05 | 8.8611e-05 | 0.00010827 | 0.0001447 | 0.00018687 | 0.00023486 | 0.00028966 | 0.0003517 | 0.00042109 | 0.00049793 | 0.00058236 | 0.00067452 | 0.00077353 | 0.00087918 | 0.00099161 | 0.0011109 | 0.0012345 | 0.0013624 | 0.0014947 | 0.0016315 | 0.0017728 | 0.0019187 | 0.0020693 | 0.0022246 | 0.0023833 | 0.0025453 | 0.0027107 | 0.0013832 | 0.0084839 | 0.019242 | 0.033045 | 0.041739 | 0.053462 | 0.066315 | 0.088611 | 0.10827 | 0.1447
51 | PMA | Western | TNT2 | Newton 22 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | PMA | Western | TNT3 | Ax-Newton 11 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | Ax | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | PMA | Western | TQT2 | Queenstown 22 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0 | 0 | 0 | 0 | 9.1654e-05 | 0.0002361 | 0.00049056 | 0.001174 | 0.0016275 | 0.0021261 | 0.0034223 | 0.0048952 | 0.0055722 | 0.0070423 | 0.0087091 | 0.010575 | 0.012674 | 0.01502 | 0.017616 | 0.020467 | 0.023575 | 0.026945 | 0.030548 | 0.034376 | 0.038432 | 0.04272 | 0.047151 | 0.051727 | 0.056449 | 0.06132 | 0.066341 | 0.071516 | 0.076846 | 0.082334 | 0.08793 | 0.093637 | 0.099455 | 0.091654 | 0.2361 | 0.49056 | 1.174 | 1.6275 | 2.1261 | 3.4223 | 4.8952 | 5.5722 | 7.0423
51 | PMA | Western | TQT3 | Queenstown 11 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | Queenstown 11 kV | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | PMA | Western | TQU2 | Que | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | Que | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | PMA | Western | TRB2 | Rosebery 44 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | Rosebery | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | PMA | Western | TSR2 | Savage River | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | Savage River | MI | 0 | 0 | 0 | 0 | 1.9607e-05 | 9.1384e-05 | 0.0002155 | 0.00034516 | 0.00047973 | 0.00057629 | 0.00071016 | 0.00091455 | 0.0011053 | 0.0014575 | 0.0018621 | 0.0023187 | 0.0028358 | 0.0034159 | 0.0040591 | 0.004765 | 0.0055335 | 0.0063647 | 0.0072497 | 0.0081855 | 0.0091724 | 0.01021 | 0.011276 | 0.012369 | 0.01349 | 0.014638 | 0.015814 | 0.017018 | 0.018249 | 0.019508 | 0.020782 | 0.022073 | 0.023378 | 0.019607 | 0.091384 | 0.2155 | 0.34516 | 0.47973 | 0.57629 | 0.71016 | 0.91455 | 1.1053 | 1.4575
51 | PMA | Southern | BEZ | Bellerive | low | maximum | Battery | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0 | 0 | 0 | 0 | 0 | 0.0011522 | 0.0036454 | 0.0061422 | 0.0079498 | 0.010291 | 0.013093 | 0.017848 | 0.021647 | 0.028844 | 0.037185 | 0.046696 | 0.057584 | 0.069945 | 0.083815 | 0.099232 | 0.11623 | 0.13486 | 0.15496 | 0.1765 | 0.19951 | 0.22405 | 0.24956 | 0.27609 | 0.30365 | 0.33226 | 0.36196 | 0.39276 | 0.42469 | 0.45777 | 0.49172 | 0.52654 | 0.56226 | 0 | 1.1522 | 3.6454 | 6.1422 | 7.9498 | 10.2906 | 13.0935 | 17.8479 | 21.6468 | 28.844
51 | PMA | Southern | CLZ | Claremont | low | maximum | Battery | non-coincident | POE50 | summer | zone | zone plus embedded | MW | 0 | Zs | 0 | 0 | 0 | 0 | 0 | 0.0023733 | 0.0049983 | 0.007835 | 0.010398 | 0.013014 | 0.016281 | 0.021537 | 0.026611 | 0.036107 | 0.047058 | 0.059477 | 0.073609 | 0.089552 | 0.10733 | 0.12695 | 0.14844 | 0.17182 | 0.19687 | 0.22352 | 0.2518 | 0.28173 | 0.31264 | 0.34455 | 0.37746 | 0.4114 | 0.44636 | 0.48237 | 0.51943 | 0.55756 | 0.5964 | 0.63596 | 0.67625 | 0 | 2.3733 | 4.9983 | 7.835 | 10.3982 | 13.0143 | 16.2813 | 21.5374 | 26.611 | 36.1069
51 | PMA | Southern | DPZ | Derwent Park | low | maximum | Battery | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0 | 0 | 0 | 0 | 0 | 0.00089199 | 0.0019393 | 0.0030523 | 0.0040367 | 0.0051053 | 0.0064002 | 0.008486 | 0.010455 | 0.014146 | 0.018411 | 0.023257 | 0.028783 | 0.035031 | 0.042012 | 0.049738 | 0.05822 | 0.067472 | 0.077408 | 0.088008 | 0.099283 | 0.11125 | 0.12364 | 0.13646 | 0.14972 | 0.16344 | 0.1776 | 0.19224 | 0.20734 | 0.22293 | 0.23885 | 0.25511 | 0.27173 | 0 | 0.89199 | 1.9393 | 3.0523 | 4.0367 | 5.1053 | 6.4002 | 8.486 | 10.4551 | 14.1463
51 | PMA | Southern | EHZ | East Hobart | low | maximum | Battery | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0 | 0 | 0 | 0 | 0 | 0.00024612 | 0.00054165 | 0.00088445 | 0.0010909 | 0.0013215 | 0.0016345 | 0.0021288 | 0.0025487 | 0.0033592 | 0.004289 | 0.005339 | 0.006529 | 0.0078667 | 0.0093532 | 0.01099 | 0.012777 | 0.014718 | 0.016792 | 0.018995 | 0.021327 | 0.023791 | 0.026332 | 0.02895 | 0.031647 | 0.034423 | 0.037279 | 0.040215 | 0.043233 | 0.046333 | 0.049486 | 0.052693 | 0.055954 | 0 | 0.24612 | 0.54165 | 0.88445 | 1.0909 | 1.3215 | 1.6345 | 2.1288 | 2.5487 | 3.3592
51 | PMA | Southern | GBZ | Geilston Bay | low | maximum | Battery | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0 | 0 | 0 | 0 | 0 | 0.0017655 | 0.005559 | 0.0093564 | 0.012111 | 0.015689 | 0.019961 | 0.027198 | 0.032987 | 0.043955 | 0.056669 | 0.071168 | 0.08777 | 0.10662 | 0.12778 | 0.1513 | 0.17724 | 0.20568 | 0.23636 | 0.26924 | 0.30439 | 0.34186 | 0.38085 | 0.42138 | 0.4635 | 0.50725 | 0.55265 | 0.59976 | 0.6486 | 0.69923 | 0.75118 | 0.80449 | 0.85917 | 0 | 1.7655 | 5.559 | 9.3564 | 12.1106 | 15.6893 | 19.9605 | 27.1976 | 32.9872 | 43.9554
51 | PMA | Southern | GRZ | Gretna | low | maximum | Battery | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0 | 0 | 0 | 0 | 0 | 4.6565e-05 | 0.00010625 | 0.00018145 | 0.0002298 | 0.00029473 | 0.00036588 | 0.00048587 | 0.00058593 | 0.00077572 | 0.00099464 | 0.001243 | 0.001526 | 0.0018456 | 0.0022023 | 0.0025968 | 0.0030295 | 0.0035012 | 0.0040075 | 0.0045472 | 0.0051209 | 0.0057293 | 0.006359 | 0.0070103 | 0.0076836 | 0.0083791 | 0.0090973 | 0.0098384 | 0.010603 | 0.011391 | 0.012195 | 0.013017 | 0.013855 | 0 | 0.046565 | 0.10625 | 0.18145 | 0.2298 | 0.29473 | 0.36588 | 0.48587 | 0.58593 | 0.77572
51 | PMA | Southern | HOZ | Howrah | low | maximum | Battery | non-coincident | POE50 | summer | zone | zone plus embedded | MW | 0 | Zs | 0 | 0 | 0 | 0 | 0 | 0.0020148 | 0.0063739 | 0.010739 | 0.0139 | 0.017993 | 0.022893 | 0.031206 | 0.037849 | 0.050433 | 0.065017 | 0.081646 | 0.10068 | 0.1223 | 0.14655 | 0.1735 | 0.20323 | 0.23581 | 0.27095 | 0.3086 | 0.34884 | 0.39174 | 0.43635 | 0.48274 | 0.53092 | 0.58095 | 0.63287 | 0.68672 | 0.74255 | 0.8004 | 0.85976 | 0.92064 | 0.98309 | 0 | 2.0148 | 6.3739 | 10.7395 | 13.9 | 17.9929 | 22.8935 | 31.2063 | 37.8486 | 50.4328
51 | PMA | Southern | NTZ | New Town | low | maximum | Battery | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0 | 0 | 0 | 0 | 0 | 0.0022529 | 0.0048252 | 0.0076953 | 0.0099002 | 0.012217 | 0.015212 | 0.019995 | 0.024401 | 0.032739 | 0.042336 | 0.0532 | 0.065545 | 0.07945 | 0.094933 | 0.11201 | 0.13068 | 0.15099 | 0.17272 | 0.19582 | 0.22031 | 0.2462 | 0.27293 | 0.3005 | 0.32892 | 0.3582 | 0.38835 | 0.41937 | 0.45127 | 0.48408 | 0.51747 | 0.55146 | 0.58604 | 0 | 2.2529 | 4.8252 | 7.6953 | 9.9002 | 12.2174 | 15.2119 | 19.995 | 24.4006 | 32.7388
51 | PMA | Southern | RIZ | Richmond | low | maximum | Battery | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0 | 0 | 0 | 0 | 0 | 0.00049651 | 0.0013642 | 0.002303 | 0.0030612 | 0.0039301 | 0.0049726 | 0.0066361 | 0.0081129 | 0.010862 | 0.014044 | 0.017665 | 0.021803 | 0.026489 | 0.031734 | 0.037548 | 0.04394 | 0.050924 | 0.058437 | 0.066462 | 0.075013 | 0.084101 | 0.093526 | 0.1033 | 0.11342 | 0.1239 | 0.13474 | 0.14596 | 0.15756 | 0.16956 | 0.18183 | 0.19439 | 0.20724 | 0 | 0.49651 | 1.3642 | 2.303 | 3.0612 | 3.9301 | 4.9726 | 6.6361 | 8.1129 | 10.8616
51 | PMA | Southern | RPZ | Rosny Park | low | maximum | Battery | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0 | 0 | 0 | 0 | 0 | 0.001236 | 0.0039104 | 0.0065887 | 0.0085277 | 0.011039 | 0.014045 | 0.019145 | 0.02322 | 0.030941 | 0.039888 | 0.050091 | 0.06177 | 0.07503 | 0.089909 | 0.10645 | 0.12468 | 0.14467 | 0.16623 | 0.18933 | 0.21402 | 0.24033 | 0.26771 | 0.29616 | 0.32572 | 0.35642 | 0.38827 | 0.42131 | 0.45556 | 0.49105 | 0.52747 | 0.56482 | 0.60313 | 0 | 1.236 | 3.9104 | 6.5887 | 8.5277 | 11.0387 | 14.0453 | 19.1454 | 23.2205 | 30.9409
51 | PMA | Southern | SBZ | Sandy Bay | low | maximum | Battery | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0 | 0 | 0 | 0 | 0 | 0.0043081 | 0.010311 | 0.017079 | 0.021252 | 0.025891 | 0.031834 | 0.041462 | 0.049811 | 0.065834 | 0.084264 | 0.10513 | 0.12883 | 0.15554 | 0.18529 | 0.21812 | 0.25407 | 0.29318 | 0.33509 | 0.37969 | 0.42702 | 0.47714 | 0.52893 | 0.58242 | 0.63764 | 0.6946 | 0.75333 | 0.81386 | 0.8762 | 0.94038 | 1.0058 | 1.0725 | 1.1405 | 0 | 4.3081 | 10.3108 | 17.0793 | 21.2519 | 25.8907 | 31.8343 | 41.4623 | 49.8106 | 65.834
51 | PMA | Southern | SUZ | Summerleas Road | low | maximum | Battery | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0 | 0 | 0 | 0 | 0 | 0.0013928 | 0.0045151 | 0.007797 | 0.009941 | 0.0123 | 0.014883 | 0.019384 | 0.023506 | 0.031302 | 0.040328 | 0.050608 | 0.062362 | 0.075688 | 0.090622 | 0.1072 | 0.12545 | 0.14543 | 0.16695 | 0.18998 | 0.21455 | 0.2407 | 0.26787 | 0.29607 | 0.32533 | 0.35567 | 0.3871 | 0.41966 | 0.45337 | 0.48825 | 0.52399 | 0.56059 | 0.59808 | 0 | 1.3928 | 4.5151 | 7.797 | 9.941 | 12.2999 | 14.8825 | 19.3843 | 23.5056 | 31.3022
51 | PMA | Southern | TWY2 | Wayatinah | low | maximum | Battery | non-coincident | POE50 | summer | zone | zone | MW | 0 | RT | 0 | 0 | 0 | 0 | 4.5648e-06 | 2.7764e-05 | 6.3353e-05 | 0.00010819 | 0.00013702 | 0.00017574 | 0.00021817 | 0.00028971 | 0.00034936 | 0.00046252 | 0.00059304 | 0.00074114 | 0.00090984 | 0.0011004 | 0.0013131 | 0.0015482 | 0.0018062 | 0.0020875 | 0.0023893 | 0.0027111 | 0.0030532 | 0.0034159 | 0.0037913 | 0.0041796 | 0.004581 | 0.0049957 | 0.0054239 | 0.0058658 | 0.0063215 | 0.0067914 | 0.0072711 | 0.0077607 | 0.0082603 | 0.0045648 | 0.027764 | 0.063353 | 0.10819 | 0.13702 | 0.17574 | 0.21817 | 0.28971 | 0.34936 | 0.46252
51 | PMA | Southern | WHZ | West Hobart Zone | low | maximum | Battery | non-coincident | POE50 | summer | zone | zone plus embedded | MW | 0 | Zs | 0 | 0 | 0 | 0 | 0 | 0.0036555 | 0.0083445 | 0.013713 | 0.016982 | 0.020624 | 0.025441 | 0.033135 | 0.039731 | 0.052432 | 0.06702 | 0.083511 | 0.10222 | 0.12328 | 0.14671 | 0.17252 | 0.20075 | 0.23143 | 0.26426 | 0.29916 | 0.33615 | 0.37527 | 0.41565 | 0.4573 | 0.50025 | 0.5445 | 0.59008 | 0.63698 | 0.68524 | 0.73486 | 0.78539 | 0.83683 | 0.8892 | 0 | 3.6555 | 8.3445 | 13.7133 | 16.9817 | 20.6236 | 25.4407 | 33.1346 | 39.7314 | 52.4319
51 | PMA | Western | THZ | Trial Harbour | low | maximum | Battery | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0 | 0 | 0 | 0 | 0 | 7.7555e-05 | 0.00016114 | 0.00038565 | 0.00053461 | 0.0006984 | 0.0011241 | 0.001608 | 0.0018304 | 0.0023132 | 0.0028607 | 0.0034737 | 0.0041631 | 0.0049337 | 0.0057865 | 0.0067229 | 0.0077439 | 0.008851 | 0.010035 | 0.011292 | 0.012624 | 0.014033 | 0.015488 | 0.016991 | 0.018542 | 0.020142 | 0.021792 | 0.023491 | 0.025242 | 0.027045 | 0.028883 | 0.030758 | 0.032669 | 0 | 0.077555 | 0.16114 | 0.38565 | 0.53461 | 0.6984 | 1.1241 | 1.608 | 1.8304 | 2.3132
51 | PMA | Western | RBZ | Rosebery 22 kV | low | maximum | Battery | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0 | 0 | 0 | 0 | 8.151e-05 | 0.00024647 | 0.00053498 | 0.001128 | 0.0015649 | 0.0019993 | 0.0030239 | 0.004235 | 0.0048781 | 0.0062191 | 0.0077443 | 0.0094551 | 0.011382 | 0.013539 | 0.015926 | 0.018547 | 0.021404 | 0.0245 | 0.027806 | 0.031314 | 0.035028 | 0.038949 | 0.042995 | 0.047166 | 0.051464 | 0.055891 | 0.060448 | 0.065136 | 0.069957 | 0.074914 | 0.07996 | 0.085097 | 0.090326 | 0.08151 | 0.24647 | 0.53498 | 1.128 | 1.5649 | 1.9993 | 3.0239 | 4.235 | 4.8781 | 6.2191
51 | PMA | total terminal |  | total terminal | low | maximum | Battery | non-coincident | POE50 | summer | zone | zone | MW | #N/A | #N/A | 0 | 0 | 0 | 0 | 0.034477 | 0.13522 | 0.36171 | 0.59079 | 0.76773 | 0.94034 | 1.1577 | 1.4909 | 1.8097 | 2.405 | 3.0931 | 3.8754 | 4.768 | 5.7775 | 6.9058 | 8.1548 | 9.5264 | 11.023 | 12.6305 | 14.3456 | 16.1703 | 18.1068 | 20.1126 | 22.1887 | 24.3364 | 26.5569 | 28.8515 | 31.2214 | 33.6681 | 36.1928 | 38.7725 | 41.408 | 44.1002 | 34.4766 | 135.2206 | 361.7143 | 590.7933 | 767.7301 | 940.3353 | 1157.7341 | 1490.9417 | 1809.7196 | 2404.9827
51 | PMA | total zone |  | total zone | low | maximum | Battery | non-coincident | POE50 | summer | zone | zone | MW | #N/A | #N/A | 0 | 0 | 0 | 0 | 8.6075e-05 | 0.02292 | 0.059521 | 0.098911 | 0.12669 | 0.15915 | 0.19974 | 0.26617 | 0.32234 | 0.42914 | 0.55244 | 0.69251 | 0.85224 | 1.0329 | 1.2348 | 1.4583 | 1.7039 | 1.972 | 2.2602 | 2.5679 | 2.8954 | 3.2433 | 3.6039 | 3.9775 | 4.3643 | 4.7645 | 5.1784 | 5.6063 | 6.0483 | 6.5048 | 6.9716 | 7.4488 | 7.9367 | 0.086075 | 22.9196 | 59.5206 | 98.9109 | 126.6913 | 159.1522 | 199.742 | 266.1748 | 322.3423 | 429.1391
48 | PMA | George Town | TGT3 | George Town 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0.078266 | 0.089154 | 0.10375 | 0.12051 | 0.1365 | 0.15152 | 0.16575 | 0.17918 | 0.19212 | 0.20409 | 0.21525 | 0.22571 | 0.2353 | 0.24412 | 0.25245 | 0.26015 | 0.26726 | 0.27407 | 0.28068 | 0.28704 | 0.29313 | 0.29891 | 0.30444 | 0.30975 | 0.31477 | 0.31959 | 0.3242 | 0.32855 | 0.33271 | 0.33666 | 0.3404 | 0.34395 | 0.34732 | 0.35054 | 0.35361 | 0.35657 | 0.3594 | 136.5015 | 151.5159 | 165.7462 | 179.1831 | 192.1189 | 204.0912 | 215.2525 | 225.706 | 235.2999 | 244.125
48 | PMA | North | TNW2 | Norwood 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0.89761 | 1.0512 | 1.2232 | 1.4231 | 1.6318 | 1.8109 | 1.9756 | 2.132 | 2.2812 | 2.4189 | 2.5467 | 2.6658 | 2.7747 | 2.8744 | 2.9681 | 3.0544 | 3.1336 | 3.2093 | 3.2823 | 3.3524 | 3.4192 | 3.4823 | 3.5425 | 3.5999 | 3.6541 | 3.7059 | 3.7552 | 3.8016 | 3.8457 | 3.8874 | 3.9268 | 3.964 | 3.9992 | 4.0326 | 4.0644 | 4.0949 | 4.1241 | 1631.8478 | 1810.9378 | 1975.5555 | 2131.9918 | 2281.2469 | 2418.8879 | 2546.6736 | 2665.787 | 2774.6763 | 2874.3881
48 | PMA | North | TTR2 | Trevallyn 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 1.8699 | 2.188 | 2.5558 | 2.9926 | 3.4526 | 3.8708 | 4.2615 | 4.6326 | 4.9873 | 5.3153 | 5.6203 | 5.9051 | 6.166 | 6.4054 | 6.6307 | 6.8386 | 7.03 | 7.2131 | 7.39 | 7.5601 | 7.7227 | 7.8764 | 8.0233 | 8.1639 | 8.2966 | 8.4238 | 8.5449 | 8.6594 | 8.7683 | 8.8714 | 8.9691 | 9.0614 | 9.1489 | 9.2321 | 9.3116 | 9.3878 | 9.4608 | 3452.6345 | 3870.7926 | 4261.5278 | 4632.6151 | 4987.3204 | 5315.3177 | 5620.2699 | 5905.1422 | 6166.0336 | 6405.3899
48 | PMA | Northwest | TBU3 | Burnie 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0.94235 | 1.0982 | 1.277 | 1.4722 | 1.6825 | 1.863 | 2.0037 | 2.1363 | 2.2628 | 2.379 | 2.4864 | 2.5861 | 2.677 | 2.7598 | 2.8374 | 2.9085 | 2.9736 | 3.0355 | 3.0951 | 3.1519 | 3.206 | 3.2568 | 3.3051 | 3.351 | 3.3941 | 3.4352 | 3.4741 | 3.5106 | 3.5452 | 3.5777 | 3.6084 | 3.6372 | 3.6643 | 3.69 | 3.7144 | 3.7376 | 3.7597 | 1682.5056 | 1862.9759 | 2003.7295 | 2136.33 | 2262.8173 | 2378.9627 | 2486.3559 | 2586.1192 | 2676.9508 | 2759.8075
48 | PMA | Southern | TKR2 | Knights Rd 11 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0.059251 | 0.068351 | 0.079726 | 0.092454 | 0.10628 | 0.11915 | 0.12942 | 0.1393 | 0.14884 | 0.15775 | 0.16612 | 0.17401 | 0.1813 | 0.18806 | 0.19448 | 0.20047 | 0.20603 | 0.2114 | 0.21664 | 0.22172 | 0.22663 | 0.23131 | 0.23583 | 0.24019 | 0.24435 | 0.24837 | 0.25224 | 0.25593 | 0.25947 | 0.26286 | 0.26609 | 0.26918 | 0.27214 | 0.27497 | 0.27771 | 0.28035 | 0.28291 | 106.283 | 119.1528 | 129.4229 | 139.2966 | 148.8434 | 157.7501 | 166.1198 | 174.0091 | 181.3041 | 188.0626
48 | PMA | Southern | CAZ | Cambridge | low | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.21308 | 0.24943 | 0.29203 | 0.34484 | 0.41211 | 0.47245 | 0.51749 | 0.56069 | 0.60225 | 0.641 | 0.6773 | 0.71145 | 0.74295 | 0.77208 | 0.79969 | 0.82537 | 0.84916 | 0.87211 | 0.89444 | 0.91607 | 0.93689 | 0.95671 | 0.97581 | 0.9942 | 1.0117 | 1.0286 | 1.0448 | 1.0602 | 1.075 | 1.0891 | 1.1025 | 1.1153 | 1.1275 | 1.1392 | 1.1505 | 1.1614 | 1.1718 | 412.1061 | 472.452 | 517.4937 | 560.6932 | 602.2526 | 640.9977 | 677.3 | 711.4454 | 742.9549 | 772.0788
51 | PMA | George Town | TGT3 | George Town 22 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.0009099 | 0.0044324 | 0.012593 | 0.021025 | 0.026243 | 0.03106 | 0.037971 | 0.046023 | 0.055418 | 0.073018 | 0.093359 | 0.11648 | 0.14286 | 0.17269 | 0.20603 | 0.24293 | 0.28345 | 0.32765 | 0.37513 | 0.42578 | 0.47966 | 0.53683 | 0.59603 | 0.6573 | 0.72066 | 0.78614 | 0.85379 | 0.92364 | 0.99571 | 1.0701 | 1.146 | 1.2235 | 1.3027 | 0.9099 | 4.4324 | 12.5925 | 21.0254 | 26.2426 | 31.0601 | 37.9708 | 46.0232 | 55.4179 | 73.0176
51 | PMA | North | TNW2 | Norwood 22 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.00094259 | 0.003717 | 0.010365 | 0.016625 | 0.021098 | 0.025155 | 0.030488 | 0.03825 | 0.047002 | 0.062706 | 0.080902 | 0.10161 | 0.12523 | 0.15195 | 0.18177 | 0.21473 | 0.25085 | 0.29017 | 0.3323 | 0.37712 | 0.42467 | 0.47498 | 0.52691 | 0.58049 | 0.63573 | 0.69264 | 0.75125 | 0.81157 | 0.87362 | 0.93741 | 1.0024 | 1.0685 | 1.1357 | 0.94259 | 3.717 | 10.3646 | 16.6253 | 21.0978 | 25.1548 | 30.4879 | 38.2497 | 47.0018 | 62.7064
51 | PMA | North | TTR2 | Trevallyn 22 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.0022056 | 0.010438 | 0.029156 | 0.047279 | 0.059407 | 0.070591 | 0.085645 | 0.10577 | 0.12889 | 0.17135 | 0.22046 | 0.27628 | 0.33995 | 0.41192 | 0.49228 | 0.58112 | 0.67856 | 0.78471 | 0.89854 | 1.0198 | 1.1485 | 1.2849 | 1.4259 | 1.5715 | 1.7218 | 1.8769 | 2.0368 | 2.2016 | 2.3714 | 2.5461 | 2.7243 | 2.9059 | 3.0909 | 2.2056 | 10.4379 | 29.1556 | 47.2788 | 59.4072 | 70.591 | 85.6446 | 105.7715 | 128.8874 | 171.3465
51 | PMA | Northwest | TBU3 | Burnie 22 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.0016276 | 0.0081703 | 0.019413 | 0.030762 | 0.040608 | 0.048961 | 0.060283 | 0.077183 | 0.091835 | 0.11995 | 0.15211 | 0.18833 | 0.22924 | 0.27508 | 0.32584 | 0.38151 | 0.44211 | 0.50764 | 0.57744 | 0.65128 | 0.72918 | 0.81115 | 0.89539 | 0.98188 | 1.0706 | 1.1617 | 1.255 | 1.3506 | 1.4485 | 1.5486 | 1.6502 | 1.753 | 1.8573 | 1.6276 | 8.1703 | 19.4126 | 30.7622 | 40.6082 | 48.9608 | 60.2829 | 77.1833 | 91.8351 | 119.9471
51 | PMA | Southern | TKR2 | Knights Rd 11 kV | low | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.00051591 | 0.0037584 | 0.011414 | 0.018363 | 0.023141 | 0.02763 | 0.033509 | 0.04302 | 0.051371 | 0.067419 | 0.086019 | 0.10724 | 0.13155 | 0.15919 | 0.19024 | 0.2248 | 0.26298 | 0.30489 | 0.35019 | 0.39883 | 0.45091 | 0.50653 | 0.56451 | 0.62491 | 0.68779 | 0.75322 | 0.82126 | 0.89198 | 0.96546 | 1.0418 | 1.1202 | 1.2009 | 1.2838 | 0.51591 | 3.7584 | 11.4139 | 18.3634 | 23.1408 | 27.63 | 33.509 | 43.0196 | 51.3709 | 67.4195
51 | PMA | Southern | CAZ | Cambridge | low | maximum | Battery | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0 | 0 | 0 | 0 | 0 | 0.00073559 | 0.0023272 | 0.0039213 | 0.0050752 | 0.0065697 | 0.008359 | 0.011394 | 0.01382 | 0.018414 | 0.023739 | 0.029811 | 0.036762 | 0.044654 | 0.053509 | 0.063351 | 0.074205 | 0.086099 | 0.09893 | 0.11268 | 0.12737 | 0.14303 | 0.15932 | 0.17626 | 0.19385 | 0.21212 | 0.23108 | 0.25074 | 0.27113 | 0.29225 | 0.31392 | 0.33615 | 0.35895 | 0 | 0.73559 | 2.3272 | 3.9213 | 5.0752 | 6.5697 | 8.359 | 11.3943 | 13.8196 | 18.4144
48 | PMA | George Town | TGT3 | George Town 22 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0.078266 | 0.089154 | 0.10375 | 0.12051 | 0.13662 | 0.15214 | 0.16731 | 0.18198 | 0.19636 | 0.20993 | 0.22284 | 0.23517 | 0.24693 | 0.25817 | 0.269 | 0.27975 | 0.29072 | 0.30175 | 0.31254 | 0.32303 | 0.33319 | 0.34293 | 0.35241 | 0.36164 | 0.37054 | 0.37928 | 0.38783 | 0.39613 | 0.40429 | 0.41232 | 0.4202 | 0.42793 | 0.43553 | 0.44301 | 0.45037 | 0.45761 | 0.46472 | 136.6215 | 152.1445 | 167.3131 | 181.9791 | 196.3551 | 209.926 | 222.8364 | 235.1733 | 246.9252 | 258.1691
48 | PMA | North | TNW2 | Norwood 22 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0.89761 | 1.0512 | 1.2232 | 1.4231 | 1.6332 | 1.8182 | 1.9937 | 2.1644 | 2.3303 | 2.4863 | 2.6341 | 2.7747 | 2.908 | 3.0351 | 3.1569 | 3.2773 | 3.3997 | 3.5222 | 3.6415 | 3.7571 | 3.8684 | 3.9748 | 4.078 | 4.1779 | 4.2738 | 4.3678 | 4.4592 | 4.5476 | 4.6342 | 4.719 | 4.8019 | 4.883 | 4.9623 | 5.04 | 5.1162 | 5.1908 | 5.264 | 1633.2376 | 1818.1748 | 1993.6828 | 2164.4032 | 2330.2653 | 2486.2815 | 2634.083 | 2774.6516 | 2908.0213 | 3035.0574
48 | PMA | North | TTR2 | Trevallyn 22 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 1.8699 | 2.188 | 2.5558 | 2.9926 | 3.4559 | 3.8879 | 4.3045 | 4.7095 | 5.1037 | 5.4755 | 5.8282 | 6.1644 | 6.484 | 6.7889 | 7.0821 | 7.3721 | 7.6675 | 7.9639 | 8.2531 | 8.5336 | 8.8045 | 9.0637 | 9.3156 | 9.56 | 9.7952 | 10.0258 | 10.2507 | 10.4685 | 10.6824 | 10.8921 | 11.0975 | 11.2988 | 11.4961 | 11.6898 | 11.8799 | 12.0665 | 12.2496 | 3455.9106 | 3887.9385 | 4304.532 | 4709.5075 | 5103.6976 | 5475.4869 | 5828.213 | 6164.4044 | 6483.9599 | 6788.914
48 | PMA | Northwest | TBU3 | Burnie 22 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0.94235 | 1.0982 | 1.277 | 1.4722 | 1.6837 | 1.8692 | 2.0193 | 2.164 | 2.3046 | 2.4362 | 2.5604 | 2.6782 | 2.7894 | 2.895 | 2.9958 | 3.0951 | 3.1956 | 3.2958 | 3.3931 | 3.4869 | 3.5769 | 3.6626 | 3.7454 | 3.8252 | 3.9016 | 3.9761 | 4.0483 | 4.1179 | 4.1857 | 4.2519 | 4.3164 | 4.3791 | 4.4403 | 4.5001 | 4.5583 | 4.6152 | 4.6707 | 1683.7161 | 1869.2441 | 2019.2942 | 2164.0092 | 2304.5677 | 2436.2131 | 2560.4248 | 2678.1535 | 2789.3982 | 2894.9569
48 | PMA | Southern | TKR2 | Knights Rd 11 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0.059251 | 0.068351 | 0.079726 | 0.092454 | 0.10637 | 0.1196 | 0.13056 | 0.14133 | 0.15194 | 0.16204 | 0.17172 | 0.18103 | 0.18997 | 0.19858 | 0.20694 | 0.21529 | 0.22387 | 0.23256 | 0.24113 | 0.24951 | 0.25769 | 0.26559 | 0.27333 | 0.28092 | 0.28829 | 0.29558 | 0.30277 | 0.30979 | 0.31674 | 0.32363 | 0.33044 | 0.33717 | 0.34384 | 0.35044 | 0.35698 | 0.36346 | 0.36988 | 106.3701 | 119.6041 | 130.5555 | 141.3333 | 151.9433 | 162.0402 | 171.7219 | 181.0332 | 189.9701 | 198.5816
48 | PMA | Southern | CAZ | Cambridge | base | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.21308 | 0.24943 | 0.29203 | 0.34484 | 0.41248 | 0.4744 | 0.52243 | 0.56958 | 0.61577 | 0.65969 | 0.70169 | 0.74198 | 0.78058 | 0.81769 | 0.85363 | 0.88944 | 0.9262 | 0.96333 | 0.99984 | 1.0355 | 1.0702 | 1.1036 | 1.1364 | 1.1683 | 1.1994 | 1.23 | 1.2601 | 1.2894 | 1.3184 | 1.3471 | 1.3754 | 1.4033 | 1.4308 | 1.458 | 1.485 | 1.5116 | 1.5379 | 412.4758 | 474.404 | 522.4339 | 569.5839 | 615.7718 | 659.6932 | 701.6852 | 741.9845 | 780.5843 | 817.6923
51 | PMA | George Town | TGT3 | George Town 22 kV | base | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.0009099 | 0.0044324 | 0.012593 | 0.021025 | 0.026243 | 0.031862 | 0.041388 | 0.052646 | 0.065793 | 0.094006 | 0.1263 | 0.16272 | 0.20394 | 0.25022 | 0.30165 | 0.35829 | 0.42022 | 0.48754 | 0.5597 | 0.63656 | 0.71823 | 0.80479 | 0.89446 | 0.98729 | 1.0833 | 1.1826 | 1.2851 | 1.3909 | 1.5001 | 1.6128 | 1.7278 | 1.8454 | 1.9655 | 0.9099 | 4.4324 | 12.5925 | 21.0254 | 26.2426 | 31.8622 | 41.3884 | 52.6458 | 65.7934 | 94.006
51 | PMA | North | TNW2 | Norwood 22 kV | base | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.00094259 | 0.003717 | 0.010365 | 0.016625 | 0.021098 | 0.025907 | 0.033267 | 0.044118 | 0.056366 | 0.081292 | 0.10993 | 0.1423 | 0.17898 | 0.22019 | 0.26596 | 0.31633 | 0.37134 | 0.43103 | 0.49487 | 0.56273 | 0.63465 | 0.71069 | 0.78924 | 0.87034 | 0.95398 | 1.0402 | 1.129 | 1.2204 | 1.3144 | 1.4111 | 1.5096 | 1.6099 | 1.7121 | 0.94259 | 3.717 | 10.3646 | 16.6253 | 21.0978 | 25.9071 | 33.2666 | 44.1177 | 56.3661 | 81.2925
51 | PMA | North | TTR2 | Trevallyn 22 kV | base | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.0022056 | 0.010438 | 0.029156 | 0.047279 | 0.059407 | 0.072588 | 0.093371 | 0.12151 | 0.15386 | 0.22162 | 0.2993 | 0.38696 | 0.48617 | 0.59757 | 0.72126 | 0.85739 | 1.0061 | 1.1676 | 1.3404 | 1.5242 | 1.7192 | 1.9256 | 2.1391 | 2.3597 | 2.5875 | 2.8225 | 3.065 | 3.3148 | 3.5721 | 3.8371 | 4.1073 | 4.3829 | 4.6639 | 2.2056 | 10.4379 | 29.1556 | 47.2788 | 59.4072 | 72.5875 | 93.3706 | 121.5083 | 153.8585 | 221.625
51 | PMA | Northwest | TBU3 | Burnie 22 kV | base | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.0016276 | 0.0081703 | 0.019413 | 0.030762 | 0.040608 | 0.050334 | 0.065999 | 0.089626 | 0.11013 | 0.15555 | 0.20702 | 0.26452 | 0.32896 | 0.40063 | 0.47953 | 0.56566 | 0.65901 | 0.7596 | 0.86652 | 0.97949 | 1.0985 | 1.2237 | 1.3524 | 1.4846 | 1.6204 | 1.7596 | 1.9024 | 2.0487 | 2.1986 | 2.352 | 2.5075 | 2.6653 | 2.8253 | 1.6276 | 8.1703 | 19.4126 | 30.7622 | 40.6082 | 50.3339 | 65.9994 | 89.6264 | 110.1314 | 155.5503
51 | PMA | Southern | TKR2 | Knights Rd 11 kV | base | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.00051591 | 0.0037584 | 0.011414 | 0.018363 | 0.023141 | 0.028461 | 0.036584 | 0.04988 | 0.061567 | 0.087407 | 0.11704 | 0.15055 | 0.18861 | 0.23153 | 0.27945 | 0.33249 | 0.39082 | 0.45459 | 0.52334 | 0.59702 | 0.67579 | 0.75981 | 0.84738 | 0.93861 | 1.0336 | 1.1323 | 1.235 | 1.3417 | 1.4525 | 1.5675 | 1.6858 | 1.8074 | 1.9324 | 0.51591 | 3.7584 | 11.4139 | 18.3634 | 23.1408 | 28.4605 | 36.5839 | 49.8798 | 61.5673 | 87.4071
51 | PMA | Southern | CAZ | Cambridge | base | maximum | Battery | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0 | 0 | 0 | 0 | 0 | 0.00073559 | 0.0023272 | 0.0039213 | 0.0050752 | 0.0068405 | 0.009317 | 0.01356 | 0.016954 | 0.024331 | 0.032793 | 0.042364 | 0.053227 | 0.065468 | 0.079118 | 0.094211 | 0.11078 | 0.12887 | 0.14834 | 0.16917 | 0.19139 | 0.21505 | 0.23967 | 0.26526 | 0.29184 | 0.31944 | 0.34808 | 0.37777 | 0.40854 | 0.44042 | 0.47313 | 0.50669 | 0.54112 | 0 | 0.73559 | 2.3272 | 3.9213 | 5.0752 | 6.8405 | 9.317 | 13.5604 | 16.9545 | 24.3313
48 | PMA | George Town | TGT3 | George Town 22 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0.078266 | 0.089154 | 0.10375 | 0.12051 | 0.13674 | 0.15278 | 0.16892 | 0.18489 | 0.20082 | 0.21649 | 0.23201 | 0.24744 | 0.26281 | 0.27803 | 0.29349 | 0.30937 | 0.32572 | 0.34232 | 0.35872 | 0.37481 | 0.39053 | 0.40581 | 0.42091 | 0.4358 | 0.45035 | 0.46483 | 0.47918 | 0.49333 | 0.50744 | 0.52151 | 0.53553 | 0.5495 | 0.56342 | 0.5773 | 0.59114 | 0.60494 | 0.61871 | 136.7416 | 152.7804 | 168.9211 | 184.8901 | 200.823 | 216.4935 | 232.005 | 247.4426 | 262.8074 | 278.0262
48 | PMA | North | TNW2 | Norwood 22 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0.89761 | 1.0512 | 1.2232 | 1.4231 | 1.6346 | 1.8255 | 2.0123 | 2.1981 | 2.382 | 2.5621 | 2.7397 | 2.9156 | 3.0899 | 3.2619 | 3.4358 | 3.6137 | 3.796 | 3.9804 | 4.1618 | 4.3389 | 4.5113 | 4.6782 | 4.8424 | 5.0037 | 5.1605 | 5.316 | 5.4695 | 5.6203 | 5.77 | 5.9186 | 6.0661 | 6.2124 | 6.3577 | 6.502 | 6.6453 | 6.7877 | 6.929 | 1634.6275 | 1825.4959 | 2012.2889 | 2198.1486 | 2381.9643 | 2562.108 | 2739.679 | 2915.5619 | 3089.9266 | 3261.8557
48 | PMA | North | TTR2 | Trevallyn 22 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 1.8699 | 2.188 | 2.5558 | 2.9926 | 3.4592 | 3.9053 | 4.3487 | 4.7896 | 5.2264 | 5.6557 | 6.0795 | 6.5002 | 6.918 | 7.3307 | 7.7492 | 8.1777 | 8.618 | 9.064 | 9.5036 | 9.9336 | 10.353 | 10.7597 | 11.1607 | 11.5551 | 11.9395 | 12.3214 | 12.699 | 13.0704 | 13.44 | 13.8077 | 14.1731 | 14.5364 | 14.8978 | 15.2573 | 15.615 | 15.9709 | 16.325 | 3459.1868 | 3905.2851 | 4348.6743 | 4789.5671 | 5226.4461 | 5655.7384 | 6079.5166 | 6500.1851 | 6917.973 | 7330.7104
48 | PMA | Northwest | TBU3 | Burnie 22 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0.94235 | 1.0982 | 1.277 | 1.4722 | 1.6849 | 1.8756 | 2.0353 | 2.1928 | 2.3486 | 2.5006 | 2.6498 | 2.7971 | 2.9425 | 3.0854 | 3.2294 | 3.376 | 3.5258 | 3.6766 | 3.8244 | 3.9682 | 4.1076 | 4.242 | 4.3738 | 4.5026 | 4.6275 | 4.7508 | 4.8721 | 4.9906 | 5.1079 | 5.2239 | 5.3386 | 5.4519 | 5.564 | 5.6748 | 5.7844 | 5.8929 | 6.0002 | 1684.9267 | 1875.585 | 2035.2676 | 2192.8229 | 2348.5934 | 2500.5822 | 2649.8089 | 2797.1013 | 2942.5351 | 3085.3873
48 | PMA | Southern | TKR2 | Knights Rd 11 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0.059251 | 0.068351 | 0.079726 | 0.092454 | 0.10646 | 0.12006 | 0.13172 | 0.14345 | 0.15521 | 0.16688 | 0.17851 | 0.19016 | 0.20185 | 0.2135 | 0.22544 | 0.23777 | 0.25057 | 0.26365 | 0.27667 | 0.28952 | 0.30218 | 0.31457 | 0.32691 | 0.33915 | 0.3512 | 0.36328 | 0.37534 | 0.38731 | 0.39934 | 0.41141 | 0.42353 | 0.43569 | 0.44789 | 0.46015 | 0.47246 | 0.48482 | 0.49723 | 106.4572 | 120.0606 | 131.7181 | 143.4544 | 155.214 | 166.8754 | 178.5082 | 190.1613 | 201.8465 | 213.5035
48 | PMA | Southern | CAZ | Cambridge | high | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.21308 | 0.24943 | 0.29203 | 0.34484 | 0.41285 | 0.47638 | 0.52751 | 0.57884 | 0.63004 | 0.68076 | 0.73121 | 0.78165 | 0.83211 | 0.88234 | 0.93365 | 0.98657 | 1.0414 | 1.0972 | 1.1527 | 1.2074 | 1.2611 | 1.3136 | 1.3657 | 1.4173 | 1.468 | 1.5187 | 1.5692 | 1.6193 | 1.6694 | 1.7197 | 1.77 | 1.8204 | 1.8708 | 1.9214 | 1.972 | 2.0228 | 2.0737 | 412.8455 | 476.3789 | 527.506 | 578.8434 | 630.0357 | 680.7593 | 731.2125 | 781.646 | 832.1149 | 882.3446
51 | PMA | George Town | TGT3 | George Town 22 kV | high | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.0009099 | 0.0044324 | 0.012593 | 0.021025 | 0.026243 | 0.032521 | 0.043815 | 0.057939 | 0.075196 | 0.12045 | 0.17165 | 0.22887 | 0.293 | 0.36442 | 0.44327 | 0.52967 | 0.62374 | 0.72566 | 0.83473 | 0.95084 | 1.0741 | 1.2046 | 1.3401 | 1.4806 | 1.626 | 1.7765 | 1.9321 | 2.0929 | 2.2589 | 2.4302 | 2.6055 | 2.7848 | 2.9683 | 0.9099 | 4.4324 | 12.5925 | 21.0254 | 26.2426 | 32.521 | 43.8153 | 57.9388 | 75.1965 | 120.4518
51 | PMA | North | TNW2 | Norwood 22 kV | high | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.00094259 | 0.003717 | 0.010365 | 0.016625 | 0.021098 | 0.026487 | 0.035212 | 0.048826 | 0.064903 | 0.10439 | 0.1493 | 0.19965 | 0.25623 | 0.31934 | 0.38907 | 0.46546 | 0.5486 | 0.63858 | 0.73473 | 0.83692 | 0.94521 | 1.0596 | 1.1781 | 1.3007 | 1.4273 | 1.558 | 1.6928 | 1.8317 | 1.9748 | 2.122 | 2.2723 | 2.4257 | 2.5822 | 0.94259 | 3.717 | 10.3646 | 16.6253 | 21.0978 | 26.4867 | 35.2122 | 48.826 | 64.9032 | 104.392
51 | PMA | North | TTR2 | Trevallyn 22 kV | high | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.0022056 | 0.010438 | 0.029156 | 0.047279 | 0.059407 | 0.074159 | 0.0988 | 0.1341 | 0.17656 | 0.28468 | 0.40723 | 0.54434 | 0.69816 | 0.86952 | 1.0587 | 1.2659 | 1.4913 | 1.7353 | 1.9962 | 2.2736 | 2.5678 | 2.8789 | 3.2013 | 3.5351 | 3.8802 | 4.2368 | 4.605 | 4.9848 | 5.3764 | 5.7798 | 6.1921 | 6.6133 | 7.0434 | 2.2056 | 10.4379 | 29.1556 | 47.2788 | 59.4072 | 74.1593 | 98.7997 | 134.1013 | 176.5642 | 284.677
51 | PMA | Northwest | TBU3 | Burnie 22 kV | high | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.0016276 | 0.0081703 | 0.019413 | 0.030762 | 0.040608 | 0.051479 | 0.070052 | 0.099695 | 0.12661 | 0.20017 | 0.28258 | 0.37381 | 0.4751 | 0.58684 | 0.70909 | 0.84185 | 0.98516 | 1.1391 | 1.3025 | 1.475 | 1.6568 | 1.8478 | 2.0445 | 2.2471 | 2.4554 | 2.6694 | 2.8892 | 3.1146 | 3.3458 | 3.5826 | 3.8233 | 4.0681 | 4.3167 | 1.6276 | 8.1703 | 19.4126 | 30.7622 | 40.6082 | 51.4791 | 70.0522 | 99.6946 | 126.6095 | 200.1737
51 | PMA | Southern | TKR2 | Knights Rd 11 kV | high | maximum | Battery | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0 | 0 | 0 | 0 | 0.00051591 | 0.0037584 | 0.011414 | 0.018363 | 0.023141 | 0.029098 | 0.03873 | 0.055411 | 0.070752 | 0.11243 | 0.15961 | 0.21242 | 0.27178 | 0.3381 | 0.41161 | 0.49252 | 0.58103 | 0.67742 | 0.78112 | 0.89211 | 1.0106 | 1.1368 | 1.2686 | 1.4059 | 1.549 | 1.6978 | 1.8527 | 2.0136 | 2.1807 | 2.3542 | 2.5329 | 2.7167 | 2.9059 | 0.51591 | 3.7584 | 11.4139 | 18.3634 | 23.1408 | 29.0985 | 38.7296 | 55.4106 | 70.7516 | 112.4274
51 | PMA | Southern | CAZ | Cambridge | high | maximum | Battery | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0 | 0 | 0 | 0 | 0 | 0.00073559 | 0.0023272 | 0.0039213 | 0.0050752 | 0.0070492 | 0.0099853 | 0.015309 | 0.019764 | 0.03162 | 0.045053 | 0.060095 | 0.077 | 0.095882 | 0.11679 | 0.13979 | 0.16492 | 0.19225 | 0.2216 | 0.25298 | 0.28643 | 0.32199 | 0.35904 | 0.3976 | 0.43769 | 0.47935 | 0.52259 | 0.56744 | 0.61395 | 0.66213 | 0.71164 | 0.7625 | 0.81474 | 0 | 0.73559 | 2.3272 | 3.9213 | 5.0752 | 7.0492 | 9.9853 | 15.309 | 19.7641 | 31.6195
Note on A2: Dhor Ngor-Apuol: Data acquired from "NIEIR Final Substation ALL SCENARIOS 05042023"

## Feeder DER (hidden)
| NET DER AVERAGE DAY MAX DEMAND IMPACT (kW) | [9 empty] | NET DER AVERAGE DAY MIN DEMAND IMPACT (kW)
Feeder | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
12017 | 54.2933 | 102.2039 | 158.3107 | 220.7165 | 284.3494 | 354.0076 | 431.3843 | 598.2703 | 738.3074 | 868.9035 | -486.3746 | -595.3591 | -714.055 | -829.7761 | -931.7136 | -1024.1476 | -1111.5569 | -1211.1373 | -1310.2904 | -1397.0625
12018 | 32.9689 | 62.1469 | 97.0035 | 137.1205 | 179.2653 | 227.3641 | 281.999 | 402.3861 | 502.1691 | 594.8805 | -273.9201 | -339.7522 | -411.9875 | -482.8333 | -545.5396 | -602.4505 | -656.3133 | -715.6078 | -774.8986 | -825.1967
12019 | 40.2314 | 75.8369 | 118.3718 | 167.3259 | 218.7545 | 277.4486 | 344.1188 | 491.0252 | 612.7887 | 725.9229 | -334.2601 | -414.5941 | -502.7416 | -589.1935 | -665.713 | -735.1604 | -800.8883 | -873.2445 | -945.596 | -1006.9739
12030 | 40.1108 | 78.0333 | 122.7522 | 173.0762 | 224.9365 | 282.2755 | 346.8155 | 486.6118 | 603.332 | 712.2669 | -348.5289 | -434.6431 | -528.7031 | -620.6053 | -701.6979 | -775.2374 | -844.7795 | -922.756 | -1001.2648 | -1069.2707
12031 | 54.2594 | 106.9521 | 168.6114 | 237.0603 | 306.7504 | 382.9378 | 467.3643 | 648.1011 | 801.2346 | 944.5103 | -485.1165 | -605.1924 | -735.9888 | -863.4962 | -975.798 | -1077.5944 | -1173.8128 | -1283.0736 | -1393.0631 | -1489.5553
12032 | 25.9172 | 48.8854 | 76.3211 | 107.894 | 141.0599 | 178.9087 | 221.8988 | 316.6229 | 395.1343 | 468.0795 | -215.432 | -267.2496 | -324.1029 | -379.858 | -429.2034 | -473.9849 | -516.3648 | -563.02 | -609.6656 | -649.232
12033 | 13.3228 | 25.103 | 39.1239 | 55.1612 | 71.9205 | 90.8745 | 112.403 | 159.409 | 198.6279 | 235.0918 | -112.3188 | -138.9381 | -168.1057 | -196.6804 | -221.9496 | -244.8797 | -266.5784 | -290.577 | -314.6395 | -335.138
12035 | 31.6386 | 59.6394 | 93.0895 | 131.5878 | 172.0321 | 218.1902 | 270.6206 | 386.1503 | 481.9071 | 570.8777 | -262.8677 | -326.0436 | -395.3642 | -463.3515 | -523.5276 | -578.1422 | -629.8317 | -686.7338 | -743.6322 | -791.9008
12036 | 0.071906 | 0.13554 | 0.21157 | 0.29906 | 0.39098 | 0.49589 | 0.61505 | 0.87761 | 1.0952 | 1.2974 | -0.59743 | -0.74101 | -0.89856 | -1.0531 | -1.1898 | -1.314 | -1.4314 | -1.5608 | -1.6901 | -1.7998
12037 | 8.4849 | 15.9942 | 24.9649 | 35.2895 | 46.1359 | 58.5146 | 72.5755 | 103.5585 | 129.2387 | 153.099 | -70.4963 | -87.439 | -106.0295 | -124.2624 | -140.4006 | -155.0472 | -168.9094 | -184.1695 | -199.4286 | -212.3734
12038 | 34.5554 | 66.0629 | 103.1682 | 144.8287 | 187.6697 | 234.9395 | 288.0551 | 402.9428 | 498.9333 | 588.4701 | -304.7631 | -376.3566 | -454.5254 | -530.8912 | -598.276 | -659.4108 | -717.2492 | -782.4129 | -847.7106 | -904.4695
12039 | 41.0023 | 77.9867 | 122.1155 | 172.8277 | 226.0383 | 286.7074 | 355.5773 | 507.243 | 632.934 | 749.6685 | -342.922 | -426.2852 | -517.6585 | -607.1726 | -686.3111 | -758.0618 | -825.899 | -900.6111 | -975.1688 | -1038.3199
13043 | 12.2294 | 24.8069 | 39.7159 | 56.7215 | 74.4599 | 94.6012 | 117.3941 | 167.5005 | 208.944 | 247.3363 | -109.4664 | -137.6047 | -168.2366 | -198.0169 | -224.135 | -247.6325 | -269.6725 | -293.8465 | -317.6991 | -337.6444
13044 | 9.2304 | 18.1183 | 28.8145 | 41.3312 | 54.6864 | 70.1919 | 87.9431 | 127.73 | 160.3671 | 190.7057 | -95.0164 | -114.7418 | -136.3115 | -157.3135 | -175.7279 | -192.2105 | -207.5824 | -223.3786 | -239.1969 | -252.3098
13045 | 40.5973 | 82.3793 | 132.039 | 188.9679 | 248.6225 | 316.6926 | 393.9094 | 564.4298 | 705.1509 | 835.5835 | -379.5919 | -472.8185 | -574.3286 | -672.9622 | -759.3797 | -836.9662 | -909.5777 | -987.9288 | -1065.6278 | -1130.268
13046 | 0.20925 | 0.41074 | 0.65322 | 0.93698 | 1.2397 | 1.5913 | 1.9937 | 2.8956 | 3.6355 | 4.3233 | -2.154 | -2.6012 | -3.0902 | -3.5663 | -3.9838 | -4.3574 | -4.7059 | -5.064 | -5.4226 | -5.7199
13047 | 4.1646 | 8.4724 | 13.5877 | 19.4428 | 25.5698 | 32.5515 | 40.4658 | 57.9223 | 72.3352 | 85.6912 | -38.6313 | -48.2469 | -58.7136 | -68.8822 | -77.7909 | -85.7909 | -93.2799 | -101.3931 | -109.4249 | -116.112
13048 | 9.1374 | 17.9358 | 28.5241 | 40.9147 | 54.1354 | 69.4847 | 87.057 | 126.4431 | 158.7513 | 188.7843 | -94.0591 | -113.5857 | -134.9381 | -155.7285 | -173.9574 | -190.2739 | -205.4909 | -221.128 | -236.7869 | -249.7676
13049 | 23.3665 | 45.8663 | 72.9434 | 104.6293 | 138.438 | 177.6898 | 222.6267 | 323.3468 | 405.9672 | 482.769 | -240.5327 | -290.4673 | -345.0707 | -398.237 | -444.8528 | -486.5782 | -525.4919 | -565.4799 | -605.5237 | -638.7188
13050 | 10.0474 | 18.9885 | 29.675 | 41.9882 | 54.9377 | 69.7349 | 86.5522 | 123.6544 | 154.3835 | 182.9358 | -84.7249 | -104.8757 | -126.9813 | -148.6513 | -167.8197 | -185.201 | -201.6358 | -219.6432 | -237.6674 | -252.9301
13052 | 21.2635 | 43.3917 | 69.5744 | 99.3487 | 130.322 | 165.3953 | 205.0292 | 291.9517 | 363.9126 | 430.5423 | -187.5498 | -237.0847 | -290.9722 | -343.3397 | -389.2564 | -430.5772 | -469.3478 | -512.1767 | -554.2965 | -589.5573
13053 | 22.6282 | 46.6191 | 74.9814 | 107.2026 | 140.695 | 178.5997 | 221.415 | 315.2922 | 392.9899 | 464.9062 | -201.5739 | -255.2257 | -313.5395 | -370.1509 | -419.7351 | -464.3098 | -506.0882 | -552.2149 | -597.5065 | -635.3546
13054 | 5.2897 | 10.5942 | 16.929 | 24.2493 | 31.9741 | 40.8506 | 50.9563 | 73.4067 | 91.8889 | 109.0398 | -51.4479 | -63.2594 | -76.1413 | -88.6681 | -99.6465 | -109.4917 | -118.6932 | -128.4266 | -138.144 | -146.205
13055 | 28.0107 | 57.751 | 92.9005 | 132.813 | 174.2818 | 221.1926 | 274.1684 | 390.2768 | 486.3903 | 575.3455 | -248.803 | -315.3214 | -387.6133 | -457.7922 | -519.2595 | -574.5212 | -626.3208 | -683.5824 | -739.7785 | -786.7511
13056 | 20.1354 | 38.564 | 60.5497 | 85.8233 | 112.3524 | 142.6205 | 176.9868 | 252.7335 | 315.4599 | 373.7065 | -171.3202 | -212.7964 | -258.2247 | -302.6842 | -341.9457 | -377.4944 | -411.0576 | -447.8705 | -484.6041 | -515.6409
13057 | 48.4501 | 97.9091 | 155.4446 | 218.9932 | 283.4427 | 353.7379 | 431.5883 | 599.3078 | 739.847 | 870.6418 | -475.6193 | -586.6659 | -706.6615 | -822.6286 | -923.8781 | -1014.9214 | -1100.3092 | -1196.9709 | -1292.7743 | -1375.6843
13058 | 0.62776 | 1.2322 | 1.9597 | 2.8109 | 3.7192 | 4.7738 | 5.981 | 8.6869 | 10.9066 | 12.9699 | -6.4621 | -7.8036 | -9.2706 | -10.6989 | -11.9513 | -13.0723 | -14.1177 | -15.192 | -16.2678 | -17.1596
14060 | 2.976 | 5.8417 | 9.2903 | 13.3259 | 17.6319 | 22.6311 | 28.3544 | 41.1825 | 51.7053 | 61.487 | -30.635 | -36.9948 | -43.9493 | -50.7207 | -56.6579 | -61.9722 | -66.9283 | -72.0213 | -77.1214 | -81.3493
14061 | 1.2555 | 2.4645 | 3.9193 | 5.6219 | 7.4385 | 9.5475 | 11.962 | 17.3739 | 21.8132 | 25.9398 | -12.9241 | -15.6072 | -18.5411 | -21.3978 | -23.9025 | -26.1445 | -28.2354 | -30.384 | -32.5356 | -34.3192
14062 | 0.25575 | 0.50202 | 0.79839 | 1.1452 | 1.5152 | 1.9449 | 2.4367 | 3.5391 | 4.4434 | 5.284 | -2.6327 | -3.1792 | -3.7769 | -4.3588 | -4.869 | -5.3257 | -5.7517 | -6.1893 | -6.6276 | -6.991
14063 | 5.8358 | 11.4552 | 18.2177 | 26.1313 | 34.5751 | 44.3783 | 55.6013 | 80.7563 | 101.3908 | 120.5721 | -60.0734 | -72.5446 | -86.1818 | -99.4602 | -111.1025 | -121.5235 | -131.2423 | -141.2293 | -151.2303 | -159.5208
14064 | 1.302 | 2.5557 | 4.0645 | 5.8301 | 7.714 | 9.9011 | 12.4051 | 18.0173 | 22.6211 | 26.9006 | -13.4028 | -16.1852 | -19.2278 | -22.1903 | -24.7878 | -27.1128 | -29.2811 | -31.5093 | -33.7406 | -35.5903
14065 | 7.1146 | 13.9653 | 22.2096 | 31.8573 | 42.1513 | 54.1026 | 67.7848 | 98.4519 | 123.6079 | 146.9923 | -73.2368 | -88.4408 | -105.0663 | -121.2542 | -135.4477 | -148.1522 | -160.0005 | -172.176 | -184.3684 | -194.4756
14066 | 1.8135 | 3.5598 | 5.6613 | 8.1205 | 10.7444 | 13.7909 | 17.2785 | 25.0956 | 31.5079 | 37.4686 | -18.6682 | -22.5437 | -26.7816 | -30.9079 | -34.5259 | -37.7643 | -40.7844 | -43.888 | -46.9959 | -49.5722
14067 | 2.697 | 5.294 | 8.4193 | 12.0766 | 15.9789 | 20.5095 | 25.6962 | 37.3216 | 46.8579 | 55.7226 | -27.763 | -33.5266 | -39.8291 | -45.9657 | -51.3462 | -56.1623 | -60.6538 | -65.2693 | -69.8913 | -73.7228
14068 | 3.8595 | 7.5759 | 12.0484 | 17.2821 | 22.8664 | 29.3498 | 36.7722 | 53.4085 | 67.0553 | 79.7409 | -39.7298 | -47.9777 | -56.9968 | -65.7784 | -73.4782 | -80.3701 | -86.7977 | -93.4027 | -100.0169 | -105.4998
14069 | 2.3837 | 4.6962 | 7.4753 | 10.7197 | 14.1738 | 18.1778 | 22.7563 | 33.0021 | 41.4122 | 49.2275 | -24.2902 | -29.4258 | -35.0388 | -40.5027 | -45.293 | -49.5823 | -53.5842 | -57.7194 | -61.8579 | -65.2891
14070 | 3.162 | 6.2068 | 9.8709 | 14.1588 | 18.7339 | 24.0456 | 30.1266 | 43.7564 | 54.9368 | 65.3299 | -32.5497 | -39.307 | -46.6961 | -53.8908 | -60.199 | -65.8454 | -71.1113 | -76.5227 | -81.9415 | -86.4336
14071 | 0.02325 | 0.045638 | 0.072581 | 0.10411 | 0.13775 | 0.17681 | 0.22152 | 0.32174 | 0.40395 | 0.48037 | -0.23934 | -0.28902 | -0.34335 | -0.39626 | -0.44264 | -0.48416 | -0.52288 | -0.56267 | -0.60251 | -0.63554
16091 | 30.3247 | 64.4743 | 105.4487 | 152.4436 | 201.6071 | 256.9337 | 319.7731 | 455.936 | 570.9496 | 679.2636 | -293.4069 | -372.5552 | -460.7117 | -548.8517 | -628.5693 | -702.6883 | -774.592 | -857.9249 | -943.0252 | -1018.9416
16092 | 16.8033 | 35.726 | 58.4305 | 84.4709 | 111.713 | 142.3702 | 177.1903 | 252.6399 | 316.3703 | 376.3885 | -162.5805 | -206.4375 | -255.2861 | -304.1256 | -348.2981 | -389.3684 | -429.2111 | -475.3869 | -522.5421 | -564.6083
16093 | 7.5352 | 16.0209 | 26.2024 | 37.8799 | 50.0963 | 63.8441 | 79.4588 | 113.2932 | 141.8723 | 168.7867 | -72.9072 | -92.5743 | -114.4799 | -136.3813 | -156.1899 | -174.6074 | -192.4744 | -213.1813 | -234.3275 | -253.1915
16094 | 28.3522 | 60.2671 | 98.5569 | 142.4685 | 188.4027 | 240.0923 | 298.7985 | 426.0024 | 533.442 | 634.6176 | -274.111 | -348.0729 | -430.4447 | -512.7921 | -587.2618 | -656.4937 | -723.6486 | -801.4701 | -880.9339 | -951.8072
16095 | 4.9461 | 10.3711 | 16.8431 | 24.22 | 31.8976 | 40.5053 | 50.2573 | 71.3547 | 89.1045 | 105.7595 | -45.5608 | -58.0566 | -71.8867 | -85.6151 | -97.937 | -109.3082 | -120.2558 | -132.862 | -145.6372 | -156.8755
16096 | 32.8853 | 67.591 | 108.9824 | 156.3207 | 205.7632 | 261.5648 | 324.8754 | 462.6771 | 578.1721 | 685.9383 | -305.894 | -385.0265 | -472.1798 | -558.1131 | -634.6498 | -704.6471 | -771.4165 | -846.4789 | -922.2181 | -987.7464
16097 | 6.3577 | 13.2462 | 21.4416 | 30.755 | 40.4238 | 51.2443 | 63.4882 | 89.9555 | 112.1797 | 132.9952 | -57.2191 | -73.0389 | -90.4946 | -107.7616 | -123.2016 | -137.3974 | -151.0122 | -166.6525 | -182.4122 | -196.1874
16098 | 32.4306 | 68.1062 | 110.7066 | 159.3196 | 209.9642 | 266.7939 | 331.2091 | 470.6317 | 587.995 | 698.1652 | -301.2808 | -383.5094 | -474.5991 | -565.1076 | -646.4271 | -721.545 | -793.9362 | -877.296 | -961.9256 | -1036.494
17100 | 1.5731 | 3.3115 | 5.3988 | 7.797 | 10.3098 | 13.1435 | 16.3646 | 23.3568 | 29.2598 | 34.8142 | -15.1059 | -19.1281 | -23.6065 | -28.081 | -32.1243 | -35.8792 | -39.5174 | -43.7139 | -48.0001 | -51.816
17101 | 16.8337 | 34.2829 | 54.4901 | 76.7592 | 99.3538 | 124.072 | 151.5162 | 209.9095 | 259.5426 | 306.1707 | -182.0786 | -220.4229 | -261.492 | -300.7192 | -334.5402 | -364.5245 | -392.247 | -422.4338 | -452.7082 | -479.0854
17102 | 0.026255 | 0.055822 | 0.091298 | 0.13199 | 0.17455 | 0.22245 | 0.27686 | 0.39475 | 0.49433 | 0.58811 | -0.25403 | -0.32256 | -0.39888 | -0.4752 | -0.54422 | -0.60839 | -0.67064 | -0.74279 | -0.81647 | -0.8822
17103 | 16.6633 | 34.4284 | 55.7892 | 80.4129 | 106.2946 | 135.5964 | 168.9588 | 241.6279 | 302.9119 | 360.4856 | -157.7659 | -198.7325 | -244.3117 | -289.7871 | -330.8101 | -368.8157 | -405.5527 | -447.5231 | -490.4018 | -528.4222
17104 | 3.5707 | 7.5918 | 12.4165 | 17.9501 | 23.739 | 30.2537 | 37.6529 | 53.686 | 67.2287 | 79.9825 | -34.5483 | -43.868 | -54.2483 | -64.6267 | -74.0134 | -82.7408 | -91.2074 | -101.0197 | -111.0402 | -119.9793
17105 | 23.908 | 49.9424 | 81.2201 | 117.204 | 154.9567 | 197.5981 | 246.1025 | 351.54 | 440.5135 | 524.1793 | -228.2456 | -288.4008 | -355.3581 | -422.2181 | -482.5941 | -538.6087 | -592.8311 | -655.1332 | -718.773 | -775.3395
17106 | 12.8125 | 27.2411 | 44.5532 | 64.4091 | 85.1812 | 108.5573 | 135.1076 | 192.6379 | 241.2324 | 286.9962 | -123.9676 | -157.4086 | -194.6557 | -231.8958 | -265.5773 | -296.8934 | -327.2735 | -362.4825 | -398.4383 | -430.5138
17107 | 4.6664 | 9.8949 | 16.1695 | 23.3694 | 30.9047 | 39.3893 | 49.0281 | 69.924 | 87.5717 | 104.1876 | -45.058 | -57.1706 | -70.6605 | -84.1453 | -96.3387 | -107.6721 | -118.6633 | -131.3856 | -144.3781 | -155.9624
17108 | 0.79382 | 1.6431 | 2.6642 | 3.8409 | 5.0773 | 6.4765 | 8.0693 | 11.5377 | 14.4629 | 17.2115 | -7.5262 | -9.4854 | -11.6653 | -13.8406 | -15.8033 | -17.622 | -19.3805 | -21.3914 | -23.4458 | -25.2681
17109 | 2.6518 | 5.638 | 9.2211 | 13.3306 | 17.6297 | 22.4678 | 27.9628 | 39.8697 | 49.9272 | 59.3988 | -25.6572 | -32.5784 | -40.2873 | -47.9948 | -54.9658 | -61.4472 | -67.7349 | -75.022 | -82.4637 | -89.1023
18131 | 12.9272 | 25.3748 | 40.3548 | 57.8845 | 76.5886 | 98.304 | 123.1646 | 178.8864 | 224.5948 | 267.0841 | -133.0708 | -160.6963 | -190.9048 | -220.3182 | -246.1076 | -269.1915 | -290.7199 | -312.8426 | -334.9962 | -353.3608
18132 | 0.53476 | 1.0497 | 1.6694 | 2.3945 | 3.1682 | 4.0665 | 5.0949 | 7.4 | 9.2908 | 11.0484 | -5.5047 | -6.6475 | -7.8971 | -9.1139 | -10.1807 | -11.1356 | -12.0262 | -12.9413 | -13.8578 | -14.6174
18133 | 3.3945 | 6.6632 | 10.5968 | 15.1999 | 20.1114 | 25.8136 | 32.3418 | 46.9738 | 58.9763 | 70.1336 | -34.9431 | -42.1972 | -50.1297 | -57.8533 | -64.6254 | -70.687 | -76.3401 | -82.1493 | -87.9666 | -92.789
18134 | 15.3452 | 30.1212 | 47.9031 | 68.7118 | 90.9145 | 116.6918 | 146.2026 | 212.3472 | 266.6053 | 317.0423 | -157.9618 | -190.7546 | -226.6136 | -261.5288 | -292.1421 | -319.5439 | -345.0992 | -371.3599 | -397.6574 | -419.4571
18135 | 16.5225 | 33.3003 | 53.3843 | 76.5731 | 101.0086 | 128.9258 | 160.7202 | 230.7541 | 289.0099 | 343.2247 | -160.766 | -198.6036 | -240.1567 | -280.9227 | -317.0061 | -349.7295 | -380.673 | -414.3123 | -448.1619 | -477.0054
18136 | 14.1278 | 29.3061 | 47.3781 | 67.9574 | 89.3635 | 113.3849 | 140.5896 | 199.5291 | 248.9899 | 295.2586 | -128.533 | -163.3111 | -201.663 | -239.5617 | -273.4078 | -304.4748 | -334.2196 | -368.16 | -402.3758 | -432.1885
18141 | 11.4856 | 22.5452 | 35.8548 | 51.4297 | 68.0481 | 87.3421 | 109.4304 | 158.9386 | 199.55 | 237.3014 | -118.232 | -142.7769 | -169.6169 | -195.7503 | -218.664 | -239.1738 | -258.3015 | -277.9573 | -297.6405 | -313.9573
18142 | 4.7663 | 9.3558 | 14.879 | 21.3423 | 28.2386 | 36.2452 | 45.4114 | 65.9563 | 82.8092 | 98.4753 | -49.0639 | -59.2495 | -70.3876 | -81.2324 | -90.7411 | -99.2523 | -107.1899 | -115.3466 | -123.5148 | -130.2859
18143 | 33.9919 | 66.723 | 106.1127 | 152.207 | 201.3893 | 258.4901 | 323.8609 | 470.3811 | 590.5711 | 702.2967 | -349.9093 | -422.5504 | -501.9835 | -579.3258 | -647.1391 | -707.8382 | -764.447 | -822.6185 | -880.8713 | -929.161
18144 | 54.1895 | 112.7462 | 182.4295 | 261.6697 | 343.9844 | 436.1836 | 540.5394 | 766.2841 | 955.8021 | 1133.238 | -489.3874 | -623.7682 | -772.0183 | -918.619 | -1049.6557 | -1170.0709 | -1285.4952 | -1417.8128 | -1551.1594 | -1667.6006
18145 | 5.8591 | 12.2073 | 19.7599 | 28.3429 | 37.2533 | 47.2252 | 58.5087 | 82.9001 | 103.3813 | 122.5642 | -52.7313 | -67.3103 | -83.3969 | -99.3097 | -113.5387 | -126.6212 | -139.1681 | -153.5818 | -168.1053 | -180.8002
18146 | 66.2648 | 134.1678 | 215.3799 | 308.9354 | 407.3139 | 519.3887 | 646.9159 | 926.9527 | 1160.4745 | 1377.8415 | -638.1674 | -791.7084 | -960.4435 | -1126.1842 | -1273.1092 | -1406.628 | -1533.1557 | -1671.8663 | -1811.5412 | -1931.023
20534 | 9.4116 | 19.6681 | 31.99 | 46.1648 | 61.0355 | 77.8303 | 96.9337 | 138.457 | 173.4973 | 206.4484 | -89.8781 | -113.5787 | -139.9596 | -166.303 | -190.0925 | -212.1646 | -233.5317 | -258.0877 | -283.1707 | -305.4678
20535 | 28.899 | 60.8034 | 99.113 | 143.131 | 189.258 | 241.2799 | 300.4181 | 428.8029 | 537.1838 | 639.1617 | -277.3993 | -351.2112 | -433.3921 | -515.4966 | -589.6871 | -658.5799 | -725.3288 | -802.2998 | -880.915 | -950.8985
20536 | 28.3281 | 59.1467 | 96.1734 | 138.7752 | 183.4747 | 233.9676 | 291.4057 | 416.2739 | 521.6411 | 620.7185 | -270.3429 | -341.5463 | -420.7996 | -499.9348 | -571.3924 | -637.6839 | -701.8505 | -775.5602 | -850.8529 | -917.7703
20537 | 22.7334 | 46.9657 | 76.1029 | 109.6914 | 144.9965 | 184.9676 | 230.4784 | 329.6103 | 413.2107 | 491.749 | -215.2223 | -271.1014 | -333.2719 | -395.3005 | -451.2554 | -503.0941 | -553.2018 | -610.4447 | -668.9266 | -720.7813
20539 | 4.8871 | 10.0965 | 16.3603 | 23.581 | 31.1707 | 39.7636 | 49.5473 | 70.8583 | 88.8303 | 105.7142 | -46.2676 | -58.2803 | -71.6454 | -84.98 | -97.009 | -108.1531 | -118.925 | -131.2309 | -143.8031 | -154.9506
20540 | 4.9695 | 10.2667 | 16.636 | 23.9784 | 31.6961 | 40.4337 | 50.3824 | 72.0525 | 90.3275 | 107.4959 | -47.0474 | -59.2625 | -72.8529 | -86.4123 | -98.644 | -109.9759 | -120.9294 | -133.4426 | -146.2267 | -157.5621
20541 | 22.1667 | 46.0591 | 74.6405 | 107.3411 | 141.4951 | 179.7852 | 223.3539 | 317.8093 | 397.1336 | 471.9277 | -205.1112 | -260.1897 | -321.2661 | -381.9938 | -436.5847 | -487.0111 | -535.6045 | -591.2111 | -647.9279 | -698.0935
20544 | 23.5297 | 48.6107 | 78.7683 | 113.5333 | 150.0749 | 191.4459 | 238.5507 | 341.1546 | 427.6831 | 508.9721 | -222.7603 | -280.5965 | -344.9445 | -409.1455 | -467.0603 | -520.7145 | -572.5772 | -631.825 | -692.3552 | -746.026
20545 | 11.6962 | 24.1635 | 39.1544 | 56.4355 | 74.5997 | 95.1645 | 118.5795 | 169.5821 | 212.5939 | 253.0013 | -110.7303 | -139.4797 | -171.466 | -203.3792 | -232.1676 | -258.8382 | -284.6183 | -314.0694 | -344.1579 | -370.8368
20547 | 42.9675 | 90.0275 | 146.5236 | 211.4436 | 279.4829 | 356.2465 | 443.5183 | 633.0655 | 793.0044 | 943.4134 | -409.9557 | -518.7194 | -639.7424 | -760.56 | -869.6384 | -970.832 | -1068.7823 | -1181.4986 | -1296.5695 | -1398.8305
20548 | 37.0505 | 77.0358 | 124.7293 | 179.1183 | 235.7557 | 299.3223 | 371.3626 | 527.3898 | 658.5469 | 781.4846 | -337.6739 | -429.5924 | -531.2204 | -631.9605 | -722.2356 | -805.3926 | -885.3008 | -976.9271 | -1069.6586 | -1150.9685
20549 | 30.3188 | 63.2459 | 102.4985 | 147.1777 | 193.638 | 245.3675 | 304.2016 | 431.3249 | 538.2479 | 638.3894 | -276.0904 | -351.9807 | -435.9466 | -519.2379 | -593.9344 | -662.7933 | -729.0087 | -804.8691 | -882.1559 | -950.3987
20551 | 5.9305 | 12.2519 | 19.8529 | 28.6152 | 37.8252 | 48.2524 | 60.1248 | 85.9853 | 107.7941 | 128.2824 | -56.1449 | -70.7221 | -86.9405 | -103.1219 | -117.7188 | -131.2419 | -144.3135 | -159.2464 | -174.5026 | -188.0299
20552 | 28.5266 | 58.9341 | 95.4963 | 137.6442 | 181.9461 | 232.1031 | 289.2114 | 413.6052 | 518.5096 | 617.0619 | -270.0676 | -340.1864 | -418.1999 | -496.0352 | -566.2493 | -631.298 | -694.1747 | -766.0049 | -839.3898 | -904.4587
20553 | 41.6288 | 82.4564 | 130.0004 | 182.235 | 234.867 | 291.7629 | 354.4472 | 487.838 | 601.0492 | 706.5427 | -384.5962 | -477.9938 | -579.8691 | -679.6289 | -768.0675 | -849.0318 | -926.3938 | -1018.0322 | -1109.2001 | -1190.1269
20554 | 11.4216 | 23.5963 | 38.2353 | 55.1107 | 72.8485 | 92.9306 | 115.7959 | 165.6013 | 207.6035 | 247.0623 | -108.131 | -136.2055 | -167.441 | -198.6051 | -226.7177 | -252.7622 | -277.9371 | -306.6968 | -336.0791 | -362.1317
21081 | 33.206 | 69.6583 | 112.9002 | 161.7596 | 212.2448 | 268.0963 | 331.1374 | 467.1154 | 581.7477 | 688.9791 | -295.3856 | -379.3761 | -472.0098 | -563.5947 | -645.4499 | -720.6894 | -792.8193 | -875.5953 | -959.789 | -1033.9462
21082 | 7.8271 | 16.4195 | 26.6122 | 38.129 | 50.0291 | 63.1941 | 78.0538 | 110.1058 | 137.1262 | 162.4022 | -69.6266 | -89.4244 | -111.2595 | -132.8473 | -152.1418 | -169.8768 | -186.8788 | -206.3903 | -226.236 | -243.7159
21083 | 10.6734 | 22.3902 | 36.2893 | 51.9941 | 68.2215 | 86.1738 | 106.437 | 150.1442 | 186.9903 | 221.4576 | -94.9454 | -121.9423 | -151.7175 | -181.1554 | -207.466 | -231.6501 | -254.8348 | -281.4414 | -308.5036 | -332.3399
21084 | 3.8627 | 8.1031 | 13.1333 | 18.8169 | 24.6897 | 31.1867 | 38.5201 | 54.3379 | 67.6727 | 80.1465 | -34.3612 | -44.1315 | -54.9073 | -65.561 | -75.0829 | -83.8353 | -92.2259 | -101.855 | -111.6489 | -120.2754
21085 | 49.7864 | 104.3982 | 169.2468 | 242.6902 | 318.7571 | 403.1248 | 498.2772 | 704.3559 | 878.0449 | 1040.6926 | -444.9331 | -570.4945 | -708.9076 | -845.5939 | -967.5773 | -1079.4609 | -1186.4825 | -1308.12 | -1432.2357 | -1541.4259
21086 | 24.193 | 50.751 | 82.2558 | 117.8534 | 154.6355 | 195.3273 | 241.2572 | 340.327 | 423.8447 | 501.9705 | -215.2095 | -276.4026 | -343.8929 | -410.619 | -470.2563 | -525.0737 | -577.6255 | -637.9337 | -699.2749 | -753.3037
21087 | 21.3806 | 44.8514 | 72.6939 | 104.1534 | 136.6596 | 172.6212 | 213.2119 | 300.7651 | 374.5743 | 443.6182 | -190.1921 | -244.2717 | -303.9165 | -362.886 | -415.5907 | -464.0357 | -510.4786 | -563.7762 | -617.9866 | -665.7348
21088 | 12.4692 | 26.1574 | 42.3952 | 60.7424 | 79.7001 | 100.6729 | 124.3455 | 175.4066 | 218.4522 | 258.7187 | -110.9203 | -142.4596 | -177.2445 | -211.6356 | -242.373 | -270.6262 | -297.7117 | -328.795 | -360.4106 | -388.2574
21089 | 29.1418 | 61.1317 | 99.0812 | 141.9634 | 186.2752 | 235.3006 | 290.6356 | 410.005 | 510.6351 | 604.7711 | -259.2637 | -332.9684 | -414.2568 | -494.6222 | -566.447 | -632.4631 | -695.7471 | -768.353 | -842.2087 | -907.2582
22323 | 17.6775 | 37.2412 | 60.3751 | 86.3275 | 112.9593 | 142.2117 | 174.9594 | 245.2154 | 304.7304 | 360.449 | -172.3616 | -217.7034 | -267.7563 | -317.3452 | -361.7862 | -402.7986 | -442.2763 | -488.3806 | -534.9796 | -576.555
22324 | 20.9184 | 43.569 | 70.3253 | 100.3594 | 131.2225 | 165.1988 | 203.1303 | 284.977 | 354.3382 | 419.3722 | -214.4061 | -266.4654 | -323.7625 | -380.3164 | -430.8089 | -477.2186 | -521.7253 | -573.1518 | -625.1707 | -671.6906
22325 | 31.3757 | 66.0994 | 107.1599 | 153.2226 | 200.4915 | 252.4115 | 310.5356 | 435.2329 | 540.8661 | 639.7611 | -305.9246 | -386.4019 | -475.2408 | -563.2561 | -642.1344 | -714.9273 | -784.9963 | -866.827 | -949.5356 | -1023.3276
22326 | 9.3532 | 19.6073 | 31.8326 | 45.6847 | 60.0203 | 75.873 | 93.7835 | 132.2556 | 164.9604 | 195.6627 | -85.8835 | -109.8103 | -136.4367 | -163.0579 | -187.1465 | -209.5836 | -231.3858 | -257.0314 | -283.2391 | -306.8231
22328 | 30.2841 | 63.7996 | 103.4315 | 147.8917 | 193.5159 | 243.6295 | 299.7313 | 420.0902 | 522.0481 | 617.5023 | -295.2808 | -372.9581 | -458.7061 | -543.6591 | -619.793 | -690.0533 | -757.6845 | -836.668 | -916.499 | -987.7236
22329 | 36.0132 | 75.8631 | 122.9848 | 175.8471 | 230.0938 | 289.6792 | 356.3827 | 499.4921 | 620.7225 | 734.2208 | -351.2852 | -443.6375 | -545.5826 | -646.5794 | -737.0886 | -820.6124 | -901.0083 | -994.8917 | -1089.7824 | -1174.4443
22330 | 2.0333 | 4.2625 | 6.9201 | 9.9315 | 13.0479 | 16.4941 | 20.3877 | 28.7512 | 35.861 | 42.5354 | -18.6703 | -23.8718 | -29.6602 | -35.4474 | -40.684 | -45.5617 | -50.3013 | -55.8764 | -61.5737 | -66.7007
22331 | 37.8474 | 79.7321 | 129.2611 | 184.8251 | 241.845 | 304.4766 | 374.594 | 525.0223 | 652.4515 | 771.7522 | -369.0175 | -466.0914 | -573.2517 | -679.4192 | -774.5656 | -862.3718 | -946.8927 | -1045.5994 | -1145.3659 | -1234.3765
22333 | 0.027111 | 0.056833 | 0.092268 | 0.13242 | 0.17397 | 0.21992 | 0.27184 | 0.38335 | 0.47815 | 0.56714 | -0.24894 | -0.31829 | -0.39547 | -0.47263 | -0.54245 | -0.60749 | -0.67068 | -0.74502 | -0.82098 | -0.88934
23340 | 3.7327 | 7.8637 | 12.7485 | 18.2285 | 23.852 | 30.0288 | 36.9436 | 51.7786 | 64.3455 | 76.1107 | -36.3951 | -45.9693 | -56.5382 | -67.0091 | -76.3931 | -85.0531 | -93.389 | -103.1242 | -112.9638 | -121.7427
23341 | 23.4526 | 49.4076 | 80.0993 | 114.5301 | 149.8623 | 188.6713 | 232.1175 | 325.3256 | 404.2838 | 478.2053 | -228.6709 | -288.8257 | -355.2305 | -421.0197 | -479.9792 | -534.3901 | -586.7649 | -647.9313 | -709.7539 | -764.9116
23342 | 29.4494 | 62.8152 | 102.2637 | 146.5481 | 192.0308 | 242.0479 | 298.0351 | 418.3911 | 520.2176 | 615.5584 | -291.3226 | -368.4623 | -453.5098 | -537.619 | -612.8435 | -682.0991 | -748.6017 | -825.7652 | -903.8174 | -973.2531
23343 | 28.7699 | 60.6097 | 98.26 | 140.4971 | 183.8401 | 231.4481 | 284.7447 | 399.0856 | 495.9457 | 586.6272 | -280.5167 | -354.3102 | -435.7708 | -516.4762 | -588.8034 | -655.5506 | -719.8002 | -794.8346 | -870.674 | -938.3375
23347 | 19.0996 | 40.248 | 65.2563 | 93.3132 | 122.1066 | 153.7359 | 189.1467 | 265.1228 | 329.4777 | 389.7271 | -186.3172 | -235.3263 | -289.4249 | -343.0183 | -391.0442 | -435.3607 | -478.0146 | -527.8136 | -578.1477 | -623.0492
23348 | 29.7207 | 63.637 | 103.7343 | 148.7564 | 195.0085 | 245.8898 | 302.8424 | 425.3481 | 528.954 | 625.9637 | -295.3192 | -373.673 | -460.0263 | -545.3806 | -621.6716 | -691.8578 | -759.204 | -837.1905 | -916.0941 | -986.2241
26161 | 27.7147 | 59.3528 | 96.7975 | 138.9308 | 182.3239 | 230.183 | 283.7182 | 399.2967 | 497.4749 | 589.6682 | -274.2574 | -346.9913 | -427.203 | -506.5685 | -577.6314 | -643.1455 | -706.1813 | -779.2535 | -853.8037 | -920.5518
26162 | 30.7387 | 65.8192 | 107.2929 | 153.8605 | 201.7005 | 254.3288 | 313.2368 | 439.9493 | 547.1127 | 647.4534 | -305.4481 | -386.491 | -475.8074 | -564.0902 | -642.9981 | -715.5915 | -785.2468 | -865.9056 | -947.5132 | -1020.0459
26163 | 19.7794 | 42.3525 | 69.0395 | 99.0043 | 129.7877 | 163.6523 | 201.5577 | 283.0932 | 352.0493 | 416.6153 | -196.546 | -248.6944 | -306.1667 | -362.9738 | -413.7485 | -460.4599 | -505.2809 | -557.1823 | -609.6941 | -656.3665
26164 | 45.2636 | 96.9205 | 157.9917 | 226.5638 | 297.0095 | 374.5061 | 461.2498 | 647.8375 | 805.6385 | 953.3929 | -449.7808 | -569.1185 | -700.6394 | -830.6383 | -946.8324 | -1053.7281 | -1156.2974 | -1275.0699 | -1395.2393 | -1502.0456
26165 | 9.4159 | 20.1593 | 32.8607 | 47.122 | 61.7729 | 77.89 | 95.9302 | 134.7344 | 167.5524 | 198.2809 | -93.5519 | -118.3719 | -145.7261 | -172.7643 | -196.9317 | -219.1655 | -240.5001 | -265.2064 | -290.2032 | -312.4209
26166 | 17.5274 | 37.5306 | 61.1792 | 87.7324 | 115.0111 | 145.0202 | 178.61 | 250.8624 | 311.9678 | 369.1828 | -174.1688 | -220.3801 | -271.309 | -321.6485 | -366.6424 | -408.0357 | -447.7537 | -493.746 | -540.2792 | -581.6379
26167 | 23.0926 | 50.1863 | 82.4949 | 119.1264 | 157.064 | 199.0506 | 246.5054 | 348.51 | 435.23 | 516.6971 | -220.4744 | -283.6068 | -353.847 | -424.0528 | -487.5651 | -546.7079 | -604.1702 | -671.6586 | -740.782 | -802.9982
27171 | 37.9391 | 79.9212 | 129.5634 | 185.252 | 242.398 | 305.1669 | 375.4331 | 526.1852 | 653.889 | 773.4469 | -370.1094 | -467.402 | -574.7988 | -681.1947 | -776.5406 | -864.526 | -949.2148 | -1048.1102 | -1148.0642 | -1237.2416
27173 | 11.5227 | 23.4772 | 37.3979 | 52.826 | 68.5436 | 85.7806 | 104.9428 | 145.832 | 180.6174 | 213.2337 | -140.9394 | -167.5487 | -196.2488 | -223.8852 | -247.9137 | -269.3944 | -289.4211 | -311.4581 | -333.5074 | -352.7503
27175 | 32.0471 | 67.5151 | 109.4557 | 156.5059 | 204.7881 | 257.8213 | 317.1915 | 444.5627 | 552.4608 | 653.4761 | -312.4779 | -394.6799 | -485.4226 | -575.3238 | -655.8919 | -730.244 | -801.8136 | -885.3959 | -969.875 | -1045.2464
27176 | 10.1319 | 21.3592 | 34.6354 | 49.5294 | 64.8141 | 81.604 | 100.3999 | 140.7286 | 174.8893 | 206.8711 | -98.867 | -124.8845 | -153.6032 | -182.0529 | -207.5464 | -231.0701 | -253.7105 | -280.142 | -306.8583 | -330.6906
27178 | 23.7695 | 50.0753 | 81.1817 | 116.0778 | 151.8875 | 191.2209 | 235.2542 | 329.7219 | 409.7471 | 484.6675 | -231.7611 | -292.7287 | -360.0309 | -426.7092 | -486.4654 | -541.6116 | -594.6942 | -656.6871 | -719.3451 | -775.2482
28221 | 22.2661 | 46.677 | 75.7803 | 108.7559 | 142.882 | 180.619 | 223.2542 | 314.8352 | 392.6868 | 465.7714 | -204.4722 | -261.4322 | -324.8178 | -388.1901 | -445.5327 | -498.9431 | -550.8415 | -611.8881 | -674.2717 | -730.4092
28222 | 62.3267 | 122.33 | 191.2193 | 265.9866 | 340.7338 | 421.3293 | 509.8485 | 695.5428 | 853.726 | 1002.108 | -615.6336 | -747.8365 | -888.9571 | -1023.4595 | -1139.2558 | -1242.0263 | -1337.167 | -1443.9557 | -1549.9558 | -1642.2763
28223 | 63.8397 | 129.6632 | 206.5243 | 291.5673 | 377.9126 | 472.0721 | 576.2551 | 798.2043 | 987.1764 | 1164.1078 | -689.8868 | -839.5204 | -1002.3407 | -1160.949 | -1300.5987 | -1427.2263 | -1546.9865 | -1683.6625 | -1820.0116 | -1941.3106
28224 | 25.8095 | 54.1047 | 87.8395 | 126.0633 | 165.6212 | 209.3654 | 258.7881 | 364.9489 | 455.195 | 539.9156 | -236.9886 | -303.0129 | -376.4863 | -449.9453 | -516.4159 | -578.3292 | -638.4907 | -709.2577 | -781.5758 | -846.6538
28225 | 0.34404 | 0.7245 | 1.1747 | 1.6801 | 2.1991 | 2.7695 | 3.4086 | 4.7796 | 5.9414 | 7.0294 | -3.3391 | -4.2213 | -5.1959 | -6.1621 | -7.0287 | -7.829 | -8.5999 | -9.5008 | -10.4123 | -11.226
28228 | 20.2518 | 42.454 | 68.9245 | 98.9173 | 129.957 | 164.2815 | 203.0617 | 286.3622 | 357.1751 | 423.6523 | -185.9564 | -237.7633 | -295.4152 | -353.0559 | -405.2129 | -453.7941 | -501.0006 | -556.5289 | -613.2743 | -664.3387
28229 | 2.0062 | 4.2056 | 6.8279 | 9.799 | 12.8739 | 16.2742 | 20.1159 | 28.3679 | 35.3828 | 41.9682 | -18.4214 | -23.5535 | -29.2647 | -34.9747 | -40.1416 | -44.9542 | -49.6306 | -55.1314 | -60.7527 | -65.8113
28231 | 36.4565 | 76.7813 | 124.4874 | 178.0361 | 233.0139 | 293.4252 | 361.0916 | 506.2714 | 629.2812 | 744.4629 | -354.2775 | -447.7725 | -551.0291 | -653.3825 | -745.1619 | -829.9069 | -911.5264 | -1006.8873 | -1103.3355 | -1189.4308
28232 | 73.264 | 139.4555 | 216.236 | 300.5974 | 385.8211 | 478.4756 | 580.8478 | 796.7562 | 981.5833 | 1155.2704 | -658.4493 | -806.7422 | -966.8125 | -1121.272 | -1255.946 | -1376.8763 | -1490.144 | -1617.6059 | -1745.9282 | -1858.8748
29481 | 15.277 | 31.3917 | 50.2333 | 71.183 | 92.5675 | 116.0292 | 142.1094 | 198.0035 | 245.4551 | 289.9295 | -177.3561 | -213.6146 | -252.9709 | -291.17 | -324.6696 | -354.8953 | -383.344 | -415.2256 | -447.0907 | -475.3514
29482 | 6.8795 | 13.7482 | 21.6693 | 30.3793 | 39.2105 | 48.8853 | 59.6426 | 82.6146 | 102.0133 | 120.2378 | -93.7735 | -108.6684 | -124.4816 | -139.4034 | -152.0861 | -163.1423 | -173.1777 | -183.6356 | -194.1343 | -202.8509
29483 | 39.0326 | 78.0041 | 122.9466 | 172.3649 | 222.4709 | 277.3633 | 338.398 | 468.7353 | 578.7991 | 682.2004 | -532.0484 | -616.5583 | -706.2786 | -790.941 | -862.9 | -925.6303 | -982.5683 | -1041.9042 | -1101.4714 | -1150.9269
29485 | 0.048791 | 0.097505 | 0.15368 | 0.21546 | 0.27809 | 0.3467 | 0.423 | 0.58592 | 0.7235 | 0.85275 | -0.66506 | -0.7707 | -0.88285 | -0.98868 | -1.0786 | -1.157 | -1.2282 | -1.3024 | -1.3768 | -1.4387
29486 | 2.2932 | 4.5827 | 7.2231 | 10.1264 | 13.0702 | 16.2951 | 19.8809 | 27.5382 | 34.0044 | 40.0793 | -31.2578 | -36.2228 | -41.4939 | -46.4678 | -50.6954 | -54.3808 | -57.7259 | -61.2119 | -64.7114 | -67.617
29488 | 23.9902 | 47.1278 | 73.8342 | 103.2569 | 133.1488 | 165.9661 | 202.5171 | 280.7375 | 346.8058 | 408.9295 | -301.9917 | -352.1053 | -405.2966 | -455.4494 | -498.0268 | -535.0718 | -568.6208 | -603.1963 | -638.0518 | -667.1025
29489 | 10.5876 | 21.1586 | 33.3493 | 46.754 | 60.3452 | 75.2348 | 91.7904 | 127.1444 | 156.9992 | 185.0469 | -144.3181 | -167.2414 | -191.5781 | -214.5427 | -234.0616 | -251.0772 | -266.5217 | -282.6165 | -298.7741 | -312.1889
29490 | 16.9304 | 33.8343 | 53.3281 | 74.7633 | 96.4967 | 120.3063 | 146.7801 | 203.3139 | 251.0541 | 295.9044 | -230.776 | -267.4322 | -306.3483 | -343.0707 | -374.2829 | -401.4921 | -426.189 | -451.926 | -477.7632 | -499.2146
29491 | 2.7323 | 5.4603 | 8.6063 | 12.0655 | 15.573 | 19.4154 | 23.6879 | 32.8115 | 40.5159 | 47.754 | -37.2434 | -43.1591 | -49.4395 | -55.3659 | -60.403 | -64.7941 | -68.7798 | -72.9333 | -77.103 | -80.5649
30603 | 62.9696 | 120.6693 | 188.7139 | 266.0489 | 346.8293 | 437.7382 | 540.8313 | 765.8745 | 956.5854 | 1137.5282 | -604.8902 | -732.0897 | -869.0429 | -999.6907 | -1111.6555 | -1209.344 | -1297.9049 | -1382.2985 | -1471.6844 | -1548.4242
30604 | 31.8835 | 61.098 | 95.5489 | 134.7015 | 175.5966 | 221.6177 | 273.8054 | 387.7237 | 484.2617 | 575.8536 | -306.2996 | -370.7 | -440.0361 | -506.1769 | -562.857 | -612.3077 | -657.1359 | -699.8537 | -745.096 | -783.9346
30605 | 54.4566 | 103.9869 | 161.748 | 226.4396 | 293.1923 | 367.5421 | 451.2015 | 632.45 | 785.5286 | 930.0572 | -534.4148 | -642.1614 | -756.9295 | -865.0155 | -956.4759 | -1035.252 | -1105.6543 | -1172.3344 | -1241.7765 | -1300.0311
30606 | 57.8249 | 111.9631 | 175.5733 | 247.5365 | 322.4347 | 406.4963 | 501.6687 | 709.0606 | 885.0153 | 1051.9465 | -540.9623 | -659.7849 | -787.2778 | -908.4336 | -1011.8477 | -1101.7245 | -1182.8655 | -1259.8861 | -1341.6015 | -1411.5142
30607 | 196.8105 | 273.5744 | 363.7468 | 465.887 | 572.3698 | 692.1412 | 827.9812 | 1124.7405 | 1376.4053 | 1615.3803 | -873.2856 | -1040.857 | -1220.2165 | -1390.0261 | -1534.3163 | -1658.9767 | -1770.768 | -1874.3999 | -1987.5598 | -2081.5126
30608 | 42.3118 | 81.0825 | 126.8044 | 178.7689 | 233.0485 | 294.1338 | 363.4062 | 514.6218 | 642.7681 | 764.3508 | -406.45 | -491.9204 | -583.9447 | -671.7322 | -746.9659 | -812.6066 | -872.1143 | -928.8217 | -988.8837 | -1040.4482
31002 | 22.521 | 43.3033 | 67.7834 | 95.565 | 124.5502 | 157.1399 | 194.076 | 274.6541 | 342.9593 | 407.7596 | -214.8826 | -260.64 | -309.8547 | -356.7482 | -396.8873 | -431.8672 | -463.5386 | -493.6905 | -525.6156 | -553.0244
31007 | 51.3321 | 102.443 | 162.1674 | 229.0263 | 297.9106 | 374.4 | 460.197 | 645.2262 | 801.5278 | 948.7258 | -520.6038 | -633.1526 | -753.5849 | -867.5119 | -964.4188 | -1048.3068 | -1123.6271 | -1196.081 | -1271.0809 | -1334.2363
31008 | 53.7978 | 107.3385 | 170.3623 | 241.7037 | 315.9261 | 399.0779 | 492.9753 | 696.9925 | 869.4131 | 1032.3602 | -535.899 | -654.1428 | -781.3369 | -902.3988 | -1005.9674 | -1096.103 | -1177.5314 | -1255.2341 | -1336.7229 | -1406.2062
31010 | 24.3332 | 48.1738 | 75.9458 | 106.9182 | 138.7308 | 173.9696 | 213.4274 | 298.3874 | 370.1003 | 437.5697 | -246.8396 | -299.0922 | -354.8244 | -407.3505 | -451.8606 | -490.2454 | -524.5686 | -557.4982 | -591.4539 | -619.8606
32374 | 48.7997 | 96.8625 | 153.3031 | 216.2173 | 280.508 | 351.0077 | 429.3285 | 596.8468 | 739.6 | 873.434 | -457.2893 | -567.3013 | -687.5657 | -805.2448 | -909.2794 | -1003.8866 | -1093.5912 | -1195.2805 | -1297.9974 | -1388.9555
32377 | 15.5771 | 30.9189 | 48.935 | 69.0174 | 89.5393 | 112.0431 | 137.0434 | 190.516 | 236.0834 | 278.8038 | -145.9686 | -181.0849 | -219.4738 | -257.0375 | -290.2458 | -320.4448 | -349.0789 | -381.5385 | -414.3262 | -443.3604
32379 | 63.5068 | 126.0964 | 199.5397 | 281.3093 | 364.7747 | 456.2037 | 557.693 | 774.6677 | 959.4947 | 1132.7068 | -593.6419 | -736.8867 | -893.417 | -1046.5361 | -1181.8705 | -1304.9389 | -1421.6317 | -1554.2022 | -1687.9659 | -1806.3553
33271 | 1248.201 | 1347.6605 | 1465.3356 | 1600.5337 | 1743.3344 | 1905.9843 | 2092.0611 | 2503.2357 | 2850.0032 | 3180.0033 | -2273.0514 | -2488.5914 | -2719.2892 | -2937.0321 | -3121.1412 | -3278.7873 | -3418.6547 | -3540.259 | -3673.6847 | -3782.0001
33272 | 508.4013 | 588.3939 | 681.4581 | 784.8901 | 890.7233 | 1007.5357 | 1138.1406 | 1418.4411 | 1656.2197 | 1880.4265 | -1283.1685 | -1459.7962 | -1649.0866 | -1829.4336 | -1984.1886 | -2120.2533 | -2244.782 | -2375.0189 | -2508.1019 | -2620.6457
33273 | 0.28553 | 0.57541 | 0.9077 | 1.2658 | 1.621 | 2.0002 | 2.4135 | 3.2727 | 4.011 | 4.699 | -2.9712 | -3.6203 | -4.3163 | -4.9842 | -5.5637 | -6.0831 | -6.569 | -7.1327 | -7.6864 | -8.1743
33274 | 67.9583 | 136.9488 | 216.035 | 301.2777 | 385.8138 | 476.089 | 574.4811 | 779.0275 | 954.7802 | 1118.5774 | -706.9101 | -861.4084 | -1027.0751 | -1186.064 | -1324.0323 | -1447.713 | -1563.3994 | -1697.6367 | -1829.5036 | -1945.687
33275 | 4.7968 | 9.6669 | 15.2493 | 21.2659 | 27.2323 | 33.6034 | 40.5473 | 54.9814 | 67.3843 | 78.9435 | -49.9162 | -60.8212 | -72.5136 | -83.7339 | -93.4698 | -102.1968 | -110.3591 | -119.8294 | -129.1322 | -137.3282
33276 | 362.8909 | 464.9038 | 582.4848 | 712.4897 | 845.3413 | 992.303 | 1156.9384 | 1512.343 | 1812.0929 | 2094.7054 | -1389.9274 | -1604.9033 | -1830.6566 | -2039.7859 | -2213.7764 | -2361.0646 | -2490.2666 | -2611.9995 | -2739.8412 | -2842.543
34251 | 37.1439 | 74.4729 | 117.5951 | 164.4042 | 211.0464 | 260.9547 | 315.3781 | 429.9249 | 527.5069 | 618.2838 | -362.0461 | -447.2683 | -539.667 | -629.5497 | -708.6771 | -780.6667 | -849.0071 | -930.1166 | -1010.013 | -1080.7703
34252 | 68.9024 | 136.7654 | 216.4566 | 305.2865 | 396.0584 | 495.595 | 606.1725 | 842.682 | 1044.2265 | 1233.1775 | -645.6753 | -801.0087 | -970.8176 | -1136.9759 | -1283.8687 | -1417.4509 | -1544.1115 | -1687.7002 | -1832.7372 | -1961.1707
34253 | 36.3397 | 72.7046 | 114.7745 | 160.4742 | 206.0142 | 254.7081 | 307.7625 | 419.6948 | 514.8492 | 603.2909 | -364.9698 | -448.449 | -539.2109 | -627.8164 | -706.1172 | -777.6461 | -845.8245 | -927.3938 | -1007.4611 | -1078.7098
34254 | 0.038243 | 0.075287 | 0.11753 | 0.16269 | 0.20714 | 0.25426 | 0.30536 | 0.41054 | 0.50108 | 0.58592 | -0.80901 | -0.89167 | -0.98002 | -1.0646 | -1.1377 | -1.2032 | -1.2644 | -1.336 | -1.4062 | -1.467
34256 | 41.9874 | 83.9233 | 132.6049 | 185.7885 | 239.0798 | 296.376 | 359.0684 | 491.8462 | 604.7006 | 709.7781 | -398.8041 | -495.1145 | -599.9999 | -702.5092 | -793.1664 | -875.9648 | -954.8556 | -1048.3524 | -1140.875 | -1222.9189
34259 | 68.9426 | 137.8237 | 217.4566 | 303.8947 | 389.9812 | 481.9935 | 582.224 | 793.4138 | 973.1206 | 1140.1743 | -730.3406 | -888.251 | -1059.8024 | -1227.1249 | -1374.8515 | -1509.6818 | -1638.0859 | -1791.5646 | -1941.6565 | -2075.6838
34260 | 17.0343 | 33.7884 | 53.4164 | 75.2242 | 97.4461 | 121.7542 | 148.713 | 206.206 | 255.2633 | 301.2383 | -176.2977 | -214.5674 | -256.3294 | -297.1228 | -333.1286 | -365.8331 | -396.8092 | -432.0055 | -467.2498 | -498.6629
34261 | 16.1681 | 32.092 | 50.7916 | 71.636 | 92.9365 | 116.2941 | 142.2429 | 197.7442 | 245.0405 | 289.3817 | -151.5067 | -187.9554 | -227.8008 | -266.7896 | -301.2578 | -332.6026 | -362.323 | -396.0142 | -430.0459 | -460.1816
34262 | 10.9216 | 21.6764 | 34.3021 | 48.3701 | 62.7408 | 78.4946 | 95.9923 | 133.404 | 165.2901 | 195.1826 | -103.6953 | -128.3057 | -155.2038 | -181.5178 | -204.7761 | -225.9237 | -245.9727 | -268.7069 | -291.6459 | -311.9753
34263 | 36.6547 | 72.7938 | 115.0768 | 161.9417 | 209.5825 | 261.5688 | 319.1146 | 441.7319 | 546.2934 | 644.1954 | -373.0356 | -455.6612 | -545.8053 | -633.873 | -711.6341 | -782.3294 | -849.3538 | -926.0159 | -1002.6648 | -1070.9062
34264 | 134.2159 | 177.7638 | 228.8138 | 286.2351 | 345.6378 | 411.8734 | 486.481 | 648.0101 | 784.992 | 914.5717 | -546.2102 | -642.3889 | -745.7958 | -844.495 | -929.237 | -1003.5374 | -1071.2953 | -1139.2144 | -1210.9892 | -1271.6071
37002 | 6.8321 | 13.6258 | 22.3113 | 33.6734 | 47.0137 | 63.6478 | 83.8393 | 131.6004 | 171.3398 | 209.9263 | -57.4576 | -70.9682 | -85.4662 | -98.69 | -109.2056 | -117.0688 | -122.8257 | -120.0108 | -120.5847 | -119.7666
38422 | 0.26215 | 0.50237 | 0.78565 | 1.1076 | 1.4439 | 1.8224 | 2.2516 | 3.1885 | 3.9825 | 4.7358 | -2.5183 | -3.0478 | -3.618 | -4.1619 | -4.628 | -5.0347 | -5.4034 | -5.7548 | -6.1269 | -6.4464
39010 | 35.0987 | 70.0005 | 114.6215 | 172.9927 | 241.5262 | 326.982 | 430.713 | 676.079 | 880.2346 | 1078.4678 | -295.1807 | -364.5896 | -439.0707 | -507.0063 | -561.029 | -601.4248 | -631.0002 | -616.5388 | -619.4874 | -615.2846
39011 | 29.5055 | 58.8454 | 96.3556 | 145.4249 | 203.037 | 274.8747 | 362.0753 | 568.3402 | 739.9619 | 906.605 | -248.1412 | -306.4892 | -369.1012 | -426.2107 | -471.6244 | -505.5828 | -530.4451 | -518.2882 | -520.767 | -517.2339
39012 | 20.9091 | 41.7009 | 68.2825 | 103.0555 | 143.8825 | 194.7903 | 256.5852 | 402.7551 | 524.375 | 642.4669 | -175.8456 | -217.194 | -261.564 | -302.0348 | -334.2173 | -358.282 | -375.9007 | -367.2857 | -369.0423 | -366.5385
39013 | 14.0847 | 28.0793 | 45.9558 | 69.3104 | 96.7046 | 130.8371 | 172.2502 | 270.1597 | 351.6339 | 430.7336 | -118.5593 | -146.4211 | -176.3196 | -203.605 | -225.3231 | -241.5991 | -253.5595 | -248.043 | -249.4465 | -247.9797
39565 | 63.403 | 126.4502 | 207.0542 | 312.4969 | 436.2971 | 590.6658 | 778.0473 | 1221.2806 | 1590.0708 | 1948.1626 | -533.2195 | -658.6008 | -793.1448 | -915.8649 | -1013.4524 | -1086.4241 | -1139.8496 | -1113.7262 | -1119.0527 | -1111.4606
39568 | 8.6289 | 17.8798 | 29.146 | 42.6342 | 57.3676 | 74.6165 | 94.7086 | 139.993 | 178.0579 | 214.4637 | -83.4945 | -103.6383 | -125.5705 | -146.5819 | -164.5899 | -180.1129 | -193.9766 | -204.7764 | -217.5027 | -228.1174
39569 | 0.18769 | 0.37433 | 0.61295 | 0.92509 | 1.2916 | 1.7486 | 2.3033 | 3.6154 | 4.7071 | 5.7672 | -1.5785 | -1.9497 | -2.348 | -2.7113 | -3.0002 | -3.2162 | -3.3743 | -3.297 | -3.3128 | -3.2903
39570 | 0.90093 | 1.7968 | 2.9422 | 4.4405 | 6.1996 | 8.3931 | 11.0557 | 17.3539 | 22.5943 | 27.6826 | -7.5768 | -9.3584 | -11.2703 | -13.0141 | -14.4007 | -15.4376 | -16.1968 | -15.8256 | -15.9013 | -15.7934
39571 | 32.6212 | 65.0593 | 106.5305 | 160.7814 | 224.4773 | 303.9009 | 400.3097 | 628.3557 | 818.1004 | 1002.3406 | -274.3444 | -338.8538 | -408.0775 | -471.2176 | -521.4269 | -558.9713 | -586.459 | -573.0184 | -575.7589 | -571.8527
40001 | 12.6805 | 23.7326 | 36.5252 | 50.7033 | 65.1968 | 81.2126 | 99.1423 | 137.76 | 170.4 | 201.1723 | -123.4786 | -147.3262 | -172.6203 | -196.4096 | -216.5307 | -233.9294 | -249.5726 | -265.1123 | -280.9991 | -294.4668
40002 | 36.0994 | 74.2471 | 120.7768 | 177.5774 | 240.9172 | 316.7979 | 406.6562 | 613.6837 | 786.782 | 953.6629 | -353.6572 | -431.7264 | -514.3282 | -589.6556 | -650.1668 | -697.4117 | -734.4812 | -741.003 | -758.9538 | -769.0727
40003 | 5.4521 | 10.6895 | 16.7211 | 23.3388 | 30.0366 | 37.3634 | 45.5045 | 62.8659 | 77.5814 | 91.4174 | -57.32 | -68.6672 | -80.704 | -92.0515 | -101.6872 | -110.0798 | -117.6902 | -125.6149 | -133.598 | -140.4357
41511 | 60.2903 | 124.4506 | 199.7223 | 282.919 | 367.0947 | 458.2473 | 558.9056 | 772.4641 | 954.7464 | 1125.0831 | -574.5162 | -724.1358 | -889.0468 | -1052.4423 | -1199.013 | -1334.7053 | -1465.7389 | -1622.7082 | -1779.9654 | -1921.2106
41512 | 18.9503 | 37.2116 | 58.4389 | 81.9116 | 105.7873 | 131.9472 | 161.0242 | 222.8952 | 275.4969 | 324.9398 | -187.7577 | -228.3463 | -272.0364 | -313.9874 | -350.3399 | -382.7106 | -412.7601 | -445.476 | -478.5225 | -507.4563
41513 | 64.052 | 127.8344 | 202.4631 | 285.6226 | 370.7587 | 464.5353 | 569.1807 | 792.6485 | 983.2176 | 1162.873 | -605.0348 | -748.714 | -904.3435 | -1054.6614 | -1185.5896 | -1302.5764 | -1411.4705 | -1528.6402 | -1648.6241 | -1753.8412
41514 | 35.8221 | 73.8278 | 118.8804 | 170.1715 | 223.7178 | 283.7643 | 351.5972 | 498.7152 | 623.5195 | 741.5179 | -355.4819 | -440.7205 | -533.4695 | -623.1384 | -701.2232 | -770.6273 | -834.8205 | -899.9375 | -968.2241 | -1027.7657
41515 | 116.0733 | 226.2441 | 359.1336 | 515.2979 | 683.0707 | 876.3235 | 1098.6962 | 1592.4582 | 2008.0923 | 2403.2255 | -969.0526 | -1211.4211 | -1475.3084 | -1728.6745 | -1947.0687 | -2137.3252 | -2309.3081 | -2458.9035 | -2626.988 | -2768.8806
41516 | 81.3369 | 161.5727 | 258.4118 | 373.4529 | 498.543 | 644.7065 | 814.7654 | 1198.128 | 1519.7654 | 1827.3546 | -754.5332 | -925.5511 | -1109.1337 | -1281.4954 | -1425.8434 | -1546.6143 | -1650.6734 | -1719.7243 | -1805.139 | -1872.9658
41517 | 92.5484 | 188.6052 | 299.6985 | 420.1508 | 539.9794 | 667.8699 | 807.0977 | 1097.5446 | 1347.6255 | 1580.7354 | -882.3011 | -1103.6728 | -1344.641 | -1580.1707 | -1788.5631 | -1979.1456 | -2160.9785 | -2378.4875 | -2594.0782 | -2786.4122
41518 | 97.9334 | 199.0329 | 316.0301 | 443.0686 | 569.647 | 704.9801 | 852.5195 | 1160.5356 | 1425.7791 | 1673.1742 | -930.8453 | -1163.5737 | -1416.8457 | -1664.2598 | -1883.003 | -2082.8313 | -2273.2675 | -2500.0046 | -2725.0608 | -2925.6924
43505 | 12.0764 | 23.7759 | 38.1174 | 55.6043 | 75.039 | 98.1937 | 125.5031 | 188.0201 | 240.4584 | 290.9178 | -109.6382 | -134.355 | -160.9643 | -185.9036 | -206.6572 | -223.747 | -238.1699 | -245.3543 | -255.7841 | -263.7394
43506 | 65.0302 | 128.0303 | 205.2578 | 299.4222 | 404.0758 | 528.7612 | 675.8191 | 1012.4656 | 1294.8398 | 1566.5573 | -590.3886 | -723.4856 | -866.7734 | -1001.0683 | -1112.8241 | -1204.8508 | -1282.5162 | -1321.2035 | -1377.3668 | -1420.2048
43507 | 64.9057 | 127.7852 | 204.8648 | 298.849 | 403.3022 | 527.7489 | 674.5253 | 1010.5272 | 1292.3609 | 1563.5581 | -589.2583 | -722.1005 | -865.1139 | -999.1518 | -1110.6937 | -1202.5441 | -1280.0608 | -1318.674 | -1374.7299 | -1417.4858
45001 | 6.7945 | 13.5509 | 22.1888 | 33.4884 | 46.7553 | 63.2981 | 83.3787 | 130.8773 | 170.3984 | 208.7729 | -57.1419 | -70.5783 | -84.9966 | -98.1477 | -108.6056 | -116.4256 | -122.1508 | -119.3514 | -119.9222 | -119.1086
45002 | 26.3962 | 54.6462 | 89.0929 | 130.4365 | 175.6975 | 228.7958 | 290.7339 | 430.5767 | 548.0716 | 660.5041 | -254.3714 | -315.7305 | -382.5027 | -446.3783 | -501.0147 | -547.9561 | -589.7157 | -621.3581 | -659.1009 | -690.4122
45003 | 30.1436 | 60.1181 | 98.4396 | 148.5702 | 207.4284 | 280.8198 | 369.9065 | 580.6325 | 755.9662 | 926.2135 | -253.5081 | -313.1181 | -377.0843 | -435.429 | -481.8249 | -516.5178 | -541.9178 | -529.498 | -532.0304 | -528.4209
48180 | 46.7069 | 96.3603 | 154.8802 | 221.1331 | 290.0089 | 367.0522 | 453.972 | 642.4807 | 801.9002 | 952.4004 | -472.9787 | -582.9526 | -701.9206 | -816.4181 | -915.6954 | -1003.7379 | -1085.0641 | -1168.593 | -1255.3829 | -1330.5152
48181 | 2.9944 | 6.2268 | 10.1462 | 14.7984 | 19.8412 | 25.7026 | 32.496 | 47.7133 | 60.5215 | 72.7474 | -29.3356 | -36.4277 | -44.1584 | -51.5923 | -57.9977 | -63.5694 | -68.5985 | -72.8209 | -77.6341 | -81.7028
48182 | 57.9983 | 120.6079 | 196.5229 | 286.6304 | 384.3056 | 497.834 | 629.4167 | 924.161 | 1172.2448 | 1409.0474 | -568.2019 | -705.5701 | -855.3063 | -999.2934 | -1123.3609 | -1231.2795 | -1328.6871 | -1410.4718 | -1503.6983 | -1582.506
48183 | 55.9269 | 114.9114 | 184.4913 | 263.7553 | 346.7503 | 440.3859 | 546.7432 | 779.5363 | 976.1994 | 1162.6447 | -586.9196 | -715.5856 | -853.8841 | -985.5887 | -1098.312 | -1196.5496 | -1285.5554 | -1370.1075 | -1459.8697 | -1536.6338
48184 | 44.3097 | 92.1423 | 150.1401 | 218.9807 | 293.6029 | 380.3366 | 480.8635 | 706.0431 | 895.5748 | 1076.4879 | -434.0965 | -539.0435 | -653.4393 | -763.443 | -858.2284 | -940.6763 | -1015.0941 | -1077.5762 | -1148.7996 | -1209.0074
48185 | 44.6564 | 92.796 | 151.2128 | 220.6586 | 296.041 | 383.7721 | 485.5463 | 713.774 | 905.82 | 1089.1944 | -435.9901 | -541.4752 | -656.4397 | -766.9251 | -862.0446 | -944.662 | -1019.1064 | -1080.871 | -1151.651 | -1211.3495
48188 | 23.9907 | 49.8888 | 81.2906 | 118.5632 | 158.966 | 205.9264 | 260.3549 | 382.2744 | 484.8929 | 582.845 | -235.0337 | -291.8554 | -353.7929 | -413.3525 | -464.6723 | -509.3123 | -549.6044 | -583.4342 | -621.9969 | -654.5953
48189 | 20.1408 | 41.8829 | 68.2455 | 99.5367 | 133.4558 | 172.8803 | 218.5743 | 320.9287 | 407.0795 | 489.3127 | -197.3166 | -245.0198 | -297.0178 | -347.0195 | -390.1038 | -427.5801 | -461.4064 | -489.8073 | -522.1817 | -549.5488
48190 | 39.1409 | 81.3936 | 132.6257 | 193.4359 | 259.3531 | 335.9691 | 424.7692 | 623.6809 | 791.1031 | 950.9121 | -383.4577 | -476.1623 | -577.2134 | -674.3848 | -758.1133 | -830.9434 | -896.6801 | -951.8734 | -1014.7884 | -1067.9727
48191 | 17.2632 | 35.7042 | 57.8023 | 83.5799 | 111.1237 | 142.751 | 179.1105 | 259.8069 | 327.8271 | 392.577 | -174.3178 | -214.6907 | -258.442 | -300.351 | -336.3711 | -367.742 | -396.1173 | -421.3298 | -449.1495 | -472.7974
48192 | 72.6474 | 147.8779 | 234.5767 | 329.5897 | 425.5781 | 530.2926 | 646.375 | 893.0202 | 1102.3615 | 1298.9493 | -795.2005 | -959.2868 | -1133.9715 | -1299.5332 | -1441.0275 | -1565.266 | -1678.9351 | -1800.4512 | -1922.2518 | -2027.7845
49101 | 27.5198 | 57.2276 | 93.2487 | 136.0041 | 182.3503 | 236.2187 | 298.6538 | 438.5079 | 556.2219 | 668.583 | -269.6078 | -334.788 | -405.8368 | -474.1576 | -533.0268 | -584.2334 | -630.4526 | -669.2589 | -713.4942 | -750.8879
49302 | 0.037539 | 0.074867 | 0.12259 | 0.18502 | 0.25832 | 0.34971 | 0.46066 | 0.72308 | 0.94143 | 1.1534 | -0.3157 | -0.38994 | -0.46959 | -0.54225 | -0.60003 | -0.64324 | -0.67487 | -0.6594 | -0.66255 | -0.65806
49303 | 10.5484 | 21.0376 | 34.4477 | 51.9903 | 72.587 | 98.2694 | 129.4442 | 203.1852 | 264.5411 | 324.1171 | -88.7121 | -109.5718 | -131.956 | -152.373 | -168.6087 | -180.7491 | -189.6375 | -185.2913 | -186.1775 | -184.9144
49304 | 0.037539 | 0.074867 | 0.12259 | 0.18502 | 0.25832 | 0.34971 | 0.46066 | 0.72308 | 0.94143 | 1.1534 | -0.3157 | -0.38994 | -0.46959 | -0.54225 | -0.60003 | -0.64324 | -0.67487 | -0.6594 | -0.66255 | -0.65806
49307 | 0.488 | 0.97327 | 1.5937 | 2.4052 | 3.3581 | 4.5463 | 5.9885 | 9.4 | 12.2386 | 14.9947 | -4.1041 | -5.0692 | -6.1047 | -7.0493 | -7.8004 | -8.3621 | -8.7733 | -8.5722 | -8.6132 | -8.5548
49411 | 2.3649 | 4.7166 | 7.7232 | 11.6562 | 16.274 | 22.0319 | 29.0213 | 45.554 | 59.3099 | 72.6668 | -19.8892 | -24.5659 | -29.5844 | -34.1619 | -37.802 | -40.5238 | -42.5166 | -41.5422 | -41.7409 | -41.4577
49412 | 0.97601 | 1.9465 | 3.1873 | 4.8105 | 6.7162 | 9.0925 | 11.977 | 18.8001 | 24.4771 | 29.9895 | -8.2082 | -10.1383 | -12.2095 | -14.0986 | -15.6008 | -16.7241 | -17.5465 | -17.1444 | -17.2264 | -17.1095
49621 | 1.5391 | 3.0695 | 5.0262 | 7.5858 | 10.591 | 14.3382 | 18.8869 | 29.6462 | 38.5985 | 47.2911 | -12.9438 | -15.9873 | -19.2534 | -22.2324 | -24.6013 | -26.3726 | -27.6695 | -27.0354 | -27.1647 | -26.9804
49801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51001 | 0.29553 | 0.53156 | 0.82427 | 1.1863 | 1.5925 | 2.0794 | 2.6548 | 3.975 | 5.0756 | 6.1315 | -3.2358 | -3.7341 | -4.2744 | -4.7829 | -5.2083 | -5.5592 | -5.8558 | -5.9953 | -6.2016 | -6.3477
51002 | 2.8896 | 5.1975 | 8.0595 | 11.5991 | 15.5715 | 20.3323 | 25.9583 | 38.8666 | 49.6284 | 59.952 | -31.6386 | -36.5115 | -41.7944 | -46.766 | -50.9253 | -54.3569 | -57.2572 | -58.6205 | -60.6376 | -62.0663
51003 | 17.994 | 33.3158 | 52.4342 | 76.4775 | 103.8628 | 137.1541 | 176.8777 | 269.1456 | 345.8027 | 419.6095 | -187.1562 | -218.5335 | -252.1777 | -283.1642 | -308.3229 | -328.0646 | -343.6417 | -345.1756 | -351.9717 | -355.1197
51004 | 28.2016 | 53.286 | 83.2347 | 118.0037 | 155.0082 | 197.3393 | 245.8154 | 353.048 | 442.9999 | 528.2716 | -306.7346 | -361.4204 | -420.3322 | -476.161 | -523.5947 | -564.2557 | -600.3255 | -630.5434 | -663.7413 | -690.6246
53001 | 53.8012 | 108.7759 | 171.5019 | 238.6647 | 304.8924 | 375.2152 | 451.4354 | 608.6186 | 742.4717 | 866.5912 | -546.0201 | -668.4488 | -798.8351 | -922.5205 | -1028.5786 | -1122.2313 | -1208.3348 | -1305.5269 | -1400.3216 | -1482.393
53002 | 0.064896 | 0.11941 | 0.18517 | 0.26422 | 0.35132 | 0.45465 | 0.57613 | 0.85426 | 1.0857 | 1.3076 | -0.54485 | -0.6562 | -0.77303 | -0.87848 | -0.9623 | -1.0269 | -1.0767 | -1.085 | -1.1068 | -1.1168
53003 | 100.8161 | 193.1542 | 300.5979 | 418.7146 | 537.9083 | 667.0179 | 808.9502 | 1106.3971 | 1359.5785 | 1595.8665 | -1015.5431 | -1225.5696 | -1453.2046 | -1673.2007 | -1865.3565 | -2037.7601 | -2198.804 | -2378.9166 | -2557.4051 | -2713.53
53004 | 34.0045 | 68.6935 | 108.2861 | 150.7009 | 192.5457 | 236.9997 | 285.1995 | 384.6461 | 469.3243 | 547.8564 | -344.9594 | -422.2206 | -504.5186 | -582.599 | -649.56 | -708.6907 | -763.0562 | -824.3682 | -884.1902 | -935.9867
53006 | 0.093654 | 0.17943 | 0.27924 | 0.38896 | 0.49967 | 0.6196 | 0.75143 | 1.0277 | 1.2629 | 1.4823 | -0.94324 | -1.1383 | -1.3498 | -1.5542 | -1.7327 | -1.8929 | -2.0425 | -2.2098 | -2.3756 | -2.5207
53007 | 0.14048 | 0.26914 | 0.41885 | 0.58343 | 0.74951 | 0.9294 | 1.1271 | 1.5416 | 1.8943 | 2.2235 | -1.4149 | -1.7075 | -2.0247 | -2.3313 | -2.599 | -2.8393 | -3.0637 | -3.3147 | -3.5635 | -3.7811
53008 | 82.0496 | 151.461 | 235.0099 | 334.9657 | 444.6277 | 574.2052 | 726.1427 | 1072.8716 | 1361.5852 | 1638.2684 | -701.8383 | -844.435 | -994.3011 | -1130.0938 | -1238.6641 | -1323.2942 | -1389.5253 | -1406.5734 | -1439.7654 | -1457.7045
53009 | 87.1494 | 172.6329 | 270.8659 | 377.0727 | 482.7088 | 595.7258 | 718.886 | 974.4536 | 1191.8845 | 1393.8405 | -881.8639 | -1073.7034 | -1279.334 | -1475.7537 | -1645.3546 | -1796.0286 | -1935.4059 | -2092.1802 | -2245.9062 | -2379.7595
53010 | 2.0604 | 3.9474 | 6.1432 | 8.557 | 10.9928 | 13.6311 | 16.5315 | 22.6095 | 27.7832 | 32.6115 | -20.7513 | -25.0436 | -29.6958 | -34.1919 | -38.1191 | -41.6427 | -44.9343 | -48.6159 | -52.2642 | -55.4555
54003 | 80.8599 | 159.8866 | 257.1825 | 376.5165 | 509.6782 | 668.6719 | 856.1669 | 1285.6342 | 1643.7071 | 1987.0836 | -664.8435 | -830.9907 | -1009.9143 | -1176.9819 | -1315.479 | -1428.5147 | -1522.713 | -1563.8403 | -1627.8497 | -1673.3788
54004 | 5.1568 | 10.876 | 17.6702 | 25.5202 | 33.8516 | 43.3738 | 54.2802 | 78.4254 | 98.7151 | 117.9862 | -62.6876 | -75.0648 | -88.3034 | -100.7252 | -111.1518 | -119.953 | -127.6158 | -133.6024 | -140.3234 | -145.6288
54005 | 88.1289 | 160.2501 | 244.7802 | 340.8161 | 441.3855 | 555.1491 | 684.5608 | 969.2427 | 1208.0792 | 1434.2801 | -793.3404 | -946.8434 | -1109.0262 | -1259.2562 | -1383.72 | -1487.5252 | -1576.7143 | -1646.7847 | -1723.748 | -1784.2007
54006 | 4.1605 | 8.7029 | 14.0983 | 20.3314 | 26.946 | 34.5055 | 43.1637 | 62.3313 | 78.4382 | 93.7363 | -49.8989 | -59.7269 | -70.2373 | -80.0972 | -88.3718 | -95.3547 | -101.4328 | -106.178 | -111.5057 | -115.7103
54007 | 37.5418 | 79.1772 | 128.6388 | 185.7871 | 246.4397 | 315.7614 | 395.1596 | 570.9371 | 718.646 | 858.9394 | -456.366 | -546.4718 | -642.8491 | -733.2792 | -809.1851 | -873.2577 | -929.0428 | -972.6258 | -1021.5547 | -1060.1777
55001 | 75.6986 | 104.39 | 139.2976 | 181.4667 | 228.0013 | 283.1141 | 347.7907 | 495.2424 | 618.3075 | 736.1542 | -330.2907 | -390.303 | -454.3752 | -513.7013 | -562.462 | -601.9624 | -634.5826 | -649.1814 | -671.6901 | -687.0256
55002 | 187.1135 | 217.5038 | 257.8027 | 313.8279 | 382.5186 | 471.1072 | 580.7589 | 845.9621 | 1064.8364 | 1278.304 | -429.7625 | -484.982 | -543.1135 | -592.9408 | -628.653 | -649.2981 | -657.0598 | -603.3245 | -571.1314 | -532.4133
55003 | 23.2417 | 31.0086 | 40.8221 | 53.4002 | 67.9396 | 85.8283 | 107.3448 | 157.7239 | 199.675 | 240.2437 | -83.5189 | -99.2423 | -116.1345 | -131.6305 | -144.1085 | -153.6951 | -161.0182 | -160.0235 | -162.4688 | -163.0902
56001 | 3.0425 | 6.2843 | 10.317 | 15.4147 | 21.2607 | 28.4297 | 37.0408 | 57.2227 | 73.9765 | 90.1663 | -27.8287 | -34.2559 | -41.0112 | -47.0215 | -51.6646 | -55.005 | -57.2902 | -55.7576 | -55.5027 | -54.5659
56002 | 1.8896 | 3.9029 | 6.4074 | 9.5733 | 13.204 | 17.6564 | 23.0043 | 35.5383 | 45.9433 | 55.998 | -17.2831 | -21.2747 | -25.4701 | -29.2028 | -32.0864 | -34.161 | -35.5802 | -34.6284 | -34.4701 | -33.8883
56003 | 17.4494 | 36.1803 | 59.5566 | 89.0997 | 122.9245 | 164.2851 | 213.8514 | 329.6149 | 425.796 | 518.6337 | -135.6884 | -173.4517 | -213.5697 | -249.8885 | -278.6474 | -300.2502 | -316.1685 | -311.9251 | -315.2371 | -314.1675
56004 | 53.7373 | 106.4093 | 174.2584 | 264.5873 | 372.0734 | 507.6145 | 673.1255 | 1067.925 | 1393.9554 | 1710.2482 | -426.8565 | -527.4909 | -633.7844 | -727.3112 | -797.7701 | -844.8232 | -872.398 | -816.5007 | -789.5301 | -751.2028
57003 | 24.6598 | 49.4408 | 79.5887 | 115.9301 | 155.9433 | 203.2192 | 258.6053 | 384.5858 | 489.8027 | 590.5253 | -216.1163 | -268.4341 | -324.4466 | -376.5142 | -419.5008 | -454.5454 | -483.7062 | -497.8861 | -518.1148 | -532.6502
57004 | 94.1464 | 188.7034 | 303.764 | 442.5147 | 595.3326 | 775.9393 | 987.5729 | 1469.0604 | 1871.197 | 2256.1967 | -824.5172 | -1024.1071 | -1237.7994 | -1436.438 | -1600.4195 | -1734.0769 | -1845.2643 | -1899.0609 | -1976.0488 | -2031.3247
57005 | 12.0565 | 24.1966 | 38.9807 | 56.8365 | 76.5291 | 99.8314 | 127.1593 | 189.3954 | 241.3612 | 291.1264 | -105.2044 | -130.7893 | -158.1729 | -183.603 | -204.5665 | -221.6101 | -235.7397 | -242.3061 | -251.9109 | -258.7247
57006 | 143.9197 | 294.0253 | 470.7652 | 670.6773 | 878.4505 | 1110.832 | 1372.7557 | 1940.5872 | 2419.9918 | 2872.0596 | -1598.2923 | -1930.618 | -2288.3242 | -2628.6677 | -2919.8294 | -3173.0176 | -3401.4009 | -3618.914 | -3846.2553 | -4037.3675
61021 | 99.2597 | 176.8157 | 266.3377 | 364.5187 | 463.6806 | 571.6217 | 690.8063 | 943.1134 | 1155.3846 | 1353.1755 | -879.0516 | -1049.0745 | -1230.213 | -1401.5286 | -1547.7151 | -1675.5431 | -1791.8087 | -1914.7485 | -2036.4213 | -2140.3129
61023 | 114.8176 | 210.8111 | 321.6007 | 443.6813 | 567.8151 | 704.1891 | 856.0241 | 1181.0626 | 1455.26 | 1712.6867 | -1047.4344 | -1255.29 | -1475.0891 | -1680.3786 | -1852.7777 | -2000.2802 | -2131.0978 | -2257.4704 | -2386.2011 | -2492.933
61024 | 13.8621 | 26.6285 | 41.5984 | 58.2315 | 75.153 | 93.5921 | 113.9485 | 157.5167 | 193.9552 | 227.6778 | -132.2379 | -161.4126 | -193.2493 | -224.2806 | -251.6375 | -276.4247 | -299.8236 | -326.4705 | -352.7485 | -375.7526
61025 | 68.7394 | 132.1667 | 206.585 | 289.3305 | 373.5593 | 465.3818 | 566.8622 | 783.994 | 965.5906 | 1133.6613 | -660.8712 | -805.8961 | -964.2502 | -1118.7126 | -1254.9947 | -1378.5785 | -1495.3432 | -1628.4614 | -1759.7353 | -1874.8009
61026 | 8.7478 | 16.8054 | 26.2542 | 36.7534 | 47.4352 | 59.0754 | 71.9271 | 99.4324 | 122.4367 | 143.7265 | -83.5033 | -101.9179 | -122.0137 | -141.6024 | -158.8727 | -174.5219 | -189.2956 | -206.1216 | -222.7145 | -237.2418
61027 | 93.2808 | 179.2568 | 280.0966 | 392.1731 | 506.2205 | 630.5184 | 767.803 | 1061.5928 | 1307.304 | 1534.7068 | -892.7411 | -1089.2622 | -1303.7688 | -1512.9134 | -1697.3549 | -1864.5295 | -2022.3983 | -2202.2629 | -2379.6363 | -2534.9939
61028 | 154.9692 | 278.3587 | 418.99 | 570.0036 | 719.5347 | 879.2531 | 1053.1917 | 1414.8871 | 1721.0349 | 2005.2505 | -1408.7214 | -1678.8645 | -1964.7424 | -2233.6233 | -2462.0103 | -2661.4666 | -2842.7344 | -3041.7889 | -3235.8349 | -3401.3014
61029 | 30.5675 | 61.8971 | 99.0792 | 141.0234 | 184.2517 | 231.8576 | 285.136 | 399.3977 | 495.3811 | 584.646 | -327.3007 | -399.5323 | -479.2618 | -557.9867 | -628.3529 | -692.9662 | -754.8194 | -825.8376 | -896.8376 | -960.2724
61037 | 36.4386 | 69.9971 | 109.3478 | 153.0704 | 197.5512 | 246.0212 | 299.5313 | 414.057 | 509.8412 | 598.4864 | -347.6079 | -424.2981 | -507.9856 | -589.5563 | -661.4681 | -726.6252 | -788.1328 | -858.1784 | -927.254 | -987.7239
61039 | 26.0623 | 50.0647 | 78.2098 | 109.482 | 141.2964 | 175.964 | 214.2365 | 296.1498 | 364.6584 | 428.0609 | -248.6228 | -303.4746 | -363.3312 | -421.6737 | -473.1079 | -519.7108 | -563.7035 | -613.8028 | -663.2084 | -706.4588
61040 | 46.5501 | 89.4246 | 139.7006 | 195.5643 | 252.3981 | 314.3303 | 382.7058 | 529.0455 | 651.4373 | 764.7074 | -444.2269 | -542.2091 | -649.1343 | -753.3585 | -845.2449 | -928.5035 | -1007.102 | -1096.6154 | -1184.8892 | -1262.17
61041 | 69.7759 | 134.3167 | 210.0979 | 294.4351 | 380.3471 | 474.0557 | 577.7626 | 799.577 | 985.0863 | 1156.7897 | -677.4903 | -825.1605 | -986.5282 | -1144.0773 | -1283.2246 | -1409.5394 | -1529.0172 | -1665.4157 | -1799.9234 | -1918.0119
61043 | 140.1291 | 258.3208 | 396.5352 | 551.3029 | 710.6109 | 887.1295 | 1084.5664 | 1509.2339 | 1865.4533 | 2199.0017 | -1273.4333 | -1533.6468 | -1812.7275 | -2077.9019 | -2304.8504 | -2503.0282 | -2682.8343 | -2863.2741 | -3046.2989 | -3201.4758
62004 | 41.8626 | 87.1544 | 141.2069 | 202.6029 | 266.244 | 336.6542 | 415.9171 | 586.0523 | 729.2365 | 862.6717 | -475.039 | -579.8892 | -696.2299 | -811.7738 | -915.6779 | -1011.6384 | -1104.0453 | -1210.507 | -1317.5408 | -1413.9541
62005 | 23.3328 | 48.5768 | 78.7038 | 112.9239 | 148.3952 | 187.6394 | 231.8178 | 326.6453 | 406.4512 | 480.8234 | -264.7703 | -323.2102 | -388.0545 | -452.4547 | -510.3672 | -563.8523 | -615.3567 | -674.6948 | -734.3517 | -788.0891
62006 | 38.1228 | 76.2433 | 121.3651 | 172.0981 | 224.2383 | 281.5289 | 345.4612 | 482.5128 | 597.5347 | 704.3961 | -397.4977 | -485.2152 | -581.7959 | -676.8926 | -761.6413 | -839.2411 | -913.3084 | -998.2057 | -1082.8419 | -1158.1466
62008 | 38.5638 | 80.2735 | 130.0496 | 186.586 | 245.1879 | 310.0212 | 383.0038 | 539.6576 | 671.4947 | 794.354 | -437.4593 | -534.0149 | -641.1488 | -747.5456 | -843.2208 | -931.5787 | -1016.6618 | -1114.684 | -1213.2299 | -1301.9937
62009 | 32.3059 | 63.6569 | 100.6429 | 142.0556 | 184.4665 | 230.9328 | 282.5941 | 393.2796 | 486.0634 | 572.1507 | -326.1407 | -398.1056 | -477.0931 | -554.5918 | -623.3983 | -686.1726 | -745.8629 | -814.1303 | -881.9378 | -941.9414
62010 | 55.6004 | 115.7487 | 187.5307 | 269.0639 | 353.5776 | 447.0796 | 552.3365 | 778.2665 | 968.4065 | 1145.5997 | -630.8562 | -770.0983 | -924.5983 | -1078.0383 | -1216.0194 | -1343.4502 | -1466.1606 | -1607.534 | -1749.6656 | -1877.6921
62011 | 2.9648 | 6.1724 | 10.0005 | 14.3486 | 18.8558 | 23.8424 | 29.4559 | 41.5051 | 51.6456 | 61.0957 | -33.643 | -41.0686 | -49.3081 | -57.4911 | -64.8497 | -71.6458 | -78.1902 | -85.73 | -93.3103 | -100.1384
62013 | 35.2374 | 72.8719 | 117.7277 | 168.5964 | 221.255 | 279.4526 | 344.8796 | 485.2887 | 603.4057 | 713.429 | -394.3624 | -481.403 | -577.8648 | -673.5373 | -759.4515 | -838.6926 | -914.8961 | -1002.6218 | -1090.7065 | -1169.9048
65060 | 7.8918 | 15.4526 | 24.4235 | 34.5337 | 44.9367 | 56.3804 | 69.2547 | 96.6822 | 119.6145 | 140.8824 | -87.6788 | -105.1422 | -124.4329 | -143.5105 | -160.5944 | -176.3219 | -191.4173 | -208.9589 | -226.2555 | -241.751
65061 | 34.4172 | 67.4171 | 106.5813 | 150.7317 | 196.1708 | 246.1757 | 302.4283 | 422.2826 | 522.4934 | 615.4792 | -383.5109 | -459.7487 | -543.9842 | -627.3132 | -701.9557 | -770.6932 | -836.688 | -913.4059 | -989.0519 | -1056.8493
65062 | 48.5587 | 95.058 | 150.2226 | 212.3826 | 276.3347 | 346.6678 | 425.7956 | 594.3598 | 735.2985 | 865.9667 | -538.5555 | -645.9437 | -764.5519 | -881.831 | -986.8345 | -1083.4847 | -1176.2331 | -1283.9883 | -1390.2384 | -1485.4022
65063 | 19.528 | 37.2552 | 58.0589 | 81.2352 | 104.8822 | 130.7375 | 159.3161 | 220.6564 | 271.9723 | 319.5329 | -185.6725 | -226.023 | -269.9982 | -312.7657 | -350.3681 | -384.3168 | -416.244 | -452.106 | -487.5784 | -518.5472
65064 | 40.4719 | 78.1523 | 122.4828 | 171.9371 | 222.4125 | 277.5481 | 338.7867 | 469.6415 | 579.0733 | 680.3788 | -403.339 | -489.7065 | -584.2801 | -676.8442 | -758.8169 | -833.4357 | -904.2213 | -985.3212 | -1065.2952 | -1135.7983
65065 | 36.1258 | 70.3348 | 110.9498 | 156.8144 | 204.1092 | 256.2106 | 314.9008 | 440.3473 | 545.1855 | 642.4112 | -399.7953 | -478.5683 | -565.5023 | -651.3385 | -728.0593 | -798.5154 | -865.971 | -943.6324 | -1020.3693 | -1089.0212
65066 | 74.5189 | 136.847 | 210.8724 | 297.0323 | 389.2143 | 495.5666 | 618.177 | 892.4497 | 1121.0472 | 1338.3235 | -881.841 | -1013.0696 | -1151.8443 | -1279.8282 | -1384.9711 | -1471.088 | -1543.3391 | -1589.2949 | -1643.9325 | -1682.2818
65067 | 43.1917 | 76.9364 | 118.7076 | 171.3125 | 231.4982 | 305.2221 | 393.6951 | 601.0875 | 772.56 | 938.0373 | -344.212 | -410.1911 | -479.0169 | -539.6705 | -585.9645 | -618.6534 | -640.2901 | -622.3836 | -616.956 | -604.4327
66101 | 27.1163 | 52.0786 | 81.3578 | 113.913 | 147.0572 | 183.2036 | 223.1062 | 308.6158 | 380.125 | 446.3276 | -258.4195 | -315.4267 | -377.6253 | -438.2286 | -491.6311 | -539.985 | -585.5981 | -637.39 | -688.5105 | -733.2342
66102 | 75.6641 | 145.3564 | 227.0807 | 317.8891 | 410.2758 | 510.9509 | 622.1025 | 859.9918 | 1058.9516 | 1243.0832 | -722.1743 | -881.4455 | -1055.256 | -1224.6783 | -1374.0472 | -1509.3933 | -1637.166 | -1782.6857 | -1926.1903 | -2051.8269
66103 | 63.7443 | 122.9131 | 192.461 | 269.9613 | 348.9913 | 435.2607 | 530.9208 | 735.4178 | 906.4393 | 1064.7482 | -627.6979 | -763.2074 | -911.451 | -1056.3798 | -1184.567 | -1301.1065 | -1411.5118 | -1537.7978 | -1662.3317 | -1771.9102
66105 | 51.841 | 99.5844 | 155.5682 | 217.7721 | 281.0546 | 350.0124 | 426.1408 | 589.0756 | 725.347 | 851.4617 | -494.539 | -603.6454 | -722.707 | -838.7569 | -941.0653 | -1033.7638 | -1121.2702 | -1220.9235 | -1319.1968 | -1405.2267
66106 | 60.1951 | 116.6591 | 183.238 | 257.7142 | 333.8942 | 417.2424 | 510.1895 | 708.5864 | 874.493 | 1028.1097 | -617.7202 | -747.4051 | -889.7434 | -1029.4459 | -1153.5366 | -1266.8429 | -1374.6755 | -1498.7075 | -1621.0145 | -1729.3256
66107 | 23.3467 | 44.848 | 70.0604 | 98.0741 | 126.5734 | 157.6287 | 191.9133 | 265.2913 | 326.6613 | 383.4574 | -222.7165 | -271.8528 | -325.4724 | -377.7357 | -423.8105 | -465.5574 | -504.9661 | -549.8451 | -594.1027 | -632.8464
66108 | 0.081065 | 0.15572 | 0.24327 | 0.34053 | 0.43949 | 0.54732 | 0.66637 | 0.92115 | 1.1342 | 1.3314 | -0.77332 | -0.94393 | -1.1301 | -1.3116 | -1.4716 | -1.6165 | -1.7534 | -1.9092 | -2.0629 | -2.1974
66109 | 25.7381 | 49.4418 | 77.2368 | 108.1198 | 139.5384 | 173.7747 | 211.5711 | 292.4652 | 360.1214 | 422.7351 | -245.5295 | -299.6989 | -358.8108 | -416.4274 | -467.2216 | -513.2447 | -556.69 | -606.1661 | -654.957 | -697.6692
67081 | 38.7556 | 74.3309 | 116.0618 | 162.4926 | 209.8019 | 261.4499 | 318.469 | 440.7811 | 543.0918 | 637.8625 | -372.2114 | -453.3284 | -541.7748 | -627.8661 | -703.6388 | -772.1459 | -836.6696 | -909.5622 | -981.5434 | -1044.487
67082 | 113.6825 | 194.767 | 290.5221 | 400.307 | 516.1037 | 647.8076 | 798.1697 | 1129.9941 | 1408.7234 | 1673.175 | -975.1135 | -1149.6589 | -1335.435 | -1508.873 | -1653.7199 | -1775.4455 | -1880.9126 | -1963.8156 | -2055.9838 | -2128.5182
67083 | 20.7321 | 39.3901 | 61.0989 | 85.1052 | 109.5101 | 136.2021 | 165.7763 | 228.5301 | 281.5508 | 331.098 | -211.7673 | -253.492 | -298.3651 | -341.2302 | -378.1591 | -410.7238 | -440.5819 | -472.1015 | -503.6538 | -530.6097
67084 | 21.0124 | 37.7343 | 57.6313 | 80.6974 | 105.2528 | 133.4006 | 165.7052 | 237.4098 | 297.5924 | 354.7993 | -193.323 | -229.4034 | -267.9759 | -304.1159 | -334.3879 | -359.849 | -381.9194 | -398.6332 | -417.6294 | -432.5776
67085 | 28.3322 | 54.4249 | 85.0213 | 119.0169 | 153.6021 | 191.289 | 232.8948 | 321.942 | 396.4171 | 465.3415 | -270.2758 | -329.9047 | -394.9744 | -458.398 | -514.3117 | -564.9733 | -612.7974 | -667.26 | -720.9684 | -767.9855
67086 | 80.619 | 154.8658 | 241.9275 | 338.662 | 437.0739 | 544.3117 | 662.7006 | 916.0839 | 1128.0024 | 1324.1262 | -769.0681 | -938.7418 | -1123.897 | -1304.3686 | -1463.4706 | -1607.628 | -1743.711 | -1898.684 | -2051.5109 | -2185.2978
67087 | 97.6321 | 188.0395 | 294.3409 | 414.3057 | 538.6885 | 677.451 | 833.5047 | 1171.0465 | 1455.287 | 1722.691 | -1054.9842 | -1255.0663 | -1470.3722 | -1675.365 | -1850.9741 | -2004.0971 | -2142.6957 | -2277.4371 | -2416.6516 | -2533.3177
67088 | 646.7543 | 695.2137 | 751.7877 | 814.5158 | 878.3246 | 948.0176 | 1025.0438 | 1188.0345 | 1324.8434 | 1451.8649 | -1199.9139 | -1309.3419 | -1427.7799 | -1541.947 | -1641.3556 | -1730.1996 | -1812.8556 | -1904.6815 | -1995.1642 | -2071.9607
67089 | 52.3679 | 100.5966 | 157.1495 | 219.9855 | 283.9112 | 353.57 | 430.4722 | 595.063 | 732.7195 | 860.1162 | -499.5656 | -609.781 | -730.0527 | -847.2822 | -950.6305 | -1044.2712 | -1132.667 | -1233.3332 | -1332.6054 | -1419.5097
67090 | 98.667 | 192.6272 | 304.3667 | 433.5841 | 570.7581 | 727.4885 | 906.889 | 1303.7893 | 1636.643 | 1952.419 | -948.5405 | -1152.2551 | -1370.5424 | -1575.9245 | -1748.9183 | -1895.6301 | -2024.1082 | -2127.1658 | -2241.5317 | -2334.4926
67091 | 51.1728 | 100.0617 | 158.0222 | 223.2801 | 290.3767 | 364.0827 | 447.0187 | 623.6404 | 771.3184 | 908.119 | -562.744 | -675.5823 | -800.1237 | -923.1693 | -1033.2405 | -1134.4674 | -1231.5211 | -1344.1581 | -1455.2226 | -1554.5795
80001 | 19.8223 | 41.2083 | 66.5622 | 95.0938 | 124.4417 | 156.705 | 192.518 | 269.4795 | 334.4548 | 395.0303 | -203.6131 | -253.0379 | -307.5958 | -361.458 | -409.5859 | -453.7572 | -496.0102 | -544.4228 | -593.2317 | -636.7925
80002 | 1.3748 | 2.858 | 4.6164 | 6.5952 | 8.6306 | 10.8682 | 13.3521 | 18.6897 | 23.1961 | 27.3973 | -14.1216 | -17.5494 | -21.3333 | -25.0689 | -28.4068 | -31.4703 | -34.4007 | -37.7584 | -41.1435 | -44.1646
80003 | 37.4706 | 77.897 | 125.824 | 179.758 | 235.2349 | 296.223 | 363.9211 | 509.4031 | 632.2275 | 746.7347 | -384.8944 | -478.3233 | -581.4552 | -683.2721 | -774.2494 | -857.7474 | -937.6193 | -1029.1347 | -1121.3992 | -1203.7433
80004 | 35.5843 | 73.9756 | 119.4898 | 170.7088 | 223.3929 | 281.3107 | 345.6008 | 483.7591 | 600.4003 | 709.1431 | -365.5183 | -454.2438 | -552.184 | -648.8753 | -735.2727 | -814.5673 | -890.4183 | -977.3267 | -1064.9465 | -1143.1453
80005 | 91.1905 | 189.5719 | 306.2061 | 437.4582 | 572.4641 | 720.8812 | 885.6268 | 1239.6597 | 1538.5557 | 1817.2117 | -936.7086 | -1164.0761 | -1415.0558 | -1662.8343 | -1884.2327 | -2087.4291 | -2281.8002 | -2504.5058 | -2729.0331 | -2929.4186
80006 | 27.5092 | 56.9207 | 91.7241 | 130.7906 | 170.889 | 214.8927 | 263.6784 | 368.2346 | 456.6139 | 538.9849 | -283.6591 | -351.5716 | -426.4225 | -500.1948 | -565.9981 | -626.2937 | -683.8735 | -749.8054 | -816.1305 | -875.2876
80007 | 51.8258 | 107.7398 | 174.0279 | 248.6244 | 325.3547 | 409.7077 | 503.3414 | 704.5584 | 874.4375 | 1032.8131 | -532.3496 | -661.5717 | -804.214 | -945.0377 | -1070.8688 | -1186.3555 | -1296.8267 | -1423.4022 | -1551.0137 | -1664.9043
80008 | 83.1579 | 172.8756 | 279.2391 | 398.934 | 522.0529 | 657.4027 | 807.644 | 1130.5098 | 1403.0918 | 1657.2159 | -854.1896 | -1061.5348 | -1290.4138 | -1516.3744 | -1718.2788 | -1903.5845 | -2080.8429 | -2283.9415 | -2488.7025 | -2671.4473
80009 | 51.1864 | 106.4105 | 171.8807 | 245.5568 | 321.3405 | 404.6527 | 497.1311 | 695.8655 | 863.6486 | 1020.0702 | -525.7815 | -653.4092 | -794.2916 | -933.3777 | -1057.6564 | -1171.7181 | -1280.8264 | -1405.8402 | -1531.8772 | -1644.3626
80010 | 6.8419 | 14.2235 | 22.9747 | 32.8227 | 42.9524 | 54.0885 | 66.4498 | 93.0139 | 115.4409 | 136.3492 | -70.2793 | -87.3389 | -106.1701 | -124.7613 | -141.3732 | -156.6194 | -171.2035 | -187.9137 | -204.7606 | -219.7961
80011 | 45.8207 | 95.5958 | 154.2124 | 219.8431 | 287.1702 | 361.196 | 443.4475 | 618.513 | 767.198 | 906.0183 | -498.2808 | -611.6929 | -735.5551 | -856.1548 | -962.2678 | -1058.0001 | -1147.9477 | -1247.0632 | -1346.7872 | -1434.796
81001 | 16.0944 | 33.4676 | 54.0535 | 77.2103 | 101.0246 | 127.205 | 156.268 | 218.6774 | 271.3914 | 320.5414 | -166.079 | -206.1855 | -250.4208 | -294.0457 | -332.981 | -368.6698 | -402.764 | -441.7198 | -480.989 | -516.0086
81002 | 32.2842 | 67.5549 | 108.8605 | 154.9127 | 202.0479 | 253.8789 | 311.5177 | 434.2572 | 537.9881 | 635.0687 | -367.3486 | -446.7631 | -532.7069 | -615.377 | -687.1147 | -750.8108 | -809.6354 | -871.9321 | -934.6986 | -989.0113
81003 | 97.2166 | 203.4276 | 327.8068 | 466.4746 | 608.4011 | 764.4662 | 938.0191 | 1307.5977 | 1619.9379 | 1912.2556 | -1106.4737 | -1345.5984 | -1604.3684 | -1853.2634 | -2069.2252 | -2260.9589 | -2438.0093 | -2625.4626 | -2814.3333 | -2977.7383
82001 | 18.0706 | 37.3695 | 60.201 | 85.8213 | 112.1113 | 140.9555 | 172.9293 | 241.4318 | 299.3443 | 353.3178 | -186.421 | -230.978 | -280.0781 | -328.4605 | -371.6074 | -411.1349 | -448.8741 | -492.084 | -535.5398 | -574.2962
82002 | 90.344 | 182.3146 | 290.0488 | 409.3165 | 530.2956 | 661.7443 | 806.4834 | 1111.8628 | 1371.8246 | 1613.7211 | -948.1242 | -1159.436 | -1390.3838 | -1615.8765 | -1815.0354 | -1995.8301 | -2166.7973 | -2361.7403 | -2555.3864 | -2727.4453
82003 | 106.3843 | 203.9898 | 318.1698 | 444.9242 | 574.0396 | 715.2163 | 871.5053 | 1202.1187 | 1482.0546 | 1743.7656 | -1003.1087 | -1224.41 | -1464.5724 | -1696.673 | -1899.2461 | -2080.5071 | -2249.3188 | -2433.6381 | -2618.348 | -2779.9024
82004 | 34.3094 | 69.2939 | 110.2755 | 155.6426 | 201.6577 | 251.6502 | 306.6929 | 422.8285 | 521.6876 | 613.673 | -360.672 | -441.0684 | -528.9447 | -614.7582 | -690.5631 | -759.3923 | -824.4941 | -898.7694 | -972.5419 | -1038.1042
82005 | 75.0839 | 151.6455 | 241.3313 | 340.6144 | 441.3157 | 550.7213 | 671.1788 | 925.3346 | 1141.6817 | 1342.986 | -789.3087 | -965.2514 | -1157.5634 | -1345.361 | -1511.2555 | -1661.8841 | -1804.3554 | -1966.9023 | -2128.3489 | -2271.828
82006 | 8.6467 | 17.4637 | 27.792 | 39.2255 | 50.8224 | 63.4217 | 77.2937 | 106.5626 | 131.4773 | 154.6598 | -90.8977 | -111.1594 | -133.3063 | -154.9333 | -174.0379 | -191.3844 | -207.7916 | -226.5107 | -245.103 | -261.6263
82007 | 20.4539 | 41.4598 | 66.105 | 93.4468 | 121.2312 | 151.4654 | 184.7909 | 255.2831 | 315.2204 | 371.0052 | -214.411 | -262.7193 | -315.5902 | -367.2946 | -413.0383 | -454.6329 | -494.0352 | -539.016 | -583.7845 | -623.5941
82008 | 75.3616 | 152.2062 | 242.2237 | 341.8739 | 442.9476 | 552.7578 | 673.6607 | 928.7564 | 1145.9034 | 1347.9522 | -792.2274 | -968.8207 | -1161.8439 | -1350.336 | -1516.8439 | -1668.0294 | -1811.0276 | -1974.1756 | -2136.2192 | -2280.2288
85001 | 111.2711 | 226.4402 | 363.0816 | 520.8271 | 688.177 | 879.4482 | 1098.5331 | 1583.7804 | 1991.1603 | 2378.0558 | -1197.679 | -1445.8616 | -1710.7403 | -1958.6118 | -2166.0634 | -2340.5806 | -2491.9427 | -2608.6404 | -2739.9531 | -2844.237
85002 | 86.8315 | 172.7914 | 276.0598 | 398.0219 | 530.0656 | 683.8573 | 862.359 | 1263.9959 | 1600.4793 | 1921.8209 | -874.3298 | -1057.2892 | -1252.5552 | -1434.1697 | -1584.572 | -1708.4504 | -1812.9786 | -1876.0157 | -1955.3757 | -2014.913
85003 | 56.2017 | 114.9942 | 184.9215 | 265.3908 | 350.3156 | 446.6354 | 556.2551 | 796.7486 | 998.9826 | 1190.2585 | -600.6334 | -729.9636 | -869.6442 | -1002.7751 | -1116.7795 | -1215.7105 | -1304.7506 | -1385.5522 | -1472.0081 | -1545.0886
85004 | 22.3108 | 46.6688 | 75.1746 | 106.9188 | 139.3751 | 175.0291 | 214.6506 | 298.944 | 370.2171 | 436.9136 | -252.2191 | -307.0727 | -366.4197 | -423.4955 | -473.0174 | -516.9907 | -557.6042 | -600.708 | -644.1092 | -681.6901
85005 | 0.040308 | 0.083895 | 0.13446 | 0.18989 | 0.24576 | 0.30627 | 0.37286 | 0.51258 | 0.63156 | 0.7427 | -0.41469 | -0.51318 | -0.61944 | -0.72148 | -0.80999 | -0.88875 | -0.9617 | -1.0416 | -1.1215 | -1.1913
85006 | 108.2712 | 214.967 | 343.558 | 496.3667 | 662.7109 | 857.4313 | 1084.2222 | 1596.6509 | 2025.5785 | 2435.7373 | -1081.9749 | -1307.9497 | -1548.958 | -1772.5201 | -1956.8968 | -2107.5975 | -2233.4728 | -2302.0066 | -2392.6283 | -2458.7455
85008 | 62.8395 | 131.4767 | 211.8505 | 301.4407 | 393.1184 | 493.9063 | 605.9689 | 844.5428 | 1046.1944 | 1234.9103 | -713.5967 | -868.1663 | -1035.4516 | -1196.3818 | -1336.0499 | -1460.0876 | -1574.6657 | -1696.1288 | -1818.4845 | -1924.4106
89001 | 0.13816 | 0.27431 | 0.4384 | 0.63339 | 0.84565 | 1.0941 | 1.3835 | 2.0374 | 2.5847 | 3.1081 | -1.3807 | -1.669 | -1.9766 | -2.2618 | -2.4971 | -2.6894 | -2.85 | -2.9375 | -3.0531 | -3.1375
89002 | 0.046053 | 0.091436 | 0.14613 | 0.21113 | 0.28188 | 0.36471 | 0.46117 | 0.67914 | 0.86158 | 1.036 | -0.46022 | -0.55634 | -0.65885 | -0.75394 | -0.83237 | -0.89647 | -0.95001 | -0.97916 | -1.0177 | -1.0458
90018 | 0.029838 | 0.05764 | 0.091241 | 0.13023 | 0.17141 | 0.21779 | 0.27081 | 0.3861 | 0.4825 | 0.57263 | -0.28263 | -0.34649 | -0.41769 | -0.48862 | -0.55257 | -0.61164 | -0.66856 | -0.73235 | -0.79783 | -0.85646
90019 | 0.14919 | 0.2882 | 0.4562 | 0.65113 | 0.85703 | 1.0889 | 1.3541 | 1.9305 | 2.4125 | 2.8632 | -1.4131 | -1.7325 | -2.0884 | -2.4431 | -2.7629 | -3.0582 | -3.3428 | -3.6617 | -3.9892 | -4.2823
90020 | 3.2822 | 6.3403 | 10.0365 | 14.3249 | 18.8546 | 23.9565 | 29.7896 | 42.4715 | 53.0753 | 62.9895 | -31.0888 | -38.1144 | -45.9459 | -53.7482 | -60.7829 | -67.2808 | -73.5421 | -80.5581 | -87.7614 | -94.2107
90021 | 5.9377 | 11.4703 | 18.1569 | 25.9151 | 34.1097 | 43.3394 | 53.8921 | 76.8349 | 96.018 | 113.9538 | -56.2425 | -68.9524 | -83.1203 | -97.2353 | -109.9618 | -121.717 | -133.0443 | -145.7369 | -158.7684 | -170.4357
90023 | 14.6802 | 28.3587 | 44.8904 | 64.0716 | 84.3314 | 107.1507 | 133.2407 | 189.9637 | 237.3912 | 281.7349 | -139.0519 | -170.4753 | -205.5033 | -240.4009 | -271.8654 | -300.9285 | -328.9336 | -360.3143 | -392.5329 | -421.3786
90024 | 4.9829 | 9.6258 | 15.2372 | 21.7479 | 28.6247 | 36.3703 | 45.226 | 64.4795 | 80.5779 | 95.6295 | -47.1985 | -57.8646 | -69.7542 | -81.5995 | -92.2795 | -102.1444 | -111.6502 | -122.3018 | -133.2378 | -143.0289
91001 | 32.9156 | 62.4228 | 99.8597 | 148.2611 | 204.5758 | 274.2484 | 358.3139 | 556.028 | 719.9033 | 878.3219 | -262.118 | -321.0698 | -384.1516 | -441.5119 | -487.087 | -521.223 | -546.2629 | -536.2081 | -539.2882 | -536.0158
91002 | 34.7006 | 65.6752 | 104.4684 | 153.6444 | 210.0331 | 279.0078 | 361.6535 | 554.5657 | 714.7267 | 869.2471 | -280.7379 | -343.4876 | -410.5053 | -471.6549 | -520.6003 | -558.0033 | -586.3386 | -582.4619 | -590.5471 | -591.9075
91003 | 32.5695 | 62.894 | 99.5743 | 142.22 | 187.3552 | 238.2842 | 296.5082 | 423.5058 | 529.6634 | 629.0053 | -307.5954 | -377.0994 | -454.5257 | -531.5617 | -600.9058 | -664.8117 | -726.247 | -794.3997 | -864.6114 | -927.3624
91004 | 32.1832 | 64.5816 | 103.1029 | 147.0418 | 192.9339 | 244.3229 | 302.2232 | 427.3958 | 533.1056 | 632.6114 | -317.3047 | -390.3873 | -470.2091 | -547.6248 | -615.3222 | -675.7143 | -731.7582 | -789.2412 | -848.879 | -900.9256
91005 | 53.0214 | 106.7915 | 170.4715 | 242.6018 | 317.4599 | 400.7767 | 494.242 | 695.1706 | 865.134 | 1024.897 | -527.7324 | -649.3646 | -782.0793 | -910.7737 | -1023.3445 | -1123.927 | -1217.4264 | -1315.0778 | -1415.5254 | -1503.3878
91006 | 77.7913 | 156.5859 | 249.988 | 355.8339 | 465.6854 | 587.89 | 724.9014 | 1019.1555 | 1268.037 | 1501.8057 | -774.8216 | -953.4989 | -1148.8186 | -1338.7231 | -1505.3532 | -1654.8019 | -1794.3039 | -1941.7493 | -2093.0768 | -2225.8718
91007 | 39.8633 | 77.0064 | 121.8974 | 173.983 | 228.9975 | 290.962 | 361.8082 | 515.8363 | 644.6231 | 765.0363 | -377.588 | -462.9168 | -558.0335 | -652.7959 | -738.2361 | -817.1555 | -893.2017 | -978.4144 | -1065.9025 | -1144.2315
91008 | 89.1553 | 172.227 | 272.6268 | 389.1177 | 512.1591 | 650.7445 | 809.1938 | 1153.6817 | 1441.717 | 1711.0244 | -844.4857 | -1035.3258 | -1248.0569 | -1459.9955 | -1651.0849 | -1827.5903 | -1997.6696 | -2188.2502 | -2383.9196 | -2559.1045
91009 | 79.9776 | 159.5138 | 254.1261 | 361.3622 | 472.4323 | 595.4126 | 732.6533 | 1029.2628 | 1279.1935 | 1512.5769 | -795.1736 | -977.9627 | -1179.6468 | -1378.4395 | -1555.6991 | -1717.8407 | -1872.4323 | -2046.2936 | -2222.4567 | -2379.4355
91010 | 47.5017 | 91.7622 | 145.255 | 207.3211 | 272.8773 | 346.7153 | 431.1367 | 614.6791 | 768.1438 | 911.6301 | -449.9402 | -551.6194 | -664.962 | -777.8825 | -879.6945 | -973.7362 | -1064.3541 | -1165.895 | -1270.1472 | -1363.4854
91011 | 64.0244 | 121.3527 | 188.5181 | 263.4286 | 340.1198 | 424.4598 | 518.2549 | 717.9661 | 886.7783 | 1044.7997 | -586.8755 | -716.0627 | -855.9562 | -990.6217 | -1107.5752 | -1211.5115 | -1307.5909 | -1409.5171 | -1512.5067 | -1601.8927
91012 | 46.0678 | 91.4325 | 146.1002 | 210.3587 | 279.4388 | 359.1035 | 450.8318 | 654.8404 | 826.1085 | 988.9057 | -433.2628 | -532.6287 | -640.3985 | -743.1776 | -831.0336 | -906.6816 | -974.1001 | -1029.4455 | -1091.8179 | -1143.8305
93001 | 8.0013 | 16.954 | 27.7701 | 40.4441 | 53.9975 | 69.5053 | 87.2413 | 126.3139 | 159.1052 | 190.1047 | -96.1463 | -116.1417 | -138.0879 | -159.4103 | -178.0594 | -194.6166 | -209.9022 | -224.5097 | -240.0702 | -253.5889
93002 | 24.9514 | 52.8697 | 86.5988 | 126.1217 | 168.3869 | 216.7468 | 272.0552 | 393.9001 | 496.1569 | 592.8264 | -299.8245 | -362.1787 | -430.6162 | -497.1086 | -555.2643 | -606.8966 | -654.5636 | -700.1159 | -748.6401 | -790.7969
93003 | 32.9264 | 69.7679 | 114.2775 | 166.4327 | 222.2068 | 286.0234 | 359.0095 | 519.7985 | 654.7387 | 782.3057 | -395.6545 | -477.9384 | -568.2498 | -655.9946 | -732.738 | -800.873 | -863.7753 | -923.8871 | -987.9206 | -1043.5517
93004 | 7.8171 | 16.5636 | 27.1306 | 39.5128 | 52.7541 | 67.9048 | 85.2325 | 123.4054 | 155.4416 | 185.7273 | -93.9324 | -113.4674 | -134.9082 | -155.7397 | -173.9594 | -190.1353 | -205.069 | -219.3401 | -234.5423 | -247.7497
93005 | 35.0847 | 74.341 | 121.7681 | 177.342 | 236.7719 | 304.7716 | 382.5417 | 553.87 | 697.6552 | 833.584 | -421.5887 | -509.2661 | -605.4972 | -698.9934 | -780.7672 | -853.3683 | -920.3937 | -984.4457 | -1052.6764 | -1111.9539
93006 | 0.02632 | 0.05577 | 0.091349 | 0.13304 | 0.17762 | 0.22864 | 0.28698 | 0.41551 | 0.52337 | 0.62534 | -0.31627 | -0.38205 | -0.45424 | -0.52438 | -0.58572 | -0.64019 | -0.69047 | -0.73852 | -0.7897 | -0.83417
94001 | 26.2349 | 53.6132 | 87.7093 | 130.0422 | 177.6449 | 234.7152 | 302.1297 | 456.6937 | 585.3122 | 708.4882 | -262.273 | -320.3499 | -383.7059 | -443.8855 | -494.8428 | -537.6058 | -574.5679 | -595.1457 | -623.4817 | -645.8129
94002 | 94.9821 | 184.2786 | 294.9444 | 432.4475 | 587.5814 | 774.6768 | 996.8142 | 1509.7265 | 1936.8319 | 2347.672 | -814.331 | -999.4972 | -1198.2193 | -1382.0339 | -1532.2697 | -1651.7777 | -1747.8812 | -1770.2281 | -1821.4449 | -1853.0881
95001 | 11.2277 | 21.1973 | 33.9977 | 50.9505 | 71.0536 | 96.3403 | 127.1787 | 200.6076 | 261.3553 | 320.3448 | -85.3329 | -104.4972 | -124.7457 | -142.597 | -156.0926 | -165.1892 | -170.6312 | -160.5995 | -155.9723 | -149.2776
96202 | 0.018738 | 0.038838 | 0.064843 | 0.098929 | 0.13875 | 0.18787 | 0.24683 | 0.38464 | 0.49784 | 0.60605 | -0.16123 | -0.20268 | -0.24863 | -0.29287 | -0.33085 | -0.36297 | -0.39111 | -0.40442 | -0.42529 | -0.44116
97001 | 0.02092 | 0.043124 | 0.072067 | 0.1106 | 0.15618 | 0.21304 | 0.28182 | 0.44402 | 0.57709 | 0.70493 | -0.16488 | -0.2095 | -0.25857 | -0.30493 | -0.34369 | -0.37506 | -0.40098 | -0.40447 | -0.41793 | -0.42591
97002 | 24.5422 | 49.0128 | 80.7507 | 122.9322 | 172.8701 | 235.3367 | 311.1011 | 490.3389 | 637.8055 | 779.9783 | -190.872 | -239.3378 | -291.9692 | -340.6554 | -380.2084 | -410.7298 | -434.2737 | -428.4979 | -434.894 | -435.3585
97013 | 0.33808 | 0.59326 | 1.0189 | 1.8044 | 2.9297 | 4.5646 | 6.7263 | 12.2885 | 16.8248 | 21.3355 | -0.7686 | -0.94784 | -1.0703 | -0.98539 | -0.6686 | -0.044228 | 0.30892 | 0.43093 | 0.53772 | 0.63947
97014 | 0.02092 | 0.043124 | 0.072067 | 0.1106 | 0.15618 | 0.21304 | 0.28182 | 0.44402 | 0.57709 | 0.70493 | -0.16488 | -0.2095 | -0.25857 | -0.30493 | -0.34369 | -0.37506 | -0.40098 | -0.40447 | -0.41793 | -0.42591
98001 | 15.4549 | 30.3484 | 51.1195 | 81.9398 | 121.2025 | 173.1289 | 238.2189 | 397.9263 | 528.1214 | 654.9227 | -112.8495 | -137.779 | -164.1367 | -186.1449 | -200.9978 | -207.6753 | -207.2435 | -168.1077 | -142.4607 | -113.5338
98002 | 15.571 | 32.2747 | 53.8844 | 82.2098 | 115.3013 | 156.117 | 205.1135 | 319.6396 | 413.7081 | 503.6292 | -133.9855 | -168.4251 | -206.6153 | -243.3755 | -274.9333 | -301.629 | -325.0113 | -336.0736 | -353.4157 | -366.6054
98003 | 12.1719 | 24.5349 | 41.0545 | 64.0462 | 92.1497 | 128.1808 | 172.5338 | 279.2122 | 366.6481 | 451.2658 | -90.7718 | -113.829 | -138.7459 | -161.2201 | -178.737 | -191.0298 | -199.1045 | -186.694 | -182.1483 | -174.7917
99981 | 61.0108 | 102.1027 | 176.8774 | 326.2831 | 547.7003 | 871.3094 | 1300.0607 | 2410.8315 | 3315.3937 | 4216.4649 | -59.8884 | -69.8691 | -64.7747 | -16.8319 | 21.2762 | 26.9599 | 33.4887 | 47.14 | 59.035 | 70.3875
99982 | 0.094419 | 0.15798 | 0.27371 | 0.50508 | 0.84804 | 1.3493 | 2.0136 | 3.7344 | 5.1358 | 6.5318 | -0.091318 | -0.10645 | -0.098186 | -0.023535 | 0.032727 | 0.041484 | 0.051548 | 0.0726 | 0.090941 | 0.10845
99983 | 0.18884 | 0.31595 | 0.54742 | 1.0102 | 1.6961 | 2.6987 | 4.0271 | 7.4689 | 10.2717 | 13.0636 | -0.18264 | -0.2129 | -0.19637 | -0.04707 | 0.065453 | 0.082968 | 0.1031 | 0.1452 | 0.18188 | 0.21689
| 115.0968 | 209.5155 | 321.987 | 451.5273 | 588.2257 | 743.1487 | 919.3627 | 1305.6352 | 1630.0944 | 1936.5227 | -960.2553 | -1168.9962 | -1395.4586 | -1613.1061 | -1801.2946 | -1966.8131 | -2118.1694 | -2263.7213 | -2417.9655 | -2549.5057
Column index | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21